## Graphs
Average of All Load Types
PV Location and Size Impact (Controllable Parameters)
Power Factor and Sun Condition Impact (Uncontrollable Parameters)
Load Type Impact
Most and Least Effective Conditions
Max 1.05 pu
Target 0.97 pu
Target 2%
PV Bus 3
PV Bus 4
PV Bus 5
With CVR
Without CVR
With CVR
Without CVR
Target 2%
Smaller Size = 5.263 MVAR
Larger Size = 10.526 MVAR
PF = 0.95
PF = 0.98
PF = 0.90
Target 2%
Moderate Sun
Very Sunny
Cloudy
Z-Load
Residential (ZIP Mix)
I-Load
Commerical (ZIP Mix)
Commerical - Most Effective
Residential - Most Effective
Residential - Least Effective
Commerical - Least Effective
Avg Difference = 3.3%
Most Effective Conditions: Cloudy, High PF (0.98), Large PV Size (10.526 MVA), PV right at Load (Bus 5)
Least Effective Conditions: Very Sunny, Low PF (0.9), Small PV Size (5.263 MVA), PV furthest away (Bus 3)
Target 2%

## MW Pivot Table
PF | (All)
PV_size (MVA) | (All)
load type | (All)
sun rating | (All)
PV bus # | (All)
Row Labels | Without CVR | With CVR
1 | 7.716 | 7.4498
2 | 7.517 | 7.2368
3 | 7.407 | 7.1293
4 | 7.398 | 7.1205
5 | 7.563 | 7.2856
6 | 7.986 | 7.7149
7 | 8.626 | 8.345
8 | 9.059 | 8.7947
9 | 9.181 | 8.9244
10 | 9.23 | 8.9834
11 | 9.261 | 9.0245
12 | 9.292 | 9.0593
13 | 9.322 | 9.0891
14 | 9.338 | 9.104
15 | 9.404 | 9.1658
16 | 9.594 | 9.3523
17 | 9.883 | 9.6391
18 | 10 | 9.7552
19 | 9.966 | 9.7209
20 | 9.857 | 9.6118
21 | 9.62 | 9.3748
22 | 9.139 | 8.8746
23 | 8.547 | 8.2669
24 | 8.047 | 7.7749
Grand Total | 8.873 | 8.6166

## Voltage Pivot Table
PF | (All)
PV_size (MVA) | (All)
load type | (All)
sun rating | (All)
PV bus # | (All)
Row Labels | Without CVR | With CVR
1 | 1.0082 | 0.98038
2 | 1.0093 | 0.97931
3 | 1.01 | 0.97976
4 | 1.01 | 0.97979
5 | 1.0091 | 0.9796
6 | 1.0065 | 0.97921
7 | 1.0025 | 0.97646
8 | 0.99991 | 0.97655
9 | 0.99917 | 0.97691
10 | 0.99877 | 0.97756
11 | 0.99855 | 0.9782
12 | 0.9984 | 0.97845
13 | 0.99826 | 0.97831
14 | 0.99818 | 0.97817
15 | 0.99773 | 0.97752
16 | 0.99656 | 0.97644
17 | 0.99468 | 0.97503
18 | 0.99387 | 0.97444
19 | 0.9942 | 0.9746
20 | 0.99489 | 0.97509
21 | 0.99627 | 0.976
22 | 0.99937 | 0.97628
23 | 1.0031 | 0.9768
24 | 1.0061 | 0.97895
Grand Total | 1.001 | 0.97749

## Best and Worst % Reduction
PF | 0.9
PV_size (MVA) | 5.263
sun rating | very sunny
PV bus # | PV Bus 3
Average of % reduction in P | Column Labels |  |  |  | Best |  | Worst
Row Labels | ZIP - Comm | ZIP - Res | Grand Total | HR | Comm - Best | Res - Best | Comm | Res
1 | 1.281% | 1.312% | 1.296% | 1 | 4.584% | 4.851% | 1.281% | 1.312% | 3.57%
2 | 1.281% | 1.311% | 1.296% | 2 | 4.676% | 4.945% | 1.281% | 1.311% | 3.664%
3 | 1.281% | 1.312% | 1.297% | 3 | 4.726% | 4.998% | 1.281% | 1.312% | 3.716%
4 | 1.281% | 1.312% | 1.297% | 4 | 4.73% | 5.002% | 1.281% | 1.312% | 3.722%
5 | 1.28% | 1.311% | 1.296% | 5 | 4.655% | 4.924% | 1.28% | 1.311% | 3.646%
6 | 1.278% | 1.308% | 1.293% | 6 | 4.46% | 4.721% | 1.278% | 1.308% | 3.45%
7 | 1.271% | 1.3% | 1.285% | 7 | 4.161% | 4.409% | 1.271% | 1.3% | 3.454%
8 | 0.9547% | 0.9935% | 0.9741% | 8 | 3.956% | 4.194% | 0.9547% | 0.9935% | 3.24%
9 | 0.9543% | 0.9932% | 0.9738% | 9 | 3.897% | 4.133% | 0.9543% | 0.9932% | 3.179%
10 | 0.9541% | 0.9931% | 0.9736% | 10 | 3.874% | 4.109% | 0.9541% | 0.9931% | 3.243%
11 | 0.8656% | 0.8895% | 0.8775% | 11 | 3.859% | 4.093% | 0.8656% | 0.8895% | 3.306%
12 | 0.7875% | 0.8075% | 0.7975% | 12 | 3.844% | 4.077% | 0.7875% | 0.8075% | 3.267%
13 | 0.8108% | 0.8319% | 0.8213% | 13 | 3.83% | 4.062% | 0.8108% | 0.8319% | 3.214%
14 | 0.8484% | 0.8714% | 0.8599% | 14 | 3.822% | 4.054% | 0.8484% | 0.8714% | 3.101%
15 | 0.9535% | 0.9843% | 0.9689% | 15 | 3.79% | 4.021% | 0.9535% | 0.9843% | 3.068%
16 | 0.9529% | 0.9922% | 0.9725% | 16 | 3.698% | 3.925% | 0.9529% | 0.9922% | 2.973%
17 | 0.9519% | 0.9914% | 0.9716% | 17 | 3.557% | 3.777% | 0.9519% | 0.9914% | 2.826%
18 | 0.9515% | 0.9911% | 0.9713% | 18 | 3.5% | 3.717% | 0.9515% | 0.9911% | 2.765%
19 | 0.9516% | 0.9912% | 0.9714% | 19 | 3.517% | 3.735% | 0.9516% | 0.9912% | 2.783%
20 | 0.952% | 0.9915% | 0.9717% | 20 | 3.57% | 3.791% | 0.952% | 0.9915% | 2.838%
21 | 0.9528% | 0.9921% | 0.9724% | 21 | 3.685% | 3.912% | 0.9528% | 0.9921% | 2.957%
22 | 0.9544% | 0.9933% | 0.9739% | 22 | 3.917% | 4.154% | 0.9544% | 0.9933% | 2.88%
23 | 1.274% | 1.303% | 1.289% | 23 | 4.198% | 4.448% | 1.274% | 1.303% | 3.171%
24 | 1.277% | 1.307% | 1.292% | 24 | 4.432% | 4.691% | 1.277% | 1.307% | 4.691%
Grand Total | 1.054% | 1.087% | 1.071% | [5 empty] | 3.28%
Commerical - Most Effective
Residential - Most Effective
Residential - Least Effective
Commerical - Least Effective
Avg Difference = 3.3%
Most Effective Conditions: Cloudy, High PF (0.98), Large PV Size (10.526 MVA), PV right at Load (Bus 5)
Least Effective Conditions: Very Sunny, Low PF (0.9), Small PV Size (5.263 MVA), PV furthest away (Bus 3)

## Load Type % Reduction Tab
Average of % reduction in P | Column Labels
Row Labels | I | Z | ZIP - Comm | ZIP - Res | Grand Total
1 | 2.789% | 5.4% | 2.738% | 2.872% | 3.45%
2 | 3.02% | 5.833% | 2.957% | 3.098% | 3.727%
3 | 3.038% | 5.867% | 2.975% | 3.118% | 3.749%
4 | 3.039% | 5.87% | 2.977% | 3.119% | 3.751%
5 | 2.813% | 5.818% | 2.949% | 3.09% | 3.668%
6 | 2.746% | 5.315% | 2.692% | 2.825% | 3.394%
7 | 2.636% | 5.105% | 2.58% | 2.711% | 3.258%
8 | 2.364% | 4.573% | 2.308% | 2.426% | 2.918%
9 | 2.13% | 4.474% | 2.203% | 2.372% | 2.795%
10 | 2.086% | 4.27% | 2.07% | 2.26% | 2.672%
11 | 2.05% | 4.015% | 2.024% | 2.127% | 2.554%
12 | 2.014% | 3.947% | 1.967% | 2.09% | 2.504%
13 | 2.022% | 3.91% | 1.969% | 2.092% | 2.498%
14 | 2.035% | 3.93% | 1.979% | 2.079% | 2.506%
15 | 2.051% | 3.974% | 2.001% | 2.105% | 2.533%
16 | 2.042% | 3.952% | 1.99% | 2.093% | 2.519%
17 | 1.995% | 3.875% | 1.949% | 2.053% | 2.468%
18 | 1.981% | 3.843% | 1.933% | 2.036% | 2.448%
19 | 1.988% | 3.861% | 1.942% | 2.046% | 2.459%
20 | 2.011% | 3.905% | 1.965% | 2.07% | 2.488%
21 | 2.061% | 4% | 2.014% | 2.121% | 2.549%
22 | 2.296% | 4.557% | 2.3% | 2.419% | 2.893%
23 | 2.653% | 5.133% | 2.598% | 2.724% | 3.277%
24 | 2.737% | 5.295% | 2.682% | 2.814% | 3.382%
Grand Total | 2.358% | 4.613% | 2.323% | 2.448% | 2.936%

## PV Location % Reduction Table
PF | (All)
PV_size (MVA) | (All)
load type | (All)
sun rating | (All)
Average of % reduction in P | Column Labels
Row Labels | PV Bus 3 | PV Bus 4 | PV Bus 5 | Grand Total
1 | 2.328% | 3.386% | 4.635% | 3.45%
2 | 2.475% | 3.946% | 4.759% | 3.727%
3 | 2.475% | 3.946% | 4.827% | 3.749%
4 | 2.475% | 3.945% | 4.833% | 3.751%
5 | 2.444% | 3.828% | 4.731% | 3.668%
6 | 2.329% | 3.388% | 4.466% | 3.394%
7 | 2.325% | 3.393% | 4.056% | 3.258%
8 | 2.044% | 2.975% | 3.735% | 2.918%
9 | 1.968% | 2.788% | 3.629% | 2.795%
10 | 1.897% | 2.559% | 3.559% | 2.672%
11 | 1.825% | 2.341% | 3.496% | 2.554%
12 | 1.761% | 2.314% | 3.438% | 2.504%
13 | 1.742% | 2.323% | 3.43% | 2.498%
14 | 1.746% | 2.336% | 3.435% | 2.506%
15 | 1.81% | 2.368% | 3.42% | 2.533%
16 | 1.853% | 2.394% | 3.311% | 2.519%
17 | 1.889% | 2.417% | 3.099% | 2.468%
18 | 1.91% | 2.427% | 3.008% | 2.448%
19 | 1.914% | 2.428% | 3.035% | 2.459%
20 | 1.914% | 2.428% | 3.12% | 2.488%
21 | 1.914% | 2.427% | 3.305% | 2.549%
22 | 2.061% | 2.945% | 3.673% | 2.893%
23 | 2.33% | 3.394% | 4.108% | 3.277%
24 | 2.329% | 3.389% | 4.428% | 3.382%
Grand Total | 2.073% | 2.92% | 3.814% | 2.936%

## PV Size % Reduction Tab
PF | (All)
load type | (All)
sun rating | (All)
Average of % reduction in P | Column Labels
Row Labels | 5.263 MVA | 10.526 MVA | Grand Total
1 | 3.088% | 3.812% | 3.45%
2 | 3.225% | 4.228% | 3.727%
3 | 3.244% | 4.254% | 3.749%
4 | 3.246% | 4.257% | 3.751%
5 | 3.194% | 4.142% | 3.668%
6 | 3.04% | 3.749% | 3.394%
7 | 2.923% | 3.593% | 3.258%
8 | 2.628% | 3.208% | 2.918%
9 | 2.535% | 3.055% | 2.795%
10 | 2.439% | 2.904% | 2.672%
11 | 2.323% | 2.785% | 2.554%
12 | 2.261% | 2.748% | 2.504%
13 | 2.273% | 2.724% | 2.498%
14 | 2.295% | 2.716% | 2.506%
15 | 2.343% | 2.722% | 2.533%
16 | 2.35% | 2.689% | 2.519%
17 | 2.308% | 2.628% | 2.468%
18 | 2.292% | 2.605% | 2.448%
19 | 2.304% | 2.615% | 2.459%
20 | 2.332% | 2.643% | 2.488%
21 | 2.394% | 2.704% | 2.549%
22 | 2.618% | 3.168% | 2.893%
23 | 2.94% | 3.614% | 3.277%
24 | 3.03% | 3.734% | 3.382%
Grand Total | 2.651% | 3.221% | 2.936%

## PF % Reduction Tab
load type | (All)
sun rating | (All)
Average of % reduction in P | Column Labels
Row Labels | 90% | 95% | 98% | Grand Total
1 | 2.703% | 3.613% | 4.034% | 3.45%
2 | 3.269% | 3.861% | 4.051% | 3.727%
3 | 3.302% | 3.886% | 4.06% | 3.749%
4 | 3.304% | 3.889% | 4.061% | 3.751%
5 | 3.146% | 3.811% | 4.047% | 3.668%
6 | 2.622% | 3.55% | 4.011% | 3.394%
7 | 2.429% | 3.397% | 3.948% | 3.258%
8 | 1.613% | 3.281% | 3.86% | 2.918%
9 | 1.575% | 3.11% | 3.699% | 2.795%
10 | 1.558% | 2.984% | 3.472% | 2.672%
11 | 1.544% | 2.741% | 3.377% | 2.554%
12 | 1.528% | 2.668% | 3.318% | 2.504%
13 | 1.52% | 2.643% | 3.332% | 2.498%
14 | 1.518% | 2.645% | 3.354% | 2.506%
15 | 1.503% | 2.676% | 3.419% | 2.533%
16 | 1.443% | 2.639% | 3.476% | 2.519%
17 | 1.35% | 2.576% | 3.479% | 2.468%
18 | 1.313% | 2.551% | 3.481% | 2.448%
19 | 1.323% | 2.561% | 3.493% | 2.459%
20 | 1.359% | 2.588% | 3.516% | 2.488%
21 | 1.436% | 2.648% | 3.563% | 2.549%
22 | 1.587% | 3.274% | 3.818% | 2.893%
23 | 2.453% | 3.417% | 3.961% | 3.277%
24 | 2.604% | 3.536% | 4.005% | 3.382%
Grand Total | 2% | 3.106% | 3.701% | 2.936%

## Sun Conditions % Reduction
PF | (All)
load type | (All)
Average of % reduction in P | Column Labels
Row Labels | cloudy | moderate sun | very sunny | Grand Total
1 | 3.45% | 3.45% | 3.45% | 3.45%
2 | 3.727% | 3.727% | 3.727% | 3.727%
3 | 3.749% | 3.749% | 3.749% | 3.749%
4 | 3.751% | 3.751% | 3.751% | 3.751%
5 | 3.668% | 3.668% | 3.668% | 3.668%
6 | 3.394% | 3.394% | 3.394% | 3.394%
7 | 3.26% | 3.26% | 3.254% | 3.258%
8 | 2.927% | 2.927% | 2.899% | 2.918%
9 | 2.834% | 2.824% | 2.727% | 2.795%
10 | 2.756% | 2.729% | 2.53% | 2.672%
11 | 2.675% | 2.638% | 2.349% | 2.554%
12 | 2.656% | 2.614% | 2.244% | 2.504%
13 | 2.63% | 2.601% | 2.264% | 2.498%
14 | 2.616% | 2.592% | 2.309% | 2.506%
15 | 2.601% | 2.589% | 2.408% | 2.533%
16 | 2.554% | 2.55% | 2.454% | 2.519%
17 | 2.481% | 2.481% | 2.443% | 2.468%
18 | 2.451% | 2.451% | 2.443% | 2.448%
19 | 2.459% | 2.459% | 2.459% | 2.459%
20 | 2.488% | 2.488% | 2.488% | 2.488%
21 | 2.549% | 2.549% | 2.549% | 2.549%
22 | 2.893% | 2.893% | 2.893% | 2.893%
23 | 3.277% | 3.277% | 3.277% | 3.277%
24 | 3.382% | 3.382% | 3.382% | 3.382%
Grand Total | 2.968% | 2.96% | 2.88% | 2.936%

## AllLoadData
hour | load MW | load Mvar | PF | load type | sun rating | PV_size (MVA) | Q limit (MVar) | PV bus # | PV bus V pu (no CVR) | PV bus angle (no CVR) | Load bus (5) pu (no CVR) | Load bus (5) angle (no CVR) | PV bus V pu (CVR) | PV bus angle (CVR) | Load bus (5) pu (CVR) | Load bus (5) angle (CVR) | PV bus Q (MVar) | PV bus Q limit (MVar) | load MW CVR | load MVar CVR | MW reduction in P | % reduction in P
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99876 | -2.9197 | 1.0235 | -0.89428 | 0.98578 | -2.781 | -5.263 | 5.263 | 7.5167 | 3.6405 | -0.19925 | 2.582% | -2.582% | Constant Z
2 | 7.517 | 3.6406 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.86793 | 0.98723 | -2.7027 | -5.263 | 5.263 | 7.3231 | 3.5468 | -0.19387 | 2.579% | -2.579%
3 | 7.407 | 3.5874 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0375 | -0.99111 | 1.001 | -2.7972 | 1.0241 | -0.85338 | 0.98802 | -2.6595 | -5.263 | 5.263 | 7.216 | 3.4949 | -0.19101 | 2.579% | -2.579%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0376 | -0.9899 | 1.0011 | -2.7936 | 1.0241 | -0.85219 | 0.98809 | -2.6559 | -5.263 | 5.263 | 7.2072 | 3.4906 | -0.19077 | 2.579% | -2.579%
5 | 7.563 | 3.6629 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.87402 | 0.98689 | -2.7208 | -5.263 | 5.263 | 7.3679 | 3.5684 | -0.19507 | 2.579% | -2.579%
6 | 7.986 | 3.8678 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0364 | -1.0691 | 0.99675 | -3.0268 | 1.0229 | -0.93015 | 0.9838 | -2.8879 | -5.263 | 5.263 | 7.7799 | 3.768 | -0.20612 | 2.581% | -2.581%
7 | 8.626 | 4.1778 | 0.9 | Z | very sunny | 5.263 | 5.2525 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2832 | 1.0216 | -1.0157 | 0.97909 | -3.1432 | -5.2525 | 5.2525 | 8.4036 | 4.07 | -0.22241 | 2.578% | -2.578%
8 | 9.059 | 4.3875 | 0.9 | Z | very sunny | 5.263 | 5.1156 | 3 | 1.0341 | -1.2146 | 0.98869 | -3.4582 | 1.0241 | -1.1097 | 0.97912 | -3.3533 | -3.9125 | 5.1156 | 8.8846 | 4.303 | -0.17436 | 1.925% | -1.925%
9 | 9.181 | 4.4466 | 0.9 | Z | very sunny | 5.263 | 4.7051 | 3 | 1.0338 | -1.2312 | 0.98776 | -3.5078 | 1.0238 | -1.1261 | 0.9782 | -3.4027 | -3.9127 | 4.7051 | 9.0042 | 4.361 | -0.17675 | 1.925% | -1.925%
10 | 9.23 | 4.4703 | 0.9 | Z | very sunny | 5.263 | 4.142 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1327 | 0.97783 | -3.4225 | -3.9127 | 4.142 | 9.0523 | 4.3842 | -0.17771 | 1.925% | -1.925%
11 | 9.261 | 4.4853 | 0.9 | Z | very sunny | 5.263 | 3.5736 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0245 | -1.1461 | 0.97843 | -3.4443 | -3.5736 | 3.5736 | 9.0982 | 4.4065 | -0.16277 | 1.758% | -1.758% |  | 2.936%
12 | 9.292 | 4.5003 | 0.9 | Z | very sunny | 5.263 | 3.2578 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0253 | -1.1589 | 0.97897 | -3.4655 | -3.2578 | 3.2578 | 9.1432 | 4.4283 | -0.1488 | 1.601% | -1.601%
13 | 9.322 | 4.5149 | 0.9 | Z | very sunny | 5.263 | 3.3525 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5652 | 1.025 | -1.1604 | 0.97851 | -3.4751 | -3.3525 | 3.3525 | 9.1683 | 4.4404 | -0.15366 | 1.648% | -1.648%
14 | 9.338 | 4.5226 | 0.9 | Z | very sunny | 5.263 | 3.5052 | 3 | 1.0335 | -1.2526 | 0.98656 | -3.5717 | 1.0245 | -1.1584 | 0.97801 | -3.4775 | -3.5052 | 3.5052 | 9.177 | 4.4446 | -0.16098 | 1.724% | -1.724%
15 | 9.404 | 4.5546 | 0.9 | Z | very sunny | 5.263 | 3.942 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1562 | 0.97651 | -3.4932 | -3.913 | 3.942 | 9.2229 | 4.4668 | -0.18113 | 1.926% | -1.926%
16 | 9.594 | 4.6466 | 0.9 | Z | very sunny | 5.263 | 4.4578 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1819 | 0.97506 | -3.5706 | -3.9134 | 4.4578 | 9.4091 | 4.5571 | -0.18486 | 1.927% | -1.927%
17 | 9.883 | 4.7866 | 0.9 | Z | very sunny | 5.263 | 4.9209 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2211 | 0.97284 | -3.6888 | -3.9139 | 4.9209 | 9.6925 | 4.6943 | -0.19055 | 1.928% | -1.928%
18 | 10 | 4.8432 | 0.9 | Z | very sunny | 5.263 | 5.1893 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.237 | 0.97193 | -3.7368 | -3.9141 | 5.1893 | 9.8071 | 4.7498 | -0.19285 | 1.929% | -1.929%
19 | 9.966 | 4.8268 | 0.9 | Z | very sunny | 5.263 | 5.2577 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2324 | 0.9722 | -3.7229 | -3.914 | 5.2577 | 9.7738 | 4.7337 | -0.19218 | 1.928% | -1.928%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2176 | 0.97304 | -3.6781 | -3.9138 | 5.263 | 9.667 | 4.6819 | -0.19004 | 1.928% | -1.928%
21 | 9.62 | 4.6592 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1854 | 0.97486 | -3.5812 | -3.9134 | 5.263 | 9.4346 | 4.5694 | -0.18537 | 1.927% | -1.927%
22 | 9.139 | 4.4262 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0339 | -1.2255 | 0.98808 | -3.4907 | 1.0239 | -1.1205 | 0.97852 | -3.3857 | -3.9126 | 5.263 | 8.9631 | 4.341 | -0.17593 | 1.925% | -1.925%
23 | 8.547 | 4.1395 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2514 | 1.0217 | -1.0049 | 0.97965 | -3.1113 | -5.263 | 5.263 | 8.3262 | 4.0326 | -0.22079 | 2.583% | -2.583%
24 | 8.047 | 3.8973 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.93826 | 0.98335 | -2.9121 | -5.263 | 5.263 | 7.8393 | 3.7967 | -0.20772 | 2.581% | -2.581%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0369 | -1.0327 | 0.99874 | -2.9195 | 1.0235 | -0.8943 | 0.98578 | -2.7811 | -5.263 | 5.263 | 7.5169 | 3.6406 | -0.19907 | 2.58% | -2.58%
2 | 7.517 | 3.6406 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.86793 | 0.98723 | -2.7027 | -5.263 | 5.263 | 7.3231 | 3.5468 | -0.19387 | 2.579% | -2.579%
3 | 7.407 | 3.5874 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0375 | -0.99111 | 1.001 | -2.7972 | 1.0241 | -0.85338 | 0.98802 | -2.6595 | -5.263 | 5.263 | 7.216 | 3.4949 | -0.19101 | 2.579% | -2.579%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0376 | -0.9899 | 1.0011 | -2.7936 | 1.0241 | -0.85219 | 0.98809 | -2.6559 | -5.263 | 5.263 | 7.2072 | 3.4906 | -0.19077 | 2.579% | -2.579%
5 | 7.563 | 3.6629 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.87402 | 0.98689 | -2.7208 | -5.263 | 5.263 | 7.3679 | 3.5684 | -0.19507 | 2.579% | -2.579%
6 | 7.986 | 3.8678 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.0691 | 0.99675 | -3.0268 | 1.0229 | -0.93015 | 0.9838 | -2.8879 | -5.263 | 5.263 | 7.7799 | 3.768 | -0.20612 | 2.581% | -2.581%
7 | 8.626 | 4.1778 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2832 | 1.0216 | -1.0155 | 0.97906 | -3.143 | -5.263 | 5.263 | 8.4031 | 4.0698 | -0.22287 | 2.584% | -2.584%
8 | 9.059 | 4.3875 | 0.9 | Z | moderate sun | 5.263 | 5.2577 | 3 | 1.0341 | -1.2146 | 0.98869 | -3.4582 | 1.0241 | -1.1097 | 0.97912 | -3.3533 | -3.9125 | 5.2577 | 8.8846 | 4.303 | -0.17436 | 1.925% | -1.925%
9 | 9.181 | 4.4466 | 0.9 | Z | moderate sun | 5.263 | 5.2051 | 3 | 1.0338 | -1.2312 | 0.98776 | -3.5078 | 1.0238 | -1.1261 | 0.9782 | -3.4027 | -3.9127 | 5.2051 | 9.0042 | 4.361 | -0.17675 | 1.925% | -1.925%
10 | 9.23 | 4.4703 | 0.9 | Z | moderate sun | 5.263 | 5.0946 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1327 | 0.97783 | -3.4225 | -3.9127 | 5.0946 | 9.0523 | 4.3842 | -0.17771 | 1.925% | -1.925%
11 | 9.261 | 4.4853 | 0.9 | Z | moderate sun | 5.263 | 4.9788 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1369 | 0.97759 | -3.4351 | -3.9128 | 4.9788 | 9.0827 | 4.3989 | -0.17832 | 1.926% | -1.926%
12 | 9.292 | 4.5003 | 0.9 | Z | moderate sun | 5.263 | 4.9156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1411 | 0.97736 | -3.4477 | -3.9129 | 4.9156 | 9.1131 | 4.4137 | -0.17893 | 1.926% | -1.926%
13 | 9.322 | 4.5149 | 0.9 | Z | moderate sun | 5.263 | 4.9841 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5652 | 1.0235 | -1.1452 | 0.97713 | -3.4599 | -3.9129 | 4.9841 | 9.1425 | 4.4279 | -0.17952 | 1.926% | -1.926%
14 | 9.338 | 4.5226 | 0.9 | Z | moderate sun | 5.263 | 5.0156 | 3 | 1.0335 | -1.2526 | 0.98656 | -3.5717 | 1.0235 | -1.1473 | 0.97701 | -3.4664 | -3.9129 | 5.0156 | 9.1582 | 4.4355 | -0.17983 | 1.926% | -1.926%
15 | 9.404 | 4.5546 | 0.9 | Z | moderate sun | 5.263 | 5.1472 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1562 | 0.97651 | -3.4932 | -3.913 | 5.1472 | 9.2229 | 4.4668 | -0.18113 | 1.926% | -1.926%
16 | 9.594 | 4.6466 | 0.9 | Z | moderate sun | 5.263 | 5.2367 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1819 | 0.97506 | -3.5706 | -3.9134 | 5.2367 | 9.4091 | 4.5571 | -0.18486 | 1.927% | -1.927%
17 | 9.883 | 4.7866 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2211 | 0.97284 | -3.6888 | -3.9139 | 5.263 | 9.6925 | 4.6943 | -0.19055 | 1.928% | -1.928%
18 | 10 | 4.8432 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.237 | 0.97193 | -3.7368 | -3.9141 | 5.263 | 9.8071 | 4.7498 | -0.19285 | 1.929% | -1.929%
19 | 9.966 | 4.8268 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2324 | 0.9722 | -3.7229 | -3.914 | 5.263 | 9.7738 | 4.7337 | -0.19218 | 1.928% | -1.928%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2176 | 0.97304 | -3.6781 | -3.9138 | 5.263 | 9.667 | 4.6819 | -0.19004 | 1.928% | -1.928%
21 | 9.62 | 4.6592 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1854 | 0.97486 | -3.5812 | -3.9134 | 5.263 | 9.4346 | 4.5694 | -0.18537 | 1.927% | -1.927%
22 | 9.139 | 4.4262 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0339 | -1.2255 | 0.98808 | -3.4907 | 1.0239 | -1.1205 | 0.97852 | -3.3857 | -3.9126 | 5.263 | 8.9631 | 4.341 | -0.17593 | 1.925% | -1.925%
23 | 8.547 | 4.1395 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2514 | 1.0217 | -1.0049 | 0.97965 | -3.1113 | -5.263 | 5.263 | 8.3262 | 4.0326 | -0.22079 | 2.583% | -2.583%
24 | 8.047 | 3.8973 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.93826 | 0.98335 | -2.9121 | -5.263 | 5.263 | 7.8393 | 3.7967 | -0.20772 | 2.581% | -2.581%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0369 | -1.0327 | 0.99874 | -2.9195 | 1.0235 | -0.8943 | 0.98578 | -2.7811 | -5.263 | 5.263 | 7.5169 | 3.6406 | -0.19907 | 2.58% | -2.58%
2 | 7.517 | 3.6406 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.86793 | 0.98723 | -2.7027 | -5.263 | 5.263 | 7.3231 | 3.5468 | -0.19387 | 2.579% | -2.579%
3 | 7.407 | 3.5874 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0375 | -0.99111 | 1.001 | -2.7972 | 1.0241 | -0.85338 | 0.98802 | -2.6595 | -5.263 | 5.263 | 7.216 | 3.4949 | -0.19101 | 2.579% | -2.579%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0376 | -0.9899 | 1.0011 | -2.7936 | 1.0241 | -0.85219 | 0.98809 | -2.6559 | -5.263 | 5.263 | 7.2072 | 3.4906 | -0.19077 | 2.579% | -2.579%
5 | 7.563 | 3.6629 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.87402 | 0.98689 | -2.7208 | -5.263 | 5.263 | 7.3679 | 3.5684 | -0.19507 | 2.579% | -2.579%
6 | 7.986 | 3.8678 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.0691 | 0.99675 | -3.0268 | 1.0229 | -0.93015 | 0.9838 | -2.8879 | -5.263 | 5.263 | 7.7799 | 3.768 | -0.20612 | 2.581% | -2.581%
7 | 8.626 | 4.1778 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2832 | 1.0216 | -1.0155 | 0.97906 | -3.143 | -5.263 | 5.263 | 8.4031 | 4.0698 | -0.22287 | 2.584% | -2.584%
8 | 9.059 | 4.3875 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0341 | -1.2146 | 0.98869 | -3.4582 | 1.0241 | -1.1097 | 0.97912 | -3.3533 | -3.9125 | 5.263 | 8.8846 | 4.303 | -0.17436 | 1.925% | -1.925%
9 | 9.181 | 4.4466 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0338 | -1.2312 | 0.98776 | -3.5078 | 1.0238 | -1.1261 | 0.9782 | -3.4027 | -3.9127 | 5.263 | 9.0042 | 4.361 | -0.17675 | 1.925% | -1.925%
10 | 9.23 | 4.4703 | 0.9 | Z | cloudy | 5.263 | 5.2577 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1327 | 0.97783 | -3.4225 | -3.9127 | 5.2577 | 9.0523 | 4.3842 | -0.17771 | 1.925% | -1.925%
11 | 9.261 | 4.4853 | 0.9 | Z | cloudy | 5.263 | 5.2419 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1369 | 0.97759 | -3.4351 | -3.9128 | 5.2419 | 9.0827 | 4.3989 | -0.17832 | 1.926% | -1.926%
12 | 9.292 | 4.5003 | 0.9 | Z | cloudy | 5.263 | 5.2262 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1411 | 0.97736 | -3.4477 | -3.9129 | 5.2262 | 9.1131 | 4.4137 | -0.17893 | 1.926% | -1.926%
13 | 9.322 | 4.5149 | 0.9 | Z | cloudy | 5.263 | 5.2262 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5652 | 1.0235 | -1.1452 | 0.97713 | -3.4599 | -3.9129 | 5.2262 | 9.1425 | 4.4279 | -0.17952 | 1.926% | -1.926%
14 | 9.338 | 4.5226 | 0.9 | Z | cloudy | 5.263 | 5.2367 | 3 | 1.0335 | -1.2526 | 0.98656 | -3.5717 | 1.0235 | -1.1473 | 0.97701 | -3.4664 | -3.9129 | 5.2367 | 9.1582 | 4.4355 | -0.17983 | 1.926% | -1.926%
15 | 9.404 | 4.5546 | 0.9 | Z | cloudy | 5.263 | 5.2525 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1562 | 0.97651 | -3.4932 | -3.913 | 5.2525 | 9.2229 | 4.4668 | -0.18113 | 1.926% | -1.926%
16 | 9.594 | 4.6466 | 0.9 | Z | cloudy | 5.263 | 5.2577 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1819 | 0.97506 | -3.5706 | -3.9134 | 5.2577 | 9.4091 | 4.5571 | -0.18486 | 1.927% | -1.927%
17 | 9.883 | 4.7866 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2211 | 0.97284 | -3.6888 | -3.9139 | 5.263 | 9.6925 | 4.6943 | -0.19055 | 1.928% | -1.928%
18 | 10 | 4.8432 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.237 | 0.97193 | -3.7368 | -3.9141 | 5.263 | 9.8071 | 4.7498 | -0.19285 | 1.929% | -1.929%
19 | 9.966 | 4.8268 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2324 | 0.9722 | -3.7229 | -3.914 | 5.263 | 9.7738 | 4.7337 | -0.19218 | 1.928% | -1.928%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2176 | 0.97304 | -3.6781 | -3.9138 | 5.263 | 9.667 | 4.6819 | -0.19004 | 1.928% | -1.928%
21 | 9.62 | 4.6592 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1854 | 0.97486 | -3.5812 | -3.9134 | 5.263 | 9.4346 | 4.5694 | -0.18537 | 1.927% | -1.927%
22 | 9.139 | 4.4262 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0339 | -1.2255 | 0.98808 | -3.4907 | 1.0239 | -1.1205 | 0.97852 | -3.3857 | -3.9126 | 5.263 | 8.9631 | 4.341 | -0.17593 | 1.925% | -1.925%
23 | 8.547 | 4.1395 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2514 | 1.0217 | -1.0049 | 0.97965 | -3.1113 | -5.263 | 5.263 | 8.3262 | 4.0326 | -0.22079 | 2.583% | -2.583%
24 | 8.047 | 3.8973 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.93826 | 0.98335 | -2.9121 | -5.263 | 5.263 | 7.8393 | 3.7967 | -0.20772 | 2.581% | -2.581%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0369 | -1.0327 | 0.99874 | -2.9195 | 1.0169 | -0.82716 | 0.97948 | -2.714 | -7.7431 | 10.526 | 7.4212 | 3.5943 | -0.29478 | 3.82% | -3.82%
2 | 7.517 | 3.6406 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0099 | -0.72538 | 0.9738 | -2.5601 | -10.526 | 10.526 | 7.1253 | 3.451 | -0.39166 | 5.21% | -5.21%
3 | 7.407 | 3.5874 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0375 | -0.99111 | 1.001 | -2.7972 | 1.0102 | -0.71105 | 0.97459 | -2.5171 | -10.526 | 10.526 | 7.0211 | 3.4005 | -0.38587 | 5.21% | -5.21%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0376 | -0.9899 | 1.0011 | -2.7936 | 1.0102 | -0.70988 | 0.97466 | -2.5136 | -10.526 | 10.526 | 7.0126 | 3.3964 | -0.3854 | 5.209% | -5.209%
5 | 7.563 | 3.6629 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0098 | -0.73137 | 0.97347 | -2.5781 | -10.526 | 10.526 | 7.1689 | 3.4721 | -0.3941 | 5.211% | -5.211%
6 | 7.986 | 3.8678 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0364 | -1.0691 | 0.99675 | -3.0268 | 1.0164 | -0.86272 | 0.97751 | -2.8205 | -7.7437 | 10.526 | 7.6807 | 3.72 | -0.30526 | 3.822% | -3.822%
7 | 8.626 | 4.1778 | 0.9 | Z | very sunny | 10.526 | 10.5049 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2832 | 1.015 | -0.94734 | 0.9728 | -3.0748 | -7.7458 | 10.5049 | 8.2959 | 4.0179 | -0.33014 | 3.827% | -3.827%
8 | 9.059 | 4.3875 | 0.9 | Z | very sunny | 10.526 | 10.2313 | 3 | 1.0341 | -1.2146 | 0.98869 | -3.4582 | 1.0241 | -1.1097 | 0.97912 | -3.3533 | -3.9124 | 10.2313 | 8.8846 | 4.303 | -0.17436 | 1.925% | -1.925%
9 | 9.181 | 4.4466 | 0.9 | Z | very sunny | 10.526 | 9.4102 | 3 | 1.0338 | -1.2312 | 0.98776 | -3.5078 | 1.0238 | -1.1261 | 0.9782 | -3.4027 | -3.9127 | 9.4102 | 9.0042 | 4.361 | -0.17675 | 1.925% | -1.925%
10 | 9.23 | 4.4703 | 0.9 | Z | very sunny | 10.526 | 8.284 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1327 | 0.97783 | -3.4225 | -3.9127 | 8.284 | 9.0523 | 4.3842 | -0.17771 | 1.925% | -1.925%
11 | 9.261 | 4.4853 | 0.9 | Z | very sunny | 10.526 | 7.1472 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1369 | 0.97759 | -3.4351 | -3.9128 | 7.1472 | 9.0827 | 4.3989 | -0.17832 | 1.926% | -1.926%
12 | 9.292 | 4.5003 | 0.9 | Z | very sunny | 10.526 | 6.5156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1411 | 0.97736 | -3.4477 | -3.9129 | 6.5156 | 9.1131 | 4.4137 | -0.17893 | 1.926% | -1.926%
13 | 9.322 | 4.5149 | 0.9 | Z | very sunny | 10.526 | 6.7051 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5652 | 1.0235 | -1.1452 | 0.97713 | -3.4599 | -3.9129 | 6.7051 | 9.1425 | 4.4279 | -0.17952 | 1.926% | -1.926%
14 | 9.338 | 4.5226 | 0.9 | Z | very sunny | 10.526 | 7.0103 | 3 | 1.0335 | -1.2526 | 0.98656 | -3.5717 | 1.0235 | -1.1473 | 0.97701 | -3.4664 | -3.9129 | 7.0103 | 9.1582 | 4.4355 | -0.17983 | 1.926% | -1.926%
15 | 9.404 | 4.5546 | 0.9 | Z | very sunny | 10.526 | 7.884 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1562 | 0.97651 | -3.4932 | -3.913 | 7.884 | 9.2229 | 4.4668 | -0.18113 | 1.926% | -1.926%
16 | 9.594 | 4.6466 | 0.9 | Z | very sunny | 10.526 | 8.9155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1819 | 0.97506 | -3.5706 | -3.9134 | 8.9155 | 9.4091 | 4.5571 | -0.18486 | 1.927% | -1.927%
17 | 9.883 | 4.7866 | 0.9 | Z | very sunny | 10.526 | 9.8418 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2211 | 0.97284 | -3.6888 | -3.9139 | 9.8418 | 9.6925 | 4.6943 | -0.19055 | 1.928% | -1.928%
18 | 10 | 4.8432 | 0.9 | Z | very sunny | 10.526 | 10.3786 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.237 | 0.97193 | -3.7368 | -3.9141 | 10.3786 | 9.8071 | 4.7498 | -0.19285 | 1.929% | -1.929%
19 | 9.966 | 4.8268 | 0.9 | Z | very sunny | 10.526 | 10.5155 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2324 | 0.9722 | -3.7229 | -3.914 | 10.5155 | 9.7738 | 4.7337 | -0.19218 | 1.928% | -1.928%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2176 | 0.97304 | -3.6781 | -3.9138 | 10.526 | 9.667 | 4.6819 | -0.19004 | 1.928% | -1.928%
21 | 9.62 | 4.6592 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1854 | 0.97486 | -3.5812 | -3.9134 | 10.526 | 9.4346 | 4.5694 | -0.18537 | 1.927% | -1.927%
22 | 9.139 | 4.4262 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0339 | -1.2255 | 0.98808 | -3.4907 | 1.0239 | -1.1205 | 0.97852 | -3.3857 | -3.9126 | 10.526 | 8.9631 | 4.341 | -0.17593 | 1.925% | -1.925%
23 | 8.547 | 4.1395 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2514 | 1.0152 | -0.93687 | 0.97338 | -3.0433 | -7.7456 | 10.526 | 8.2199 | 3.9811 | -0.32707 | 3.827% | -3.827%
24 | 8.047 | 3.8973 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.87077 | 0.97707 | -2.8446 | -7.744 | 10.526 | 7.7394 | 3.7483 | -0.30763 | 3.823% | -3.823%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0369 | -1.0327 | 0.99874 | -2.9194 | 1.0169 | -0.82716 | 0.97948 | -2.714 | -7.743 | 10.526 | 7.4212 | 3.5943 | -0.29478 | 3.82% | -3.82%
2 | 7.517 | 3.6406 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0099 | -0.72538 | 0.9738 | -2.5601 | -10.526 | 10.526 | 7.1253 | 3.451 | -0.39166 | 5.21% | -5.21%
3 | 7.407 | 3.5874 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0375 | -0.99111 | 1.001 | -2.7972 | 1.0102 | -0.71105 | 0.97459 | -2.5171 | -10.526 | 10.526 | 7.0211 | 3.4005 | -0.38587 | 5.21% | -5.21%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0376 | -0.9899 | 1.0011 | -2.7936 | 1.0102 | -0.70988 | 0.97466 | -2.5136 | -10.526 | 10.526 | 7.0126 | 3.3964 | -0.3854 | 5.209% | -5.209%
5 | 7.563 | 3.6629 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0098 | -0.73137 | 0.97347 | -2.5781 | -10.526 | 10.526 | 7.1689 | 3.4721 | -0.3941 | 5.211% | -5.211%
6 | 7.986 | 3.8678 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.0691 | 0.99675 | -3.0268 | 1.0164 | -0.86272 | 0.97751 | -2.8205 | -7.7437 | 10.526 | 7.6807 | 3.72 | -0.30526 | 3.822% | -3.822%
7 | 8.626 | 4.1778 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2832 | 1.015 | -0.94734 | 0.9728 | -3.0748 | -7.7458 | 10.526 | 8.2959 | 4.0179 | -0.33014 | 3.827% | -3.827%
8 | 9.059 | 4.3875 | 0.9 | Z | moderate sun | 10.526 | 10.5155 | 3 | 1.0341 | -1.2146 | 0.98869 | -3.4582 | 1.0241 | -1.1097 | 0.97912 | -3.3533 | -3.9124 | 10.5155 | 8.8846 | 4.303 | -0.17436 | 1.925% | -1.925%
9 | 9.181 | 4.4466 | 0.9 | Z | moderate sun | 10.526 | 10.4102 | 3 | 1.0338 | -1.2312 | 0.98776 | -3.5078 | 1.0238 | -1.1261 | 0.9782 | -3.4027 | -3.9127 | 10.4102 | 9.0042 | 4.361 | -0.17675 | 1.925% | -1.925%
10 | 9.23 | 4.4703 | 0.9 | Z | moderate sun | 10.526 | 10.1892 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1327 | 0.97783 | -3.4225 | -3.9127 | 10.1892 | 9.0523 | 4.3842 | -0.17771 | 1.925% | -1.925%
11 | 9.261 | 4.4853 | 0.9 | Z | moderate sun | 10.526 | 9.9576 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1369 | 0.97759 | -3.4351 | -3.9128 | 9.9576 | 9.0827 | 4.3989 | -0.17832 | 1.926% | -1.926%
12 | 9.292 | 4.5003 | 0.9 | Z | moderate sun | 10.526 | 9.8313 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1411 | 0.97736 | -3.4477 | -3.9129 | 9.8313 | 9.1131 | 4.4137 | -0.17893 | 1.926% | -1.926%
13 | 9.322 | 4.5149 | 0.9 | Z | moderate sun | 10.526 | 9.9681 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5652 | 1.0235 | -1.1452 | 0.97713 | -3.4599 | -3.9129 | 9.9681 | 9.1425 | 4.4279 | -0.17952 | 1.926% | -1.926%
14 | 9.338 | 4.5226 | 0.9 | Z | moderate sun | 10.526 | 10.0313 | 3 | 1.0335 | -1.2526 | 0.98656 | -3.5717 | 1.0235 | -1.1473 | 0.97701 | -3.4664 | -3.9129 | 10.0313 | 9.1582 | 4.4355 | -0.17983 | 1.926% | -1.926%
15 | 9.404 | 4.5546 | 0.9 | Z | moderate sun | 10.526 | 10.2944 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1562 | 0.97651 | -3.4932 | -3.913 | 10.2944 | 9.2229 | 4.4668 | -0.18113 | 1.926% | -1.926%
16 | 9.594 | 4.6466 | 0.9 | Z | moderate sun | 10.526 | 10.4734 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1819 | 0.97506 | -3.5706 | -3.9134 | 10.4734 | 9.4091 | 4.5571 | -0.18486 | 1.927% | -1.927%
17 | 9.883 | 4.7866 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2211 | 0.97284 | -3.6888 | -3.9139 | 10.526 | 9.6925 | 4.6943 | -0.19055 | 1.928% | -1.928%
18 | 10 | 4.8432 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.237 | 0.97193 | -3.7368 | -3.9141 | 10.526 | 9.8071 | 4.7498 | -0.19285 | 1.929% | -1.929%
19 | 9.966 | 4.8268 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2324 | 0.9722 | -3.7229 | -3.914 | 10.526 | 9.7738 | 4.7337 | -0.19218 | 1.928% | -1.928%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2176 | 0.97304 | -3.6781 | -3.9138 | 10.526 | 9.667 | 4.6819 | -0.19004 | 1.928% | -1.928%
21 | 9.62 | 4.6592 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1854 | 0.97486 | -3.5812 | -3.9134 | 10.526 | 9.4346 | 4.5694 | -0.18537 | 1.927% | -1.927%
22 | 9.139 | 4.4262 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0339 | -1.2255 | 0.98808 | -3.4907 | 1.0239 | -1.1205 | 0.97852 | -3.3857 | -3.9126 | 10.526 | 8.9631 | 4.341 | -0.17593 | 1.925% | -1.925%
23 | 8.547 | 4.1395 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2514 | 1.0152 | -0.93687 | 0.97338 | -3.0433 | -7.7456 | 10.526 | 8.2199 | 3.9811 | -0.32707 | 3.827% | -3.827%
24 | 8.047 | 3.8973 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.87077 | 0.97707 | -2.8446 | -7.744 | 10.526 | 7.7394 | 3.7483 | -0.30763 | 3.823% | -3.823%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0369 | -1.0327 | 0.99874 | -2.9194 | 1.0169 | -0.82716 | 0.97948 | -2.714 | -7.743 | 10.526 | 7.4212 | 3.5943 | -0.29478 | 3.82% | -3.82%
2 | 7.517 | 3.6406 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0099 | -0.72538 | 0.9738 | -2.5601 | -10.526 | 10.526 | 7.1253 | 3.451 | -0.39166 | 5.21% | -5.21%
3 | 7.407 | 3.5874 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0375 | -0.99111 | 1.001 | -2.7972 | 1.0102 | -0.71105 | 0.97459 | -2.5171 | -10.526 | 10.526 | 7.0211 | 3.4005 | -0.38587 | 5.21% | -5.21%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0376 | -0.9899 | 1.0011 | -2.7936 | 1.0102 | -0.70988 | 0.97466 | -2.5136 | -10.526 | 10.526 | 7.0126 | 3.3964 | -0.3854 | 5.209% | -5.209%
5 | 7.563 | 3.6629 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0098 | -0.73137 | 0.97347 | -2.5781 | -10.526 | 10.526 | 7.1689 | 3.4721 | -0.3941 | 5.211% | -5.211%
6 | 7.986 | 3.8678 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.0691 | 0.99675 | -3.0268 | 1.0164 | -0.86272 | 0.97751 | -2.8205 | -7.7437 | 10.526 | 7.6807 | 3.72 | -0.30526 | 3.822% | -3.822%
7 | 8.626 | 4.1778 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2832 | 1.015 | -0.94734 | 0.9728 | -3.0748 | -7.7458 | 10.526 | 8.2959 | 4.0179 | -0.33014 | 3.827% | -3.827%
8 | 9.059 | 4.3875 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0341 | -1.2146 | 0.98869 | -3.4582 | 1.0241 | -1.1097 | 0.97912 | -3.3533 | -3.9124 | 10.526 | 8.8846 | 4.303 | -0.17436 | 1.925% | -1.925%
9 | 9.181 | 4.4466 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0338 | -1.2312 | 0.98776 | -3.5078 | 1.0238 | -1.1261 | 0.9782 | -3.4027 | -3.9127 | 10.526 | 9.0042 | 4.361 | -0.17675 | 1.925% | -1.925%
10 | 9.23 | 4.4703 | 0.9 | Z | cloudy | 10.526 | 10.5155 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1327 | 0.97783 | -3.4225 | -3.9127 | 10.5155 | 9.0523 | 4.3842 | -0.17771 | 1.925% | -1.925%
11 | 9.261 | 4.4853 | 0.9 | Z | cloudy | 10.526 | 10.4839 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1369 | 0.97759 | -3.4351 | -3.9128 | 10.4839 | 9.0827 | 4.3989 | -0.17832 | 1.926% | -1.926%
12 | 9.292 | 4.5003 | 0.9 | Z | cloudy | 10.526 | 10.4523 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1411 | 0.97736 | -3.4477 | -3.9129 | 10.4523 | 9.1131 | 4.4137 | -0.17893 | 1.926% | -1.926%
13 | 9.322 | 4.5149 | 0.9 | Z | cloudy | 10.526 | 10.4523 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5652 | 1.0235 | -1.1452 | 0.97713 | -3.4599 | -3.9129 | 10.4523 | 9.1425 | 4.4279 | -0.17952 | 1.926% | -1.926%
14 | 9.338 | 4.5226 | 0.9 | Z | cloudy | 10.526 | 10.4734 | 3 | 1.0335 | -1.2526 | 0.98656 | -3.5717 | 1.0235 | -1.1473 | 0.97701 | -3.4664 | -3.9129 | 10.4734 | 9.1582 | 4.4355 | -0.17983 | 1.926% | -1.926%
15 | 9.404 | 4.5546 | 0.9 | Z | cloudy | 10.526 | 10.5049 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1562 | 0.97651 | -3.4932 | -3.913 | 10.5049 | 9.2229 | 4.4668 | -0.18113 | 1.926% | -1.926%
16 | 9.594 | 4.6466 | 0.9 | Z | cloudy | 10.526 | 10.5155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1819 | 0.97506 | -3.5706 | -3.9134 | 10.5155 | 9.4091 | 4.5571 | -0.18486 | 1.927% | -1.927%
17 | 9.883 | 4.7866 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2211 | 0.97284 | -3.6888 | -3.9139 | 10.526 | 9.6925 | 4.6943 | -0.19055 | 1.928% | -1.928%
18 | 10 | 4.8432 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.237 | 0.97193 | -3.7368 | -3.9141 | 10.526 | 9.8071 | 4.7498 | -0.19285 | 1.929% | -1.929%
19 | 9.966 | 4.8268 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2324 | 0.9722 | -3.7229 | -3.914 | 10.526 | 9.7738 | 4.7337 | -0.19218 | 1.928% | -1.928%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2176 | 0.97304 | -3.6781 | -3.9138 | 10.526 | 9.667 | 4.6819 | -0.19004 | 1.928% | -1.928%
21 | 9.62 | 4.6592 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1854 | 0.97486 | -3.5812 | -3.9134 | 10.526 | 9.4346 | 4.5694 | -0.18537 | 1.927% | -1.927%
22 | 9.139 | 4.4262 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0339 | -1.2255 | 0.98808 | -3.4907 | 1.0239 | -1.1205 | 0.97852 | -3.3857 | -3.9126 | 10.526 | 8.9631 | 4.341 | -0.17593 | 1.925% | -1.925%
23 | 8.547 | 4.1395 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2514 | 1.0152 | -0.93687 | 0.97338 | -3.0433 | -7.7456 | 10.526 | 8.2199 | 3.9811 | -0.32707 | 3.827% | -3.827%
24 | 8.047 | 3.8973 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.87077 | 0.97707 | -2.8446 | -7.744 | 10.526 | 7.7394 | 3.7483 | -0.30763 | 3.823% | -3.823%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.5936 | 0.97912 | -2.5543 | -3.8414 | 5.263 | 7.4157 | 3.5916 | -0.30029 | 3.892% | -3.892%
2 | 7.517 | 3.6406 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99103 | -1.4048 | 0.97309 | -2.3384 | -5.263 | 5.263 | 7.1148 | 3.4459 | -0.40217 | 5.35% | -5.35%
3 | 7.407 | 3.5874 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8785 | 1.001 | -2.7972 | 0.99155 | -1.3773 | 0.97388 | -2.296 | -5.263 | 5.263 | 7.0109 | 3.3955 | -0.39615 | 5.348% | -5.348%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99159 | -1.375 | 0.97394 | -2.2925 | -5.263 | 5.263 | 7.0023 | 3.3914 | -0.39565 | 5.348% | -5.348%
5 | 7.563 | 3.6629 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8589 | 0.99082 | -1.4163 | 0.97275 | -2.3562 | -5.263 | 5.263 | 7.1583 | 3.4669 | -0.40469 | 5.351% | -5.351%
6 | 7.986 | 3.8678 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99643 | -1.6621 | 0.97714 | -2.6596 | -3.8428 | 5.263 | 7.6748 | 3.7171 | -0.31118 | 3.897% | -3.897%
7 | 8.626 | 4.1778 | 0.9 | Z | very sunny | 5.263 | 5.2525 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2832 | 0.99334 | -1.8253 | 0.97239 | -2.9112 | -3.8462 | 5.2525 | 8.2889 | 4.0145 | -0.33714 | 3.908% | -3.908%
8 | 9.059 | 4.3875 | 0.9 | Z | very sunny | 5.263 | 5.1156 | 4 | 1.0112 | -2.3117 | 0.98869 | -3.4582 | 1.0012 | -2.1239 | 0.97891 | -3.2705 | -1.9447 | 5.1156 | 8.8807 | 4.3011 | -0.17828 | 1.968% | -1.968%
9 | 9.181 | 4.4466 | 0.9 | Z | very sunny | 5.263 | 4.7051 | 4 | 1.0106 | -2.344 | 0.98776 | -3.5078 | 1.0006 | -2.1558 | 0.97798 | -3.3196 | -1.9451 | 4.7051 | 9.0002 | 4.359 | -0.18079 | 1.969% | -1.969%
10 | 9.23 | 4.4703 | 0.9 | Z | very sunny | 5.263 | 4.142 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1686 | 0.97761 | -3.3393 | -1.9452 | 4.142 | 9.0482 | 4.3822 | -0.1818 | 1.97% | -1.97%
11 | 9.261 | 4.4853 | 0.9 | Z | very sunny | 5.263 | 3.5736 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.1767 | 0.97737 | -3.3518 | -1.9453 | 3.5736 | 9.0786 | 4.3969 | -0.18244 | 1.97% | -1.97%
12 | 9.292 | 4.5003 | 0.9 | Z | very sunny | 5.263 | 3.2578 | 4 | 1.0101 | -2.3735 | 0.98691 | -3.5529 | 1.0001 | -2.1848 | 0.97714 | -3.3643 | -1.9454 | 3.2578 | 9.1089 | 4.4117 | -0.18308 | 1.97% | -1.97%
13 | 9.322 | 4.5149 | 0.9 | Z | very sunny | 5.263 | 3.3525 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5652 | 0.99992 | -2.1927 | 0.97691 | -3.3764 | -1.9455 | 3.3525 | 9.1383 | 4.4259 | -0.18369 | 1.971% | -1.971%
14 | 9.338 | 4.5226 | 0.9 | Z | very sunny | 5.263 | 3.5052 | 4 | 1.0098 | -2.3857 | 0.98656 | -3.5717 | 0.99984 | -2.1969 | 0.97679 | -3.3829 | -1.9456 | 3.5052 | 9.154 | 4.4335 | -0.18402 | 1.971% | -1.971%
15 | 9.404 | 4.5546 | 0.9 | Z | very sunny | 5.263 | 3.942 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2142 | 0.97628 | -3.4096 | -1.9457 | 3.942 | 9.2186 | 4.4648 | -0.18538 | 1.971% | -1.971%
16 | 9.594 | 4.6466 | 0.9 | Z | very sunny | 5.263 | 4.4578 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.264 | 0.97483 | -3.4865 | -1.9463 | 4.4578 | 9.4047 | 4.5549 | -0.18931 | 1.973% | -1.973%
17 | 9.883 | 4.7866 | 0.9 | Z | very sunny | 5.263 | 4.9209 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3401 | 0.9726 | -3.6041 | -1.9471 | 4.9209 | 9.6877 | 4.692 | -0.19529 | 1.976% | -1.976%
18 | 10 | 4.8432 | 0.9 | Z | very sunny | 5.263 | 5.1893 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.371 | 0.97169 | -3.6518 | -1.9475 | 5.1893 | 9.8023 | 4.7475 | -0.19772 | 1.977% | -1.977%
19 | 9.966 | 4.8268 | 0.9 | Z | very sunny | 5.263 | 5.2577 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.362 | 0.97196 | -3.6379 | -1.9474 | 5.2577 | 9.769 | 4.7313 | -0.19701 | 1.977% | -1.977%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3332 | 0.9728 | -3.5935 | -1.9471 | 5.263 | 9.6622 | 4.6796 | -0.19475 | 1.976% | -1.976%
21 | 9.62 | 4.6592 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.2709 | 0.97463 | -3.4971 | -1.9463 | 5.263 | 9.4302 | 4.5672 | -0.18984 | 1.973% | -1.973%
22 | 9.139 | 4.4262 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0108 | -2.3329 | 0.98808 | -3.4907 | 1.0008 | -2.1448 | 0.9783 | -3.3026 | -1.945 | 5.263 | 8.9591 | 4.3391 | -0.17993 | 1.969% | -1.969%
23 | 8.547 | 4.1395 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2514 | 0.99372 | -1.8051 | 0.97298 | -2.88 | -3.8458 | 5.263 | 8.2131 | 3.9778 | -0.33392 | 3.907% | -3.907%
24 | 8.047 | 3.8973 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.6776 | 0.97669 | -2.6835 | -3.8431 | 5.263 | 7.7333 | 3.7454 | -0.31365 | 3.898% | -3.898%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9195 | 0.99771 | -1.5936 | 0.97912 | -2.5543 | -3.8414 | 5.263 | 7.4157 | 3.5916 | -0.30029 | 3.892% | -3.892%
2 | 7.517 | 3.6406 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99103 | -1.4048 | 0.97309 | -2.3384 | -5.263 | 5.263 | 7.1148 | 3.4459 | -0.40217 | 5.35% | -5.35%
3 | 7.407 | 3.5874 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8785 | 1.001 | -2.7972 | 0.99155 | -1.3773 | 0.97388 | -2.296 | -5.263 | 5.263 | 7.0109 | 3.3955 | -0.39615 | 5.348% | -5.348%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99159 | -1.375 | 0.97394 | -2.2925 | -5.263 | 5.263 | 7.0023 | 3.3914 | -0.39565 | 5.348% | -5.348%
5 | 7.563 | 3.6629 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8589 | 0.99082 | -1.4163 | 0.97275 | -2.3562 | -5.263 | 5.263 | 7.1583 | 3.4669 | -0.40469 | 5.351% | -5.351%
6 | 7.986 | 3.8678 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99643 | -1.6621 | 0.97714 | -2.6596 | -3.8428 | 5.263 | 7.6748 | 3.7171 | -0.31118 | 3.897% | -3.897%
7 | 8.626 | 4.1778 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2832 | 0.99334 | -1.8253 | 0.97239 | -2.9112 | -3.8462 | 5.263 | 8.2889 | 4.0145 | -0.33714 | 3.908% | -3.908%
8 | 9.059 | 4.3875 | 0.9 | Z | moderate sun | 5.263 | 5.2577 | 4 | 1.0112 | -2.3117 | 0.98869 | -3.4582 | 1.0012 | -2.1239 | 0.97891 | -3.2705 | -1.9447 | 5.2577 | 8.8807 | 4.3011 | -0.17828 | 1.968% | -1.968%
9 | 9.181 | 4.4466 | 0.9 | Z | moderate sun | 5.263 | 5.2051 | 4 | 1.0106 | -2.344 | 0.98776 | -3.5078 | 1.0006 | -2.1558 | 0.97798 | -3.3196 | -1.9451 | 5.2051 | 9.0002 | 4.359 | -0.18079 | 1.969% | -1.969%
10 | 9.23 | 4.4703 | 0.9 | Z | moderate sun | 5.263 | 5.0946 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1686 | 0.97761 | -3.3393 | -1.9452 | 5.0946 | 9.0482 | 4.3822 | -0.1818 | 1.97% | -1.97%
11 | 9.261 | 4.4853 | 0.9 | Z | moderate sun | 5.263 | 4.9788 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.1767 | 0.97737 | -3.3518 | -1.9453 | 4.9788 | 9.0786 | 4.3969 | -0.18244 | 1.97% | -1.97%
12 | 9.292 | 4.5003 | 0.9 | Z | moderate sun | 5.263 | 4.9156 | 4 | 1.0101 | -2.3735 | 0.98691 | -3.5529 | 1.0001 | -2.1848 | 0.97714 | -3.3643 | -1.9454 | 4.9156 | 9.1089 | 4.4117 | -0.18308 | 1.97% | -1.97%
13 | 9.322 | 4.5149 | 0.9 | Z | moderate sun | 5.263 | 4.9841 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5652 | 0.99992 | -2.1927 | 0.97691 | -3.3764 | -1.9455 | 4.9841 | 9.1383 | 4.4259 | -0.18369 | 1.971% | -1.971%
14 | 9.338 | 4.5226 | 0.9 | Z | moderate sun | 5.263 | 5.0156 | 4 | 1.0098 | -2.3857 | 0.98656 | -3.5717 | 0.99984 | -2.1969 | 0.97679 | -3.3829 | -1.9456 | 5.0156 | 9.154 | 4.4335 | -0.18402 | 1.971% | -1.971%
15 | 9.404 | 4.5546 | 0.9 | Z | moderate sun | 5.263 | 5.1472 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2142 | 0.97628 | -3.4096 | -1.9457 | 5.1472 | 9.2186 | 4.4648 | -0.18538 | 1.971% | -1.971%
16 | 9.594 | 4.6466 | 0.9 | Z | moderate sun | 5.263 | 5.2367 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.264 | 0.97483 | -3.4865 | -1.9463 | 5.2367 | 9.4047 | 4.5549 | -0.18931 | 1.973% | -1.973%
17 | 9.883 | 4.7866 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3401 | 0.9726 | -3.6041 | -1.9471 | 5.263 | 9.6877 | 4.692 | -0.19529 | 1.976% | -1.976%
18 | 10 | 4.8432 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.371 | 0.97169 | -3.6518 | -1.9475 | 5.263 | 9.8023 | 4.7475 | -0.19772 | 1.977% | -1.977%
19 | 9.966 | 4.8268 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.362 | 0.97196 | -3.6379 | -1.9474 | 5.263 | 9.769 | 4.7313 | -0.19701 | 1.977% | -1.977%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3332 | 0.9728 | -3.5935 | -1.9471 | 5.263 | 9.6622 | 4.6796 | -0.19475 | 1.976% | -1.976%
21 | 9.62 | 4.6592 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.2709 | 0.97463 | -3.4971 | -1.9463 | 5.263 | 9.4302 | 4.5672 | -0.18984 | 1.973% | -1.973%
22 | 9.139 | 4.4262 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0108 | -2.3329 | 0.98808 | -3.4907 | 1.0008 | -2.1448 | 0.9783 | -3.3026 | -1.945 | 5.263 | 8.9591 | 4.3391 | -0.17993 | 1.969% | -1.969%
23 | 8.547 | 4.1395 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2514 | 0.99372 | -1.8051 | 0.97298 | -2.88 | -3.8458 | 5.263 | 8.2131 | 3.9778 | -0.33392 | 3.907% | -3.907%
24 | 8.047 | 3.8973 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.6776 | 0.97669 | -2.6835 | -3.8431 | 5.263 | 7.7333 | 3.7454 | -0.31365 | 3.898% | -3.898%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9195 | 0.99771 | -1.5936 | 0.97912 | -2.5543 | -3.8414 | 5.263 | 7.4157 | 3.5916 | -0.30029 | 3.892% | -3.892%
2 | 7.517 | 3.6406 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99103 | -1.4048 | 0.97309 | -2.3384 | -5.263 | 5.263 | 7.1148 | 3.4459 | -0.40217 | 5.35% | -5.35%
3 | 7.407 | 3.5874 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8785 | 1.001 | -2.7972 | 0.99155 | -1.3773 | 0.97388 | -2.296 | -5.263 | 5.263 | 7.0109 | 3.3955 | -0.39615 | 5.348% | -5.348%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99159 | -1.375 | 0.97394 | -2.2925 | -5.263 | 5.263 | 7.0023 | 3.3914 | -0.39565 | 5.348% | -5.348%
5 | 7.563 | 3.6629 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8589 | 0.99082 | -1.4163 | 0.97275 | -2.3562 | -5.263 | 5.263 | 7.1583 | 3.4669 | -0.40469 | 5.351% | -5.351%
6 | 7.986 | 3.8678 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99643 | -1.6621 | 0.97714 | -2.6596 | -3.8428 | 5.263 | 7.6748 | 3.7171 | -0.31118 | 3.897% | -3.897%
7 | 8.626 | 4.1778 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2832 | 0.99334 | -1.8253 | 0.97239 | -2.9112 | -3.8462 | 5.263 | 8.2889 | 4.0145 | -0.33714 | 3.908% | -3.908%
8 | 9.059 | 4.3875 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0112 | -2.3117 | 0.98869 | -3.4582 | 1.0012 | -2.1239 | 0.97891 | -3.2705 | -1.9447 | 5.263 | 8.8807 | 4.3011 | -0.17828 | 1.968% | -1.968%
9 | 9.181 | 4.4466 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0106 | -2.344 | 0.98776 | -3.5078 | 1.0006 | -2.1558 | 0.97798 | -3.3196 | -1.9451 | 5.263 | 9.0002 | 4.359 | -0.18079 | 1.969% | -1.969%
10 | 9.23 | 4.4703 | 0.9 | Z | cloudy | 5.263 | 5.2577 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1686 | 0.97761 | -3.3393 | -1.9452 | 5.2577 | 9.0482 | 4.3822 | -0.1818 | 1.97% | -1.97%
11 | 9.261 | 4.4853 | 0.9 | Z | cloudy | 5.263 | 5.2419 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.1767 | 0.97737 | -3.3518 | -1.9453 | 5.2419 | 9.0786 | 4.3969 | -0.18244 | 1.97% | -1.97%
12 | 9.292 | 4.5003 | 0.9 | Z | cloudy | 5.263 | 5.2262 | 4 | 1.0101 | -2.3735 | 0.98691 | -3.5529 | 1.0001 | -2.1848 | 0.97714 | -3.3643 | -1.9454 | 5.2262 | 9.1089 | 4.4117 | -0.18308 | 1.97% | -1.97%
13 | 9.322 | 4.5149 | 0.9 | Z | cloudy | 5.263 | 5.2262 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5652 | 0.99992 | -2.1927 | 0.97691 | -3.3764 | -1.9455 | 5.2262 | 9.1383 | 4.4259 | -0.18369 | 1.971% | -1.971%
14 | 9.338 | 4.5226 | 0.9 | Z | cloudy | 5.263 | 5.2367 | 4 | 1.0098 | -2.3857 | 0.98656 | -3.5717 | 0.99984 | -2.1969 | 0.97679 | -3.3829 | -1.9456 | 5.2367 | 9.154 | 4.4335 | -0.18402 | 1.971% | -1.971%
15 | 9.404 | 4.5546 | 0.9 | Z | cloudy | 5.263 | 5.2525 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2142 | 0.97628 | -3.4096 | -1.9457 | 5.2525 | 9.2186 | 4.4648 | -0.18538 | 1.971% | -1.971%
16 | 9.594 | 4.6466 | 0.9 | Z | cloudy | 5.263 | 5.2577 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.264 | 0.97483 | -3.4865 | -1.9463 | 5.2577 | 9.4047 | 4.5549 | -0.18931 | 1.973% | -1.973%
17 | 9.883 | 4.7866 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3401 | 0.9726 | -3.6041 | -1.9471 | 5.263 | 9.6877 | 4.692 | -0.19529 | 1.976% | -1.976%
18 | 10 | 4.8432 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.371 | 0.97169 | -3.6518 | -1.9475 | 5.263 | 9.8023 | 4.7475 | -0.19772 | 1.977% | -1.977%
19 | 9.966 | 4.8268 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.362 | 0.97196 | -3.6379 | -1.9474 | 5.263 | 9.769 | 4.7313 | -0.19701 | 1.977% | -1.977%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3332 | 0.9728 | -3.5935 | -1.9471 | 5.263 | 9.6622 | 4.6796 | -0.19475 | 1.976% | -1.976%
21 | 9.62 | 4.6592 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.2709 | 0.97463 | -3.4971 | -1.9463 | 5.263 | 9.4302 | 4.5672 | -0.18984 | 1.973% | -1.973%
22 | 9.139 | 4.4262 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0108 | -2.3329 | 0.98808 | -3.4907 | 1.0008 | -2.1448 | 0.9783 | -3.3026 | -1.945 | 5.263 | 8.9591 | 4.3391 | -0.17993 | 1.969% | -1.969%
23 | 8.547 | 4.1395 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2514 | 0.99372 | -1.8051 | 0.97298 | -2.88 | -3.8458 | 5.263 | 8.2131 | 3.9778 | -0.33392 | 3.907% | -3.907%
24 | 8.047 | 3.8973 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.6776 | 0.97669 | -2.6835 | -3.8431 | 5.263 | 7.7333 | 3.7454 | -0.31365 | 3.898% | -3.898%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9195 | 0.99771 | -1.5936 | 0.97912 | -2.5543 | -3.8414 | 10.526 | 7.4157 | 3.5916 | -0.30029 | 3.892% | -3.892%
2 | 7.517 | 3.6406 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.3617 | 0.97075 | -2.2953 | -5.7 | 10.526 | 7.0808 | 3.4294 | -0.43624 | 5.803% | -5.803%
3 | 7.407 | 3.5874 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8785 | 1.001 | -2.7972 | 0.98918 | -1.3343 | 0.97155 | -2.2531 | -5.6991 | 10.526 | 6.9774 | 3.3793 | -0.42964 | 5.8% | -5.8%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7937 | 0.98922 | -1.3321 | 0.97162 | -2.2496 | -5.699 | 10.526 | 6.9689 | 3.3752 | -0.4291 | 5.8% | -5.8%
5 | 7.563 | 3.6629 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8589 | 0.98844 | -1.3732 | 0.97042 | -2.313 | -5.7003 | 10.526 | 7.124 | 3.4503 | -0.439 | 5.805% | -5.805%
6 | 7.986 | 3.8678 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99643 | -1.6621 | 0.97714 | -2.6596 | -3.8427 | 10.526 | 7.6748 | 3.7171 | -0.31119 | 3.897% | -3.897%
7 | 8.626 | 4.1778 | 0.9 | Z | very sunny | 10.526 | 10.5049 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2832 | 0.99334 | -1.8253 | 0.97239 | -2.9112 | -3.8462 | 10.5049 | 8.2889 | 4.0145 | -0.33714 | 3.908% | -3.908%
8 | 9.059 | 4.3875 | 0.9 | Z | very sunny | 10.526 | 10.2313 | 4 | 1.0112 | -2.3117 | 0.98869 | -3.4582 | 1.0012 | -2.1239 | 0.97891 | -3.2705 | -1.9447 | 10.2313 | 8.8807 | 4.3011 | -0.17828 | 1.968% | -1.968%
9 | 9.181 | 4.4466 | 0.9 | Z | very sunny | 10.526 | 9.4102 | 4 | 1.0106 | -2.344 | 0.98776 | -3.5078 | 1.0006 | -2.1558 | 0.97798 | -3.3196 | -1.9451 | 9.4102 | 9.0002 | 4.359 | -0.18079 | 1.969% | -1.969%
10 | 9.23 | 4.4703 | 0.9 | Z | very sunny | 10.526 | 8.284 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1686 | 0.97761 | -3.3393 | -1.9452 | 8.284 | 9.0482 | 4.3822 | -0.1818 | 1.97% | -1.97%
11 | 9.261 | 4.4853 | 0.9 | Z | very sunny | 10.526 | 7.1472 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.1767 | 0.97737 | -3.3518 | -1.9453 | 7.1472 | 9.0786 | 4.3969 | -0.18244 | 1.97% | -1.97%
12 | 9.292 | 4.5003 | 0.9 | Z | very sunny | 10.526 | 6.5156 | 4 | 1.0101 | -2.3735 | 0.98691 | -3.5529 | 1.0001 | -2.1848 | 0.97714 | -3.3643 | -1.9454 | 6.5156 | 9.1089 | 4.4117 | -0.18308 | 1.97% | -1.97%
13 | 9.322 | 4.5149 | 0.9 | Z | very sunny | 10.526 | 6.7051 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5652 | 0.99992 | -2.1927 | 0.97691 | -3.3764 | -1.9455 | 6.7051 | 9.1383 | 4.4259 | -0.18369 | 1.971% | -1.971%
14 | 9.338 | 4.5226 | 0.9 | Z | very sunny | 10.526 | 7.0103 | 4 | 1.0098 | -2.3857 | 0.98656 | -3.5717 | 0.99984 | -2.1969 | 0.97679 | -3.3829 | -1.9456 | 7.0103 | 9.154 | 4.4335 | -0.18402 | 1.971% | -1.971%
15 | 9.404 | 4.5546 | 0.9 | Z | very sunny | 10.526 | 7.884 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2142 | 0.97628 | -3.4096 | -1.9457 | 7.884 | 9.2186 | 4.4648 | -0.18538 | 1.971% | -1.971%
16 | 9.594 | 4.6466 | 0.9 | Z | very sunny | 10.526 | 8.9155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.264 | 0.97483 | -3.4865 | -1.9463 | 8.9155 | 9.4047 | 4.5549 | -0.18931 | 1.973% | -1.973%
17 | 9.883 | 4.7866 | 0.9 | Z | very sunny | 10.526 | 9.8418 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3401 | 0.9726 | -3.6041 | -1.9471 | 9.8418 | 9.6877 | 4.692 | -0.19529 | 1.976% | -1.976%
18 | 10 | 4.8432 | 0.9 | Z | very sunny | 10.526 | 10.3786 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.371 | 0.97169 | -3.6518 | -1.9475 | 10.3786 | 9.8023 | 4.7475 | -0.19772 | 1.977% | -1.977%
19 | 9.966 | 4.8268 | 0.9 | Z | very sunny | 10.526 | 10.5155 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.362 | 0.97196 | -3.6379 | -1.9474 | 10.5155 | 9.769 | 4.7313 | -0.19701 | 1.977% | -1.977%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3332 | 0.9728 | -3.5935 | -1.9471 | 10.526 | 9.6622 | 4.6796 | -0.19475 | 1.976% | -1.976%
21 | 9.62 | 4.6592 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.2709 | 0.97463 | -3.4971 | -1.9463 | 10.526 | 9.4302 | 4.5672 | -0.18984 | 1.973% | -1.973%
22 | 9.139 | 4.4262 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0108 | -2.3329 | 0.98808 | -3.4907 | 1.0008 | -2.1448 | 0.9783 | -3.3026 | -1.945 | 10.526 | 8.9591 | 4.3391 | -0.17993 | 1.969% | -1.969%
23 | 8.547 | 4.1395 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2514 | 0.99372 | -1.8051 | 0.97298 | -2.88 | -3.8458 | 10.526 | 8.2131 | 3.9778 | -0.33392 | 3.907% | -3.907%
24 | 8.047 | 3.8973 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.6776 | 0.97669 | -2.6835 | -3.8431 | 10.526 | 7.7333 | 3.7454 | -0.31365 | 3.898% | -3.898%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9195 | 0.99771 | -1.5936 | 0.97912 | -2.5543 | -3.8414 | 10.526 | 7.4157 | 3.5916 | -0.30029 | 3.892% | -3.892%
2 | 7.517 | 3.6406 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.3617 | 0.97075 | -2.2953 | -5.7 | 10.526 | 7.0808 | 3.4294 | -0.43624 | 5.803% | -5.803%
3 | 7.407 | 3.5874 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8785 | 1.001 | -2.7972 | 0.98918 | -1.3343 | 0.97155 | -2.2531 | -5.6991 | 10.526 | 6.9774 | 3.3793 | -0.42964 | 5.8% | -5.8%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7937 | 0.98922 | -1.3321 | 0.97162 | -2.2496 | -5.699 | 10.526 | 6.9689 | 3.3752 | -0.4291 | 5.8% | -5.8%
5 | 7.563 | 3.6629 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8589 | 0.98844 | -1.3732 | 0.97042 | -2.313 | -5.7003 | 10.526 | 7.124 | 3.4503 | -0.439 | 5.805% | -5.805%
6 | 7.986 | 3.8678 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99643 | -1.6621 | 0.97714 | -2.6596 | -3.8427 | 10.526 | 7.6748 | 3.7171 | -0.31119 | 3.897% | -3.897%
7 | 8.626 | 4.1778 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2832 | 0.99334 | -1.8253 | 0.97239 | -2.9112 | -3.8462 | 10.526 | 8.2889 | 4.0145 | -0.33714 | 3.908% | -3.908%
8 | 9.059 | 4.3875 | 0.9 | Z | moderate sun | 10.526 | 10.5155 | 4 | 1.0112 | -2.3117 | 0.98869 | -3.4582 | 1.0012 | -2.1239 | 0.97891 | -3.2705 | -1.9447 | 10.5155 | 8.8807 | 4.3011 | -0.17828 | 1.968% | -1.968%
9 | 9.181 | 4.4466 | 0.9 | Z | moderate sun | 10.526 | 10.4102 | 4 | 1.0106 | -2.344 | 0.98776 | -3.5078 | 1.0006 | -2.1558 | 0.97798 | -3.3196 | -1.9451 | 10.4102 | 9.0002 | 4.359 | -0.18079 | 1.969% | -1.969%
10 | 9.23 | 4.4703 | 0.9 | Z | moderate sun | 10.526 | 10.1892 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1686 | 0.97761 | -3.3393 | -1.9452 | 10.1892 | 9.0482 | 4.3822 | -0.1818 | 1.97% | -1.97%
11 | 9.261 | 4.4853 | 0.9 | Z | moderate sun | 10.526 | 9.9576 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.1767 | 0.97737 | -3.3518 | -1.9453 | 9.9576 | 9.0786 | 4.3969 | -0.18244 | 1.97% | -1.97%
12 | 9.292 | 4.5003 | 0.9 | Z | moderate sun | 10.526 | 9.8313 | 4 | 1.0101 | -2.3735 | 0.98691 | -3.5529 | 1.0001 | -2.1848 | 0.97714 | -3.3643 | -1.9454 | 9.8313 | 9.1089 | 4.4117 | -0.18308 | 1.97% | -1.97%
13 | 9.322 | 4.5149 | 0.9 | Z | moderate sun | 10.526 | 9.9681 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5652 | 0.99992 | -2.1927 | 0.97691 | -3.3764 | -1.9455 | 9.9681 | 9.1383 | 4.4259 | -0.18369 | 1.971% | -1.971%
14 | 9.338 | 4.5226 | 0.9 | Z | moderate sun | 10.526 | 10.0313 | 4 | 1.0098 | -2.3857 | 0.98656 | -3.5717 | 0.99984 | -2.1969 | 0.97679 | -3.3829 | -1.9456 | 10.0313 | 9.154 | 4.4335 | -0.18402 | 1.971% | -1.971%
15 | 9.404 | 4.5546 | 0.9 | Z | moderate sun | 10.526 | 10.2944 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2142 | 0.97628 | -3.4096 | -1.9457 | 10.2944 | 9.2186 | 4.4648 | -0.18538 | 1.971% | -1.971%
16 | 9.594 | 4.6466 | 0.9 | Z | moderate sun | 10.526 | 10.4734 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.264 | 0.97483 | -3.4865 | -1.9463 | 10.4734 | 9.4047 | 4.5549 | -0.18931 | 1.973% | -1.973%
17 | 9.883 | 4.7866 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3401 | 0.9726 | -3.6041 | -1.9471 | 10.526 | 9.6877 | 4.692 | -0.19529 | 1.976% | -1.976%
18 | 10 | 4.8432 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.371 | 0.97169 | -3.6518 | -1.9475 | 10.526 | 9.8023 | 4.7475 | -0.19772 | 1.977% | -1.977%
19 | 9.966 | 4.8268 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.362 | 0.97196 | -3.6379 | -1.9474 | 10.526 | 9.769 | 4.7313 | -0.19701 | 1.977% | -1.977%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3332 | 0.9728 | -3.5935 | -1.9471 | 10.526 | 9.6622 | 4.6796 | -0.19475 | 1.976% | -1.976%
21 | 9.62 | 4.6592 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.2709 | 0.97463 | -3.4971 | -1.9463 | 10.526 | 9.4302 | 4.5672 | -0.18984 | 1.973% | -1.973%
22 | 9.139 | 4.4262 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0108 | -2.3329 | 0.98808 | -3.4907 | 1.0008 | -2.1448 | 0.9783 | -3.3026 | -1.945 | 10.526 | 8.9591 | 4.3391 | -0.17993 | 1.969% | -1.969%
23 | 8.547 | 4.1395 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2514 | 0.99372 | -1.8051 | 0.97298 | -2.88 | -3.8458 | 10.526 | 8.2131 | 3.9778 | -0.33392 | 3.907% | -3.907%
24 | 8.047 | 3.8973 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.6776 | 0.97669 | -2.6835 | -3.8431 | 10.526 | 7.7333 | 3.7454 | -0.31365 | 3.898% | -3.898%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9195 | 0.99771 | -1.5936 | 0.97912 | -2.5543 | -3.8414 | 10.526 | 7.4157 | 3.5916 | -0.30029 | 3.892% | -3.892%
2 | 7.517 | 3.6406 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.3617 | 0.97075 | -2.2953 | -5.7 | 10.526 | 7.0808 | 3.4294 | -0.43624 | 5.803% | -5.803%
3 | 7.407 | 3.5874 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8785 | 1.001 | -2.7972 | 0.98918 | -1.3343 | 0.97155 | -2.2531 | -5.6991 | 10.526 | 6.9774 | 3.3793 | -0.42964 | 5.8% | -5.8%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7937 | 0.98922 | -1.3321 | 0.97162 | -2.2496 | -5.699 | 10.526 | 6.9689 | 3.3752 | -0.4291 | 5.8% | -5.8%
5 | 7.563 | 3.6629 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8589 | 0.98844 | -1.3732 | 0.97042 | -2.313 | -5.7003 | 10.526 | 7.124 | 3.4503 | -0.439 | 5.805% | -5.805%
6 | 7.986 | 3.8678 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99643 | -1.6621 | 0.97714 | -2.6596 | -3.8427 | 10.526 | 7.6748 | 3.7171 | -0.31119 | 3.897% | -3.897%
7 | 8.626 | 4.1778 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2832 | 0.99334 | -1.8253 | 0.97239 | -2.9112 | -3.8462 | 10.526 | 8.2889 | 4.0145 | -0.33714 | 3.908% | -3.908%
8 | 9.059 | 4.3875 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0112 | -2.3117 | 0.98869 | -3.4582 | 1.0012 | -2.1239 | 0.97891 | -3.2705 | -1.9447 | 10.526 | 8.8807 | 4.3011 | -0.17828 | 1.968% | -1.968%
9 | 9.181 | 4.4466 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0106 | -2.344 | 0.98776 | -3.5078 | 1.0006 | -2.1558 | 0.97798 | -3.3196 | -1.9451 | 10.526 | 9.0002 | 4.359 | -0.18079 | 1.969% | -1.969%
10 | 9.23 | 4.4703 | 0.9 | Z | cloudy | 10.526 | 10.5155 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1686 | 0.97761 | -3.3393 | -1.9452 | 10.5155 | 9.0482 | 4.3822 | -0.1818 | 1.97% | -1.97%
11 | 9.261 | 4.4853 | 0.9 | Z | cloudy | 10.526 | 10.4839 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.1767 | 0.97737 | -3.3518 | -1.9453 | 10.4839 | 9.0786 | 4.3969 | -0.18244 | 1.97% | -1.97%
12 | 9.292 | 4.5003 | 0.9 | Z | cloudy | 10.526 | 10.4523 | 4 | 1.0101 | -2.3735 | 0.98691 | -3.5529 | 1.0001 | -2.1848 | 0.97714 | -3.3643 | -1.9454 | 10.4523 | 9.1089 | 4.4117 | -0.18308 | 1.97% | -1.97%
13 | 9.322 | 4.5149 | 0.9 | Z | cloudy | 10.526 | 10.4523 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5652 | 0.99992 | -2.1927 | 0.97691 | -3.3764 | -1.9455 | 10.4523 | 9.1383 | 4.4259 | -0.18369 | 1.971% | -1.971%
14 | 9.338 | 4.5226 | 0.9 | Z | cloudy | 10.526 | 10.4734 | 4 | 1.0098 | -2.3857 | 0.98656 | -3.5717 | 0.99984 | -2.1969 | 0.97679 | -3.3829 | -1.9456 | 10.4734 | 9.154 | 4.4335 | -0.18402 | 1.971% | -1.971%
15 | 9.404 | 4.5546 | 0.9 | Z | cloudy | 10.526 | 10.5049 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2142 | 0.97628 | -3.4096 | -1.9457 | 10.5049 | 9.2186 | 4.4648 | -0.18538 | 1.971% | -1.971%
16 | 9.594 | 4.6466 | 0.9 | Z | cloudy | 10.526 | 10.5155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.264 | 0.97483 | -3.4865 | -1.9463 | 10.5155 | 9.4047 | 4.5549 | -0.18931 | 1.973% | -1.973%
17 | 9.883 | 4.7866 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3401 | 0.9726 | -3.6041 | -1.9471 | 10.526 | 9.6877 | 4.692 | -0.19529 | 1.976% | -1.976%
18 | 10 | 4.8432 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.371 | 0.97169 | -3.6518 | -1.9475 | 10.526 | 9.8023 | 4.7475 | -0.19772 | 1.977% | -1.977%
19 | 9.966 | 4.8268 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.362 | 0.97196 | -3.6379 | -1.9474 | 10.526 | 9.769 | 4.7313 | -0.19701 | 1.977% | -1.977%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3332 | 0.9728 | -3.5935 | -1.9471 | 10.526 | 9.6622 | 4.6796 | -0.19475 | 1.976% | -1.976%
21 | 9.62 | 4.6592 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.2709 | 0.97463 | -3.4971 | -1.9463 | 10.526 | 9.4302 | 4.5672 | -0.18984 | 1.973% | -1.973%
22 | 9.139 | 4.4262 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0108 | -2.3329 | 0.98808 | -3.4907 | 1.0008 | -2.1448 | 0.9783 | -3.3026 | -1.945 | 10.526 | 8.9591 | 4.3391 | -0.17993 | 1.969% | -1.969%
23 | 8.547 | 4.1395 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2514 | 0.99372 | -1.8051 | 0.97298 | -2.88 | -3.8458 | 10.526 | 8.2131 | 3.9778 | -0.33392 | 3.907% | -3.907%
24 | 8.047 | 3.8973 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.6776 | 0.97669 | -2.6835 | -3.8431 | 10.526 | 7.7333 | 3.7454 | -0.31365 | 3.898% | -3.898%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.99874 | -2.9195 | 0.99874 | -2.9195 | 0.97 | -2.2877 | 0.97 | -2.2877 | -3.6536 | 5.263 | 7.2782 | 3.525 | -0.43776 | 5.673% | -5.673%
2 | 7.517 | 3.6406 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -2.8407 | 1.0002 | -2.8407 | 0.97 | -2.1805 | 0.97 | -2.1805 | -3.8318 | 5.263 | 7.0698 | 3.424 | -0.44723 | 5.95% | -5.95%
3 | 7.407 | 3.5874 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.1215 | 0.97 | -2.1215 | -3.9296 | 5.263 | 6.9551 | 3.3685 | -0.45191 | 6.101% | -6.101%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0011 | -2.7937 | 1.0011 | -2.7937 | 0.97 | -2.1167 | 0.97 | -2.1167 | -3.9375 | 5.263 | 6.9457 | 3.364 | -0.45227 | 6.113% | -6.113%
5 | 7.563 | 3.6629 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.99987 | -2.8589 | 0.99987 | -2.8589 | 0.97 | -2.2052 | 0.97 | -2.2052 | -3.7907 | 5.263 | 7.1178 | 3.4473 | -0.44516 | 5.886% | -5.886%
6 | 7.986 | 3.8678 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.4344 | 0.97 | -2.4344 | -3.4094 | 5.263 | 7.5631 | 3.663 | -0.42287 | 5.295% | -5.295%
7 | 8.626 | 4.1778 | 0.9 | Z | very sunny | 5.263 | 5.2525 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.7877 | 0.97 | -2.7877 | -2.8188 | 5.2525 | 8.2482 | 3.9948 | -0.37776 | 4.379% | -4.379%
8 | 9.059 | 4.3875 | 0.9 | Z | very sunny | 5.263 | 5.1156 | 5 | 0.98869 | -3.4582 | 0.98869 | -3.4582 | 0.97 | -3.0314 | 0.97 | -3.0314 | -2.4095 | 5.1156 | 8.7198 | 4.2232 | -0.33918 | 3.744% | -3.744%
9 | 9.181 | 4.4466 | 0.9 | Z | very sunny | 5.263 | 4.7051 | 5 | 0.98776 | -3.5078 | 0.98776 | -3.5078 | 0.97 | -3.1008 | 0.97 | -3.1008 | -2.2927 | 4.7051 | 8.8539 | 4.2881 | -0.3271 | 3.563% | -3.563%
10 | 9.23 | 4.4703 | 0.9 | Z | very sunny | 5.263 | 4.142 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.1287 | 0.97 | -3.1287 | -2.2456 | 4.142 | 8.9079 | 4.3143 | -0.3221 | 3.49% | -3.49%
11 | 9.261 | 4.4853 | 0.9 | Z | very sunny | 5.263 | 3.5736 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.1464 | 0.97 | -3.1464 | -2.2158 | 3.5736 | 8.9421 | 4.3309 | -0.31889 | 3.443% | -3.443%
12 | 9.292 | 4.5003 | 0.9 | Z | very sunny | 5.263 | 3.2578 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.1641 | 0.97 | -3.1641 | -2.1859 | 3.2578 | 8.9764 | 4.3474 | -0.31565 | 3.397% | -3.397%
13 | 9.322 | 4.5149 | 0.9 | Z | very sunny | 5.263 | 3.3525 | 5 | 0.98668 | -3.5652 | 0.98668 | -3.5652 | 0.97 | -3.1813 | 0.97 | -3.1813 | -2.1569 | 3.3525 | 9.0095 | 4.3635 | -0.31248 | 3.352% | -3.352%
14 | 9.338 | 4.5226 | 0.9 | Z | very sunny | 5.263 | 3.5052 | 5 | 0.98656 | -3.5717 | 0.98656 | -3.5717 | 0.97 | -3.1905 | 0.97 | -3.1905 | -2.1414 | 3.5052 | 9.0272 | 4.3721 | -0.31077 | 3.328% | -3.328%
15 | 9.404 | 4.5546 | 0.9 | Z | very sunny | 5.263 | 3.942 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.2283 | 0.97 | -3.2283 | -2.0775 | 3.942 | 9.1004 | 4.4075 | -0.30363 | 3.229% | -3.229%
16 | 9.594 | 4.6466 | 0.9 | Z | very sunny | 5.263 | 4.4578 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.3379 | 0.97 | -3.3379 | -1.8924 | 4.4578 | 9.3118 | 4.5099 | -0.28219 | 2.941% | -2.941%
17 | 9.883 | 4.7866 | 0.9 | Z | very sunny | 5.263 | 4.9209 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.6076 | 4.9209 | 9.636 | 4.6669 | -0.24698 | 2.499% | -2.499%
18 | 10 | 4.8432 | 0.9 | Z | very sunny | 5.263 | 5.1893 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.5746 | 0.97 | -3.5746 | -1.4912 | 5.1893 | 9.7682 | 4.7309 | -0.23183 | 2.318% | -2.318%
19 | 9.966 | 4.8268 | 0.9 | Z | very sunny | 5.263 | 5.2577 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.5546 | 0.97 | -3.5546 | -1.5251 | 5.2577 | 9.7297 | 4.7123 | -0.23628 | 2.371% | -2.371%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.4908 | 0.97 | -3.4908 | -1.6334 | 5.263 | 9.6067 | 4.6527 | -0.25028 | 2.539% | -2.539%
21 | 9.62 | 4.6592 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.3529 | 0.97 | -3.3529 | -1.8669 | 5.263 | 9.3408 | 4.524 | -0.27915 | 2.902% | -2.902%
22 | 9.139 | 4.4262 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.98808 | -3.4907 | 0.98808 | -3.4907 | 0.97 | -3.0769 | 0.97 | -3.0769 | -2.333 | 5.263 | 8.8077 | 4.2658 | -0.33132 | 3.625% | -3.625%
23 | 8.547 | 4.1395 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.99256 | -3.2514 | 0.99256 | -3.2514 | 0.97 | -2.7437 | 0.97 | -2.7437 | -2.8927 | 5.263 | 8.1629 | 3.9535 | -0.38408 | 4.494% | -4.494%
24 | 8.047 | 3.8973 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.9963 | -3.0511 | 0.9963 | -3.0511 | 0.97 | -2.4678 | 0.97 | -2.4678 | -3.3539 | 5.263 | 7.6278 | 3.6943 | -0.41916 | 5.209% | -5.209%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99875 | -2.9195 | 0.99875 | -2.9195 | 0.97 | -2.2877 | 0.97 | -2.2877 | -3.6536 | 5.263 | 7.2782 | 3.525 | -0.43777 | 5.674% | -5.674%
2 | 7.517 | 3.6406 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -2.8407 | 1.0002 | -2.8407 | 0.97 | -2.1805 | 0.97 | -2.1805 | -3.8318 | 5.263 | 7.0698 | 3.424 | -0.44723 | 5.95% | -5.95%
3 | 7.407 | 3.5874 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.1215 | 0.97 | -2.1215 | -3.9296 | 5.263 | 6.9551 | 3.3685 | -0.45191 | 6.101% | -6.101%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0011 | -2.7937 | 1.0011 | -2.7937 | 0.97 | -2.1167 | 0.97 | -2.1167 | -3.9375 | 5.263 | 6.9457 | 3.364 | -0.45227 | 6.113% | -6.113%
5 | 7.563 | 3.6629 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99987 | -2.8589 | 0.99987 | -2.8589 | 0.97 | -2.2052 | 0.97 | -2.2052 | -3.7907 | 5.263 | 7.1178 | 3.4473 | -0.44516 | 5.886% | -5.886%
6 | 7.986 | 3.8678 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.4344 | 0.97 | -2.4344 | -3.4094 | 5.263 | 7.5631 | 3.663 | -0.42287 | 5.295% | -5.295%
7 | 8.626 | 4.1778 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.7877 | 0.97 | -2.7877 | -2.8188 | 5.263 | 8.2482 | 3.9948 | -0.37776 | 4.379% | -4.379%
8 | 9.059 | 4.3875 | 0.9 | Z | moderate sun | 5.263 | 5.2577 | 5 | 0.98869 | -3.4582 | 0.98869 | -3.4582 | 0.97 | -3.0314 | 0.97 | -3.0314 | -2.4095 | 5.2577 | 8.7198 | 4.2232 | -0.33918 | 3.744% | -3.744%
9 | 9.181 | 4.4466 | 0.9 | Z | moderate sun | 5.263 | 5.2051 | 5 | 0.98776 | -3.5078 | 0.98776 | -3.5078 | 0.97 | -3.1008 | 0.97 | -3.1008 | -2.2927 | 5.2051 | 8.8539 | 4.2881 | -0.3271 | 3.563% | -3.563%
10 | 9.23 | 4.4703 | 0.9 | Z | moderate sun | 5.263 | 5.0946 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.1287 | 0.97 | -3.1287 | -2.2456 | 5.0946 | 8.9079 | 4.3143 | -0.3221 | 3.49% | -3.49%
11 | 9.261 | 4.4853 | 0.9 | Z | moderate sun | 5.263 | 4.9788 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.1464 | 0.97 | -3.1464 | -2.2158 | 4.9788 | 8.9421 | 4.3309 | -0.31889 | 3.443% | -3.443%
12 | 9.292 | 4.5003 | 0.9 | Z | moderate sun | 5.263 | 4.9156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.1641 | 0.97 | -3.1641 | -2.1859 | 4.9156 | 8.9764 | 4.3474 | -0.31565 | 3.397% | -3.397%
13 | 9.322 | 4.5149 | 0.9 | Z | moderate sun | 5.263 | 4.9841 | 5 | 0.98668 | -3.5652 | 0.98668 | -3.5652 | 0.97 | -3.1813 | 0.97 | -3.1813 | -2.1569 | 4.9841 | 9.0095 | 4.3635 | -0.31248 | 3.352% | -3.352%
14 | 9.338 | 4.5226 | 0.9 | Z | moderate sun | 5.263 | 5.0156 | 5 | 0.98656 | -3.5717 | 0.98656 | -3.5717 | 0.97 | -3.1905 | 0.97 | -3.1905 | -2.1414 | 5.0156 | 9.0272 | 4.3721 | -0.31077 | 3.328% | -3.328%
15 | 9.404 | 4.5546 | 0.9 | Z | moderate sun | 5.263 | 5.1472 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.2283 | 0.97 | -3.2283 | -2.0775 | 5.1472 | 9.1004 | 4.4075 | -0.30363 | 3.229% | -3.229%
16 | 9.594 | 4.6466 | 0.9 | Z | moderate sun | 5.263 | 5.2367 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.3379 | 0.97 | -3.3379 | -1.8924 | 5.2367 | 9.3118 | 4.5099 | -0.28219 | 2.941% | -2.941%
17 | 9.883 | 4.7866 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.6076 | 5.263 | 9.636 | 4.6669 | -0.24698 | 2.499% | -2.499%
18 | 10 | 4.8432 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.5746 | 0.97 | -3.5746 | -1.4912 | 5.263 | 9.7682 | 4.7309 | -0.23183 | 2.318% | -2.318%
19 | 9.966 | 4.8268 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.5546 | 0.97 | -3.5546 | -1.5251 | 5.263 | 9.7297 | 4.7123 | -0.23628 | 2.371% | -2.371%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.4908 | 0.97 | -3.4908 | -1.6334 | 5.263 | 9.6067 | 4.6527 | -0.25028 | 2.539% | -2.539%
21 | 9.62 | 4.6592 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.3529 | 0.97 | -3.3529 | -1.8669 | 5.263 | 9.3408 | 4.524 | -0.27915 | 2.902% | -2.902%
22 | 9.139 | 4.4262 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.98808 | -3.4907 | 0.98808 | -3.4907 | 0.97 | -3.0769 | 0.97 | -3.0769 | -2.333 | 5.263 | 8.8077 | 4.2658 | -0.33132 | 3.625% | -3.625%
23 | 8.547 | 4.1395 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99256 | -3.2514 | 0.99256 | -3.2514 | 0.97 | -2.7437 | 0.97 | -2.7437 | -2.8927 | 5.263 | 8.1629 | 3.9535 | -0.38408 | 4.494% | -4.494%
24 | 8.047 | 3.8973 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.9963 | -3.0511 | 0.9963 | -3.0511 | 0.97 | -2.4678 | 0.97 | -2.4678 | -3.3539 | 5.263 | 7.6278 | 3.6943 | -0.41916 | 5.209% | -5.209%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99875 | -2.9195 | 0.99875 | -2.9195 | 0.97 | -2.2877 | 0.97 | -2.2877 | -3.6536 | 5.263 | 7.2782 | 3.525 | -0.43777 | 5.674% | -5.674%
2 | 7.517 | 3.6406 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -2.8407 | 1.0002 | -2.8407 | 0.97 | -2.1805 | 0.97 | -2.1805 | -3.8318 | 5.263 | 7.0698 | 3.424 | -0.44723 | 5.95% | -5.95%
3 | 7.407 | 3.5874 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.1215 | 0.97 | -2.1215 | -3.9296 | 5.263 | 6.9551 | 3.3685 | -0.45191 | 6.101% | -6.101%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0011 | -2.7937 | 1.0011 | -2.7937 | 0.97 | -2.1167 | 0.97 | -2.1167 | -3.9375 | 5.263 | 6.9457 | 3.364 | -0.45227 | 6.113% | -6.113%
5 | 7.563 | 3.6629 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99987 | -2.8589 | 0.99987 | -2.8589 | 0.97 | -2.2052 | 0.97 | -2.2052 | -3.7907 | 5.263 | 7.1178 | 3.4473 | -0.44516 | 5.886% | -5.886%
6 | 7.986 | 3.8678 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.4344 | 0.97 | -2.4344 | -3.4094 | 5.263 | 7.5631 | 3.663 | -0.42287 | 5.295% | -5.295%
7 | 8.626 | 4.1778 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.7877 | 0.97 | -2.7877 | -2.8188 | 5.263 | 8.2482 | 3.9948 | -0.37776 | 4.379% | -4.379%
8 | 9.059 | 4.3875 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98869 | -3.4582 | 0.98869 | -3.4582 | 0.97 | -3.0314 | 0.97 | -3.0314 | -2.4095 | 5.263 | 8.7198 | 4.2232 | -0.33918 | 3.744% | -3.744%
9 | 9.181 | 4.4466 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98776 | -3.5078 | 0.98776 | -3.5078 | 0.97 | -3.1008 | 0.97 | -3.1008 | -2.2927 | 5.263 | 8.8539 | 4.2881 | -0.3271 | 3.563% | -3.563%
10 | 9.23 | 4.4703 | 0.9 | Z | cloudy | 5.263 | 5.2577 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.1287 | 0.97 | -3.1287 | -2.2456 | 5.2577 | 8.9079 | 4.3143 | -0.3221 | 3.49% | -3.49%
11 | 9.261 | 4.4853 | 0.9 | Z | cloudy | 5.263 | 5.2419 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.1464 | 0.97 | -3.1464 | -2.2158 | 5.2419 | 8.9421 | 4.3309 | -0.31889 | 3.443% | -3.443%
12 | 9.292 | 4.5003 | 0.9 | Z | cloudy | 5.263 | 5.2262 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.1641 | 0.97 | -3.1641 | -2.1859 | 5.2262 | 8.9764 | 4.3474 | -0.31565 | 3.397% | -3.397%
13 | 9.322 | 4.5149 | 0.9 | Z | cloudy | 5.263 | 5.2262 | 5 | 0.98668 | -3.5652 | 0.98668 | -3.5652 | 0.97 | -3.1813 | 0.97 | -3.1813 | -2.1569 | 5.2262 | 9.0095 | 4.3635 | -0.31248 | 3.352% | -3.352%
14 | 9.338 | 4.5226 | 0.9 | Z | cloudy | 5.263 | 5.2367 | 5 | 0.98656 | -3.5717 | 0.98656 | -3.5717 | 0.97 | -3.1905 | 0.97 | -3.1905 | -2.1414 | 5.2367 | 9.0272 | 4.3721 | -0.31077 | 3.328% | -3.328%
15 | 9.404 | 4.5546 | 0.9 | Z | cloudy | 5.263 | 5.2525 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.2283 | 0.97 | -3.2283 | -2.0775 | 5.2525 | 9.1004 | 4.4075 | -0.30363 | 3.229% | -3.229%
16 | 9.594 | 4.6466 | 0.9 | Z | cloudy | 5.263 | 5.2577 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.3379 | 0.97 | -3.3379 | -1.8924 | 5.2577 | 9.3118 | 4.5099 | -0.28219 | 2.941% | -2.941%
17 | 9.883 | 4.7866 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.6076 | 5.263 | 9.636 | 4.6669 | -0.24698 | 2.499% | -2.499%
18 | 10 | 4.8432 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.5746 | 0.97 | -3.5746 | -1.4912 | 5.263 | 9.7682 | 4.7309 | -0.23183 | 2.318% | -2.318%
19 | 9.966 | 4.8268 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.5546 | 0.97 | -3.5546 | -1.5251 | 5.263 | 9.7297 | 4.7123 | -0.23628 | 2.371% | -2.371%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.4908 | 0.97 | -3.4908 | -1.6334 | 5.263 | 9.6067 | 4.6527 | -0.25028 | 2.539% | -2.539%
21 | 9.62 | 4.6592 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.3529 | 0.97 | -3.3529 | -1.8669 | 5.263 | 9.3408 | 4.524 | -0.27915 | 2.902% | -2.902%
22 | 9.139 | 4.4262 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.98808 | -3.4907 | 0.98808 | -3.4907 | 0.97 | -3.0769 | 0.97 | -3.0769 | -2.333 | 5.263 | 8.8077 | 4.2658 | -0.33132 | 3.625% | -3.625%
23 | 8.547 | 4.1395 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99256 | -3.2514 | 0.99256 | -3.2514 | 0.97 | -2.7437 | 0.97 | -2.7437 | -2.8927 | 5.263 | 8.1629 | 3.9535 | -0.38408 | 4.494% | -4.494%
24 | 8.047 | 3.8973 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.9963 | -3.0511 | 0.9963 | -3.0511 | 0.97 | -2.4678 | 0.97 | -2.4678 | -3.3539 | 5.263 | 7.6278 | 3.6943 | -0.41916 | 5.209% | -5.209%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.99875 | -2.9195 | 0.99875 | -2.9195 | 0.97 | -2.2877 | 0.97 | -2.2877 | -3.6536 | 10.526 | 7.2782 | 3.525 | -0.43777 | 5.674% | -5.674%
2 | 7.517 | 3.6406 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -2.8407 | 1.0002 | -2.8407 | 0.97 | -2.1805 | 0.97 | -2.1805 | -3.8318 | 10.526 | 7.0698 | 3.424 | -0.44723 | 5.95% | -5.95%
3 | 7.407 | 3.5874 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.1215 | 0.97 | -2.1215 | -3.9296 | 10.526 | 6.9551 | 3.3685 | -0.45191 | 6.101% | -6.101%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0011 | -2.7937 | 1.0011 | -2.7937 | 0.97 | -2.1167 | 0.97 | -2.1167 | -3.9375 | 10.526 | 6.9457 | 3.364 | -0.45227 | 6.113% | -6.113%
5 | 7.563 | 3.6629 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.99987 | -2.8589 | 0.99987 | -2.8589 | 0.97 | -2.2052 | 0.97 | -2.2052 | -3.7907 | 10.526 | 7.1178 | 3.4473 | -0.44516 | 5.886% | -5.886%
6 | 7.986 | 3.8678 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.4344 | 0.97 | -2.4344 | -3.4094 | 10.526 | 7.5631 | 3.663 | -0.42287 | 5.295% | -5.295%
7 | 8.626 | 4.1778 | 0.9 | Z | very sunny | 10.526 | 10.5049 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.7877 | 0.97 | -2.7877 | -2.8188 | 10.5049 | 8.2482 | 3.9948 | -0.37776 | 4.379% | -4.379%
8 | 9.059 | 4.3875 | 0.9 | Z | very sunny | 10.526 | 10.2313 | 5 | 0.98869 | -3.4582 | 0.98869 | -3.4582 | 0.97 | -3.0314 | 0.97 | -3.0314 | -2.4095 | 10.2313 | 8.7198 | 4.2232 | -0.33918 | 3.744% | -3.744%
9 | 9.181 | 4.4466 | 0.9 | Z | very sunny | 10.526 | 9.4102 | 5 | 0.98776 | -3.5078 | 0.98776 | -3.5078 | 0.97 | -3.1008 | 0.97 | -3.1008 | -2.2927 | 9.4102 | 8.8539 | 4.2881 | -0.3271 | 3.563% | -3.563%
10 | 9.23 | 4.4703 | 0.9 | Z | very sunny | 10.526 | 8.284 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.1287 | 0.97 | -3.1287 | -2.2456 | 8.284 | 8.9079 | 4.3143 | -0.3221 | 3.49% | -3.49%
11 | 9.261 | 4.4853 | 0.9 | Z | very sunny | 10.526 | 7.1472 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.1464 | 0.97 | -3.1464 | -2.2158 | 7.1472 | 8.9421 | 4.3309 | -0.31889 | 3.443% | -3.443%
12 | 9.292 | 4.5003 | 0.9 | Z | very sunny | 10.526 | 6.5156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.1641 | 0.97 | -3.1641 | -2.1859 | 6.5156 | 8.9764 | 4.3474 | -0.31565 | 3.397% | -3.397%
13 | 9.322 | 4.5149 | 0.9 | Z | very sunny | 10.526 | 6.7051 | 5 | 0.98668 | -3.5652 | 0.98668 | -3.5652 | 0.97 | -3.1813 | 0.97 | -3.1813 | -2.1569 | 6.7051 | 9.0095 | 4.3635 | -0.31248 | 3.352% | -3.352%
14 | 9.338 | 4.5226 | 0.9 | Z | very sunny | 10.526 | 7.0103 | 5 | 0.98656 | -3.5717 | 0.98656 | -3.5717 | 0.97 | -3.1905 | 0.97 | -3.1905 | -2.1414 | 7.0103 | 9.0272 | 4.3721 | -0.31077 | 3.328% | -3.328%
15 | 9.404 | 4.5546 | 0.9 | Z | very sunny | 10.526 | 7.884 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.2283 | 0.97 | -3.2283 | -2.0775 | 7.884 | 9.1004 | 4.4075 | -0.30363 | 3.229% | -3.229%
16 | 9.594 | 4.6466 | 0.9 | Z | very sunny | 10.526 | 8.9155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.3379 | 0.97 | -3.3379 | -1.8924 | 8.9155 | 9.3118 | 4.5099 | -0.28219 | 2.941% | -2.941%
17 | 9.883 | 4.7866 | 0.9 | Z | very sunny | 10.526 | 9.8418 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.6076 | 9.8418 | 9.636 | 4.6669 | -0.24698 | 2.499% | -2.499%
18 | 10 | 4.8432 | 0.9 | Z | very sunny | 10.526 | 10.3786 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.5746 | 0.97 | -3.5746 | -1.4912 | 10.3786 | 9.7682 | 4.7309 | -0.23183 | 2.318% | -2.318%
19 | 9.966 | 4.8268 | 0.9 | Z | very sunny | 10.526 | 10.5155 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.5546 | 0.97 | -3.5546 | -1.5251 | 10.5155 | 9.7297 | 4.7123 | -0.23628 | 2.371% | -2.371%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.4908 | 0.97 | -3.4908 | -1.6334 | 10.526 | 9.6067 | 4.6527 | -0.25028 | 2.539% | -2.539%
21 | 9.62 | 4.6592 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.3529 | 0.97 | -3.3529 | -1.8669 | 10.526 | 9.3408 | 4.524 | -0.27915 | 2.902% | -2.902%
22 | 9.139 | 4.4262 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.98808 | -3.4907 | 0.98808 | -3.4907 | 0.97 | -3.0769 | 0.97 | -3.0769 | -2.333 | 10.526 | 8.8077 | 4.2658 | -0.33132 | 3.625% | -3.625%
23 | 8.547 | 4.1395 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.99256 | -3.2514 | 0.99256 | -3.2514 | 0.97 | -2.7437 | 0.97 | -2.7437 | -2.8927 | 10.526 | 8.1629 | 3.9535 | -0.38408 | 4.494% | -4.494%
24 | 8.047 | 3.8973 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.9963 | -3.0511 | 0.9963 | -3.0511 | 0.97 | -2.4678 | 0.97 | -2.4678 | -3.3539 | 10.526 | 7.6278 | 3.6943 | -0.41916 | 5.209% | -5.209%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99875 | -2.9195 | 0.99875 | -2.9195 | 0.97 | -2.2877 | 0.97 | -2.2877 | -3.6536 | 10.526 | 7.2782 | 3.525 | -0.43777 | 5.674% | -5.674%
2 | 7.517 | 3.6406 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -2.8407 | 1.0002 | -2.8407 | 0.97 | -2.1805 | 0.97 | -2.1805 | -3.8318 | 10.526 | 7.0698 | 3.424 | -0.44723 | 5.95% | -5.95%
3 | 7.407 | 3.5874 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.1215 | 0.97 | -2.1215 | -3.9296 | 10.526 | 6.9551 | 3.3685 | -0.45191 | 6.101% | -6.101%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0011 | -2.7937 | 1.0011 | -2.7937 | 0.97 | -2.1167 | 0.97 | -2.1167 | -3.9375 | 10.526 | 6.9457 | 3.364 | -0.45227 | 6.113% | -6.113%
5 | 7.563 | 3.6629 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99987 | -2.8589 | 0.99987 | -2.8589 | 0.97 | -2.2052 | 0.97 | -2.2052 | -3.7907 | 10.526 | 7.1178 | 3.4473 | -0.44516 | 5.886% | -5.886%
6 | 7.986 | 3.8678 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.4344 | 0.97 | -2.4344 | -3.4094 | 10.526 | 7.5631 | 3.663 | -0.42287 | 5.295% | -5.295%
7 | 8.626 | 4.1778 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.7877 | 0.97 | -2.7877 | -2.8188 | 10.526 | 8.2482 | 3.9948 | -0.37776 | 4.379% | -4.379%
8 | 9.059 | 4.3875 | 0.9 | Z | moderate sun | 10.526 | 10.5155 | 5 | 0.98869 | -3.4582 | 0.98869 | -3.4582 | 0.97 | -3.0314 | 0.97 | -3.0314 | -2.4095 | 10.5155 | 8.7198 | 4.2232 | -0.33918 | 3.744% | -3.744%
9 | 9.181 | 4.4466 | 0.9 | Z | moderate sun | 10.526 | 10.4102 | 5 | 0.98776 | -3.5078 | 0.98776 | -3.5078 | 0.97 | -3.1008 | 0.97 | -3.1008 | -2.2927 | 10.4102 | 8.8539 | 4.2881 | -0.3271 | 3.563% | -3.563%
10 | 9.23 | 4.4703 | 0.9 | Z | moderate sun | 10.526 | 10.1892 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.1287 | 0.97 | -3.1287 | -2.2456 | 10.1892 | 8.9079 | 4.3143 | -0.3221 | 3.49% | -3.49%
11 | 9.261 | 4.4853 | 0.9 | Z | moderate sun | 10.526 | 9.9576 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.1464 | 0.97 | -3.1464 | -2.2158 | 9.9576 | 8.9421 | 4.3309 | -0.31889 | 3.443% | -3.443%
12 | 9.292 | 4.5003 | 0.9 | Z | moderate sun | 10.526 | 9.8313 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.1641 | 0.97 | -3.1641 | -2.1859 | 9.8313 | 8.9764 | 4.3474 | -0.31565 | 3.397% | -3.397%
13 | 9.322 | 4.5149 | 0.9 | Z | moderate sun | 10.526 | 9.9681 | 5 | 0.98668 | -3.5652 | 0.98668 | -3.5652 | 0.97 | -3.1813 | 0.97 | -3.1813 | -2.1569 | 9.9681 | 9.0095 | 4.3635 | -0.31248 | 3.352% | -3.352%
14 | 9.338 | 4.5226 | 0.9 | Z | moderate sun | 10.526 | 10.0313 | 5 | 0.98656 | -3.5717 | 0.98656 | -3.5717 | 0.97 | -3.1905 | 0.97 | -3.1905 | -2.1414 | 10.0313 | 9.0272 | 4.3721 | -0.31077 | 3.328% | -3.328%
15 | 9.404 | 4.5546 | 0.9 | Z | moderate sun | 10.526 | 10.2944 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.2283 | 0.97 | -3.2283 | -2.0775 | 10.2944 | 9.1004 | 4.4075 | -0.30363 | 3.229% | -3.229%
16 | 9.594 | 4.6466 | 0.9 | Z | moderate sun | 10.526 | 10.4734 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.3379 | 0.97 | -3.3379 | -1.8924 | 10.4734 | 9.3118 | 4.5099 | -0.28219 | 2.941% | -2.941%
17 | 9.883 | 4.7866 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.6076 | 10.526 | 9.636 | 4.6669 | -0.24698 | 2.499% | -2.499%
18 | 10 | 4.8432 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.5746 | 0.97 | -3.5746 | -1.4912 | 10.526 | 9.7682 | 4.7309 | -0.23183 | 2.318% | -2.318%
19 | 9.966 | 4.8268 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.5546 | 0.97 | -3.5546 | -1.5251 | 10.526 | 9.7297 | 4.7123 | -0.23628 | 2.371% | -2.371%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.4908 | 0.97 | -3.4908 | -1.6334 | 10.526 | 9.6067 | 4.6527 | -0.25028 | 2.539% | -2.539%
21 | 9.62 | 4.6592 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.3529 | 0.97 | -3.3529 | -1.8669 | 10.526 | 9.3408 | 4.524 | -0.27915 | 2.902% | -2.902%
22 | 9.139 | 4.4262 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.98808 | -3.4907 | 0.98808 | -3.4907 | 0.97 | -3.0769 | 0.97 | -3.0769 | -2.333 | 10.526 | 8.8077 | 4.2658 | -0.33132 | 3.625% | -3.625%
23 | 8.547 | 4.1395 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99256 | -3.2514 | 0.99256 | -3.2514 | 0.97 | -2.7437 | 0.97 | -2.7437 | -2.8927 | 10.526 | 8.1629 | 3.9535 | -0.38408 | 4.494% | -4.494%
24 | 8.047 | 3.8973 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.9963 | -3.0511 | 0.9963 | -3.0511 | 0.97 | -2.4678 | 0.97 | -2.4678 | -3.3539 | 10.526 | 7.6278 | 3.6943 | -0.41916 | 5.209% | -5.209%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99875 | -2.9195 | 0.99875 | -2.9195 | 0.97 | -2.2877 | 0.97 | -2.2877 | -3.6536 | 10.526 | 7.2782 | 3.525 | -0.43777 | 5.674% | -5.674%
2 | 7.517 | 3.6406 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -2.8407 | 1.0002 | -2.8407 | 0.97 | -2.1805 | 0.97 | -2.1805 | -3.8318 | 10.526 | 7.0698 | 3.424 | -0.44723 | 5.95% | -5.95%
3 | 7.407 | 3.5874 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.1215 | 0.97 | -2.1215 | -3.9296 | 10.526 | 6.9551 | 3.3685 | -0.45191 | 6.101% | -6.101%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0011 | -2.7937 | 1.0011 | -2.7937 | 0.97 | -2.1167 | 0.97 | -2.1167 | -3.9375 | 10.526 | 6.9457 | 3.364 | -0.45227 | 6.113% | -6.113%
5 | 7.563 | 3.6629 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99987 | -2.8589 | 0.99987 | -2.8589 | 0.97 | -2.2052 | 0.97 | -2.2052 | -3.7907 | 10.526 | 7.1178 | 3.4473 | -0.44516 | 5.886% | -5.886%
6 | 7.986 | 3.8678 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.4344 | 0.97 | -2.4344 | -3.4094 | 10.526 | 7.5631 | 3.663 | -0.42287 | 5.295% | -5.295%
7 | 8.626 | 4.1778 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.7877 | 0.97 | -2.7877 | -2.8188 | 10.526 | 8.2482 | 3.9948 | -0.37776 | 4.379% | -4.379%
8 | 9.059 | 4.3875 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98869 | -3.4582 | 0.98869 | -3.4582 | 0.97 | -3.0314 | 0.97 | -3.0314 | -2.4095 | 10.526 | 8.7198 | 4.2232 | -0.33918 | 3.744% | -3.744%
9 | 9.181 | 4.4466 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98776 | -3.5078 | 0.98776 | -3.5078 | 0.97 | -3.1008 | 0.97 | -3.1008 | -2.2927 | 10.526 | 8.8539 | 4.2881 | -0.3271 | 3.563% | -3.563%
10 | 9.23 | 4.4703 | 0.9 | Z | cloudy | 10.526 | 10.5155 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.1287 | 0.97 | -3.1287 | -2.2456 | 10.5155 | 8.9079 | 4.3143 | -0.3221 | 3.49% | -3.49%
11 | 9.261 | 4.4853 | 0.9 | Z | cloudy | 10.526 | 10.4839 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.1464 | 0.97 | -3.1464 | -2.2158 | 10.4839 | 8.9421 | 4.3309 | -0.31889 | 3.443% | -3.443%
12 | 9.292 | 4.5003 | 0.9 | Z | cloudy | 10.526 | 10.4523 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.1641 | 0.97 | -3.1641 | -2.1859 | 10.4523 | 8.9764 | 4.3474 | -0.31565 | 3.397% | -3.397%
13 | 9.322 | 4.5149 | 0.9 | Z | cloudy | 10.526 | 10.4523 | 5 | 0.98668 | -3.5652 | 0.98668 | -3.5652 | 0.97 | -3.1813 | 0.97 | -3.1813 | -2.1569 | 10.4523 | 9.0095 | 4.3635 | -0.31248 | 3.352% | -3.352%
14 | 9.338 | 4.5226 | 0.9 | Z | cloudy | 10.526 | 10.4734 | 5 | 0.98656 | -3.5717 | 0.98656 | -3.5717 | 0.97 | -3.1905 | 0.97 | -3.1905 | -2.1414 | 10.4734 | 9.0272 | 4.3721 | -0.31077 | 3.328% | -3.328%
15 | 9.404 | 4.5546 | 0.9 | Z | cloudy | 10.526 | 10.5049 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.2283 | 0.97 | -3.2283 | -2.0775 | 10.5049 | 9.1004 | 4.4075 | -0.30363 | 3.229% | -3.229%
16 | 9.594 | 4.6466 | 0.9 | Z | cloudy | 10.526 | 10.5155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.3379 | 0.97 | -3.3379 | -1.8924 | 10.5155 | 9.3118 | 4.5099 | -0.28219 | 2.941% | -2.941%
17 | 9.883 | 4.7866 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.6076 | 10.526 | 9.636 | 4.6669 | -0.24698 | 2.499% | -2.499%
18 | 10 | 4.8432 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.5746 | 0.97 | -3.5746 | -1.4912 | 10.526 | 9.7682 | 4.7309 | -0.23183 | 2.318% | -2.318%
19 | 9.966 | 4.8268 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.5546 | 0.97 | -3.5546 | -1.5251 | 10.526 | 9.7297 | 4.7123 | -0.23628 | 2.371% | -2.371%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.4908 | 0.97 | -3.4908 | -1.6334 | 10.526 | 9.6067 | 4.6527 | -0.25028 | 2.539% | -2.539%
21 | 9.62 | 4.6592 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.3529 | 0.97 | -3.3529 | -1.8669 | 10.526 | 9.3408 | 4.524 | -0.27915 | 2.902% | -2.902%
22 | 9.139 | 4.4262 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.98808 | -3.4907 | 0.98808 | -3.4907 | 0.97 | -3.0769 | 0.97 | -3.0769 | -2.333 | 10.526 | 8.8077 | 4.2658 | -0.33132 | 3.625% | -3.625%
23 | 8.547 | 4.1395 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99256 | -3.2514 | 0.99256 | -3.2514 | 0.97 | -2.7437 | 0.97 | -2.7437 | -2.8927 | 10.526 | 8.1629 | 3.9535 | -0.38408 | 4.494% | -4.494%
24 | 8.047 | 3.8973 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.9963 | -3.0511 | 0.9963 | -3.0511 | 0.97 | -2.4678 | 0.97 | -2.4678 | -3.3539 | 10.526 | 7.6278 | 3.6943 | -0.41916 | 5.209% | -5.209%
1 | 7.716 | 2.5361 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.064 | 1.0267 | -0.91788 | 0.99578 | -2.9256 | -5.263 | 5.263 | 7.5175 | 2.4709 | -0.19852 | 2.573% | -2.573%
2 | 7.517 | 2.4707 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.89104 | 0.99695 | -2.8442 | -5.263 | 5.263 | 7.3237 | 2.4072 | -0.19327 | 2.571% | -2.571%
3 | 7.407 | 2.4346 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.87622 | 0.99759 | -2.7992 | -5.263 | 5.263 | 7.2166 | 2.372 | -0.19042 | 2.571% | -2.571%
4 | 7.398 | 2.4316 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.875 | 0.99764 | -2.7955 | -5.263 | 5.263 | 7.2078 | 2.3691 | -0.19018 | 2.571% | -2.571%
5 | 7.563 | 2.4858 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0269 | -0.89725 | 0.99668 | -2.863 | -5.263 | 5.263 | 7.3685 | 2.4219 | -0.19446 | 2.571% | -2.571%
6 | 7.986 | 2.6249 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.95438 | 0.99418 | -3.0365 | -5.263 | 5.263 | 7.7806 | 2.5573 | -0.20543 | 2.572% | -2.572%
7 | 8.626 | 2.8352 | 0.95 | Z | very sunny | 5.263 | 5.2525 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.042 | 0.99045 | -3.3019 | -5.2525 | 5.2525 | 8.4053 | 2.7627 | -0.22067 | 2.558% | -2.558%
8 | 9.059 | 2.9775 | 0.95 | Z | very sunny | 5.263 | 5.1156 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.025 | -1.1047 | 0.98818 | -3.4858 | -5.1156 | 5.1156 | 8.8333 | 2.9034 | -0.22573 | 2.492% | -2.492%
9 | 9.181 | 3.0176 | 0.95 | Z | very sunny | 5.263 | 4.7051 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6734 | 1.0258 | -1.1325 | 0.98847 | -3.548 | -4.7051 | 4.7051 | 8.9708 | 2.9486 | -0.21019 | 2.289% | -2.289%
10 | 9.23 | 3.0338 | 0.95 | Z | very sunny | 5.263 | 4.142 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.694 | 1.0272 | -1.1544 | 0.98956 | -3.5837 | -4.142 | 4.142 | 9.0441 | 2.9727 | -0.18585 | 2.014% | -2.014%
11 | 9.261 | 3.0439 | 0.95 | Z | very sunny | 5.263 | 3.5736 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0285 | -1.1731 | 0.9907 | -3.6112 | -3.5736 | 3.5736 | 9.0989 | 2.9907 | -0.16214 | 1.751% | -1.751%
12 | 9.292 | 3.0541 | 0.95 | Z | very sunny | 5.263 | 3.2578 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0293 | -1.1859 | 0.9913 | -3.6327 | -3.2578 | 3.2578 | 9.1438 | 3.0054 | -0.14821 | 1.595% | -1.595%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 5.263 | 3.3525 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0291 | -1.1885 | 0.99097 | -3.6438 | -3.3525 | 3.3525 | 9.1707 | 3.0143 | -0.15131 | 1.623% | -1.623%
14 | 9.338 | 3.0693 | 0.95 | Z | very sunny | 5.263 | 3.5052 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0287 | -1.1865 | 0.99049 | -3.6463 | -3.5052 | 3.5052 | 9.1794 | 3.0171 | -0.15859 | 1.698% | -1.698%
15 | 9.404 | 3.0909 | 0.95 | Z | very sunny | 5.263 | 3.942 | 3 | 1.0374 | -1.2888 | 0.99861 | -3.7672 | 1.0274 | -1.1838 | 0.98901 | -3.6622 | -3.942 | 3.942 | 9.2241 | 3.0318 | -0.17994 | 1.913% | -1.913%
16 | 9.594 | 3.1534 | 0.95 | Z | very sunny | 5.263 | 4.4578 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0258 | -1.1958 | 0.98656 | -3.7281 | -4.4578 | 4.4578 | 9.386 | 3.085 | -0.20803 | 2.168% | -2.168%
17 | 9.883 | 3.2484 | 0.95 | Z | very sunny | 5.263 | 4.9209 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.024 | -1.2223 | 0.98358 | -3.8368 | -4.9209 | 4.9209 | 9.6452 | 3.1702 | -0.23783 | 2.406% | -2.406%
18 | 10 | 3.2868 | 0.95 | Z | very sunny | 5.263 | 5.1893 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.2308 | 0.98218 | -3.8788 | -5.1893 | 5.1893 | 9.7459 | 3.2033 | -0.25414 | 2.541% | -2.541%
19 | 9.966 | 3.2757 | 0.95 | Z | very sunny | 5.263 | 5.2577 | 3 | 1.0364 | -1.3669 | 0.99511 | -4.0051 | 1.023 | -1.2243 | 0.98222 | -3.8625 | -5.2577 | 5.2577 | 9.7093 | 3.1913 | -0.25669 | 2.576% | -2.576%
20 | 9.857 | 3.2398 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.9958 | -3.9588 | 1.0232 | -1.2092 | 0.98288 | -3.8163 | -5.263 | 5.263 | 9.6029 | 3.1563 | -0.25411 | 2.578% | -2.578%
21 | 9.62 | 3.1619 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1767 | 0.98433 | -3.7164 | -5.263 | 5.263 | 9.3721 | 3.0805 | -0.24793 | 2.577% | -2.577%
22 | 9.139 | 3.0038 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.111 | 0.98727 | -3.5147 | -5.263 | 5.263 | 8.9036 | 2.9265 | -0.2354 | 2.576% | -2.576%
23 | 8.547 | 2.8093 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0304 | 0.99084 | -3.2682 | -5.263 | 5.263 | 8.327 | 2.737 | -0.22 | 2.574% | -2.574%
24 | 8.047 | 2.6449 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.96263 | 0.99382 | -3.0616 | -5.263 | 5.263 | 7.84 | 2.5769 | -0.20702 | 2.573% | -2.573%
1 | 7.716 | 2.5361 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0267 | -0.91789 | 0.99578 | -2.9256 | -5.263 | 5.263 | 7.5176 | 2.4709 | -0.19843 | 2.572% | -2.572%
2 | 7.517 | 2.4707 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.89104 | 0.99695 | -2.8442 | -5.263 | 5.263 | 7.3237 | 2.4072 | -0.19327 | 2.571% | -2.571%
3 | 7.407 | 2.4346 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.87622 | 0.99759 | -2.7992 | -5.263 | 5.263 | 7.2166 | 2.372 | -0.19042 | 2.571% | -2.571%
4 | 7.398 | 2.4316 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.875 | 0.99764 | -2.7955 | -5.263 | 5.263 | 7.2078 | 2.3691 | -0.19018 | 2.571% | -2.571%
5 | 7.563 | 2.4858 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0269 | -0.89725 | 0.99668 | -2.863 | -5.263 | 5.263 | 7.3685 | 2.4219 | -0.19446 | 2.571% | -2.571%
6 | 7.986 | 2.6249 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.95438 | 0.99418 | -3.0365 | -5.263 | 5.263 | 7.7806 | 2.5573 | -0.20543 | 2.572% | -2.572%
7 | 8.626 | 2.8352 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0252 | -1.0411 | 0.99037 | -3.301 | -5.263 | 5.263 | 8.4039 | 2.7622 | -0.22206 | 2.574% | -2.574%
8 | 9.059 | 2.9775 | 0.95 | Z | moderate sun | 5.263 | 5.2577 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0245 | -1.1002 | 0.98777 | -3.4814 | -5.2577 | 5.2577 | 8.8259 | 2.9009 | -0.23308 | 2.573% | -2.573%
9 | 9.181 | 3.0176 | 0.95 | Z | moderate sun | 5.263 | 5.2051 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6734 | 1.0245 | -1.1183 | 0.98716 | -3.5338 | -5.2051 | 5.2051 | 8.9472 | 2.9408 | -0.23383 | 2.547% | -2.547%
10 | 9.23 | 3.0338 | 0.95 | Z | moderate sun | 5.263 | 5.0946 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.694 | 1.0247 | -1.1286 | 0.9872 | -3.5579 | -5.0946 | 5.0946 | 9.0009 | 2.9585 | -0.22907 | 2.482% | -2.482%
11 | 9.261 | 3.0439 | 0.95 | Z | moderate sun | 5.263 | 4.9788 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.025 | -1.136 | 0.9873 | -3.574 | -4.9788 | 4.9788 | 9.0364 | 2.9701 | -0.22455 | 2.425% | -2.425%
12 | 9.292 | 3.0541 | 0.95 | Z | moderate sun | 5.263 | 4.9156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0251 | -1.1419 | 0.98727 | -3.5887 | -4.9156 | 4.9156 | 9.0696 | 2.981 | -0.22242 | 2.394% | -2.394%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 5.263 | 4.9841 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0249 | -1.1442 | 0.98691 | -3.5994 | -4.9841 | 4.9841 | 9.0957 | 2.9896 | -0.22629 | 2.428% | -2.428%
14 | 9.338 | 3.0693 | 0.95 | Z | moderate sun | 5.263 | 5.0156 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0247 | -1.1455 | 0.98673 | -3.6053 | -5.0156 | 5.0156 | 9.1099 | 2.9943 | -0.22814 | 2.443% | -2.443%
15 | 9.404 | 3.0909 | 0.95 | Z | moderate sun | 5.263 | 5.1472 | 3 | 1.0374 | -1.2888 | 0.99861 | -3.7672 | 1.0243 | -1.1509 | 0.986 | -3.6294 | -5.1472 | 5.1472 | 9.1681 | 3.0134 | -0.23589 | 2.508% | -2.508%
16 | 9.594 | 3.1534 | 0.95 | Z | moderate sun | 5.263 | 5.2367 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0237 | -1.1744 | 0.98462 | -3.7067 | -5.2367 | 5.2367 | 9.3491 | 3.0729 | -0.24495 | 2.553% | -2.553%
17 | 9.883 | 3.2484 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0231 | -1.2127 | 0.98272 | -3.8272 | -5.263 | 5.263 | 9.6282 | 3.1646 | -0.25479 | 2.578% | -2.578%
18 | 10 | 3.2868 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0229 | -1.2288 | 0.98199 | -3.8767 | -5.263 | 5.263 | 9.7422 | 3.2021 | -0.25784 | 2.578% | -2.578%
19 | 9.966 | 3.2757 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3669 | 0.99511 | -4.0051 | 1.023 | -1.2241 | 0.9822 | -3.8623 | -5.263 | 5.263 | 9.7091 | 3.1912 | -0.25695 | 2.578% | -2.578%
20 | 9.857 | 3.2398 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.9958 | -3.9588 | 1.0232 | -1.2092 | 0.98288 | -3.8163 | -5.263 | 5.263 | 9.6029 | 3.1563 | -0.25411 | 2.578% | -2.578%
21 | 9.62 | 3.1619 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1767 | 0.98433 | -3.7164 | -5.263 | 5.263 | 9.3721 | 3.0805 | -0.24793 | 2.577% | -2.577%
22 | 9.139 | 3.0038 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.111 | 0.98727 | -3.5147 | -5.263 | 5.263 | 8.9036 | 2.9265 | -0.2354 | 2.576% | -2.576%
23 | 8.547 | 2.8093 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0304 | 0.99084 | -3.2682 | -5.263 | 5.263 | 8.327 | 2.737 | -0.22 | 2.574% | -2.574%
24 | 8.047 | 2.6449 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.96263 | 0.99382 | -3.0616 | -5.263 | 5.263 | 7.84 | 2.5769 | -0.20702 | 2.573% | -2.573%
1 | 7.716 | 2.5361 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0267 | -0.91789 | 0.99578 | -2.9256 | -5.263 | 5.263 | 7.5176 | 2.4709 | -0.19843 | 2.572% | -2.572%
2 | 7.517 | 2.4707 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.89104 | 0.99695 | -2.8442 | -5.263 | 5.263 | 7.3237 | 2.4072 | -0.19327 | 2.571% | -2.571%
3 | 7.407 | 2.4346 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.87622 | 0.99759 | -2.7992 | -5.263 | 5.263 | 7.2166 | 2.372 | -0.19042 | 2.571% | -2.571%
4 | 7.398 | 2.4316 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.875 | 0.99764 | -2.7955 | -5.263 | 5.263 | 7.2078 | 2.3691 | -0.19018 | 2.571% | -2.571%
5 | 7.563 | 2.4858 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0269 | -0.89725 | 0.99668 | -2.863 | -5.263 | 5.263 | 7.3685 | 2.4219 | -0.19446 | 2.571% | -2.571%
6 | 7.986 | 2.6249 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.95438 | 0.99418 | -3.0365 | -5.263 | 5.263 | 7.7806 | 2.5573 | -0.20543 | 2.572% | -2.572%
7 | 8.626 | 2.8352 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0252 | -1.0411 | 0.99037 | -3.301 | -5.263 | 5.263 | 8.4039 | 2.7622 | -0.22206 | 2.574% | -2.574%
8 | 9.059 | 2.9775 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0245 | -1.1001 | 0.98776 | -3.4812 | -5.263 | 5.263 | 8.8257 | 2.9009 | -0.23332 | 2.576% | -2.576%
9 | 9.181 | 3.0176 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6734 | 1.0243 | -1.1167 | 0.98702 | -3.5322 | -5.263 | 5.263 | 8.9445 | 2.9399 | -0.23649 | 2.576% | -2.576%
10 | 9.23 | 3.0338 | 0.95 | Z | cloudy | 5.263 | 5.2577 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.694 | 1.0242 | -1.1235 | 0.98673 | -3.5529 | -5.2577 | 5.2577 | 8.9925 | 2.9557 | -0.23752 | 2.573% | -2.573%
11 | 9.261 | 3.0439 | 0.95 | Z | cloudy | 5.263 | 5.2419 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0242 | -1.1282 | 0.98658 | -3.5663 | -5.2419 | 5.2419 | 9.0234 | 2.9658 | -0.2376 | 2.566% | -2.566%
12 | 9.292 | 3.0541 | 0.95 | Z | cloudy | 5.263 | 5.2262 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0242 | -1.1329 | 0.98643 | -3.5797 | -5.2262 | 5.2262 | 9.0543 | 2.976 | -0.23767 | 2.558% | -2.558%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 5.263 | 5.2262 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0242 | -1.137 | 0.98625 | -3.5923 | -5.2262 | 5.2262 | 9.0836 | 2.9856 | -0.23844 | 2.558% | -2.558%
14 | 9.338 | 3.0693 | 0.95 | Z | cloudy | 5.263 | 5.2367 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0242 | -1.1394 | 0.98618 | -3.5993 | -5.2367 | 5.2367 | 9.0997 | 2.9909 | -0.23835 | 2.552% | -2.552%
15 | 9.404 | 3.0909 | 0.95 | Z | cloudy | 5.263 | 5.2525 | 3 | 1.0374 | -1.2888 | 0.99861 | -3.7672 | 1.024 | -1.148 | 0.98574 | -3.6265 | -5.2525 | 5.2525 | 9.1632 | 3.0118 | -0.24078 | 2.56% | -2.56%
16 | 9.594 | 3.1534 | 0.95 | Z | cloudy | 5.263 | 5.2577 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0236 | -1.1733 | 0.98451 | -3.7056 | -5.2577 | 5.2577 | 9.347 | 3.0722 | -0.247 | 2.574% | -2.574%
17 | 9.883 | 3.2484 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0231 | -1.2127 | 0.98272 | -3.8272 | -5.263 | 5.263 | 9.6282 | 3.1646 | -0.25479 | 2.578% | -2.578%
18 | 10 | 3.2868 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0229 | -1.2288 | 0.98199 | -3.8767 | -5.263 | 5.263 | 9.7422 | 3.2021 | -0.25784 | 2.578% | -2.578%
19 | 9.966 | 3.2757 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3669 | 0.99511 | -4.0051 | 1.023 | -1.2241 | 0.9822 | -3.8623 | -5.263 | 5.263 | 9.7091 | 3.1912 | -0.25695 | 2.578% | -2.578%
20 | 9.857 | 3.2398 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.9958 | -3.9588 | 1.0232 | -1.2092 | 0.98288 | -3.8163 | -5.263 | 5.263 | 9.6029 | 3.1563 | -0.25411 | 2.578% | -2.578%
21 | 9.62 | 3.1619 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1767 | 0.98433 | -3.7164 | -5.263 | 5.263 | 9.3721 | 3.0805 | -0.24793 | 2.577% | -2.577%
22 | 9.139 | 3.0038 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.111 | 0.98727 | -3.5147 | -5.263 | 5.263 | 8.9036 | 2.9265 | -0.2354 | 2.576% | -2.576%
23 | 8.547 | 2.8093 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0304 | 0.99084 | -3.2682 | -5.263 | 5.263 | 8.327 | 2.737 | -0.22 | 2.574% | -2.574%
24 | 8.047 | 2.6449 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.96263 | 0.99382 | -3.0616 | -5.263 | 5.263 | 7.84 | 2.5769 | -0.20702 | 2.573% | -2.573%
1 | 7.716 | 2.5361 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0128 | -0.77507 | 0.98228 | -2.7828 | -10.526 | 10.526 | 7.3151 | 2.4044 | -0.40085 | 5.195% | -5.195%
2 | 7.517 | 2.4707 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.74863 | 0.98343 | -2.7017 | -10.526 | 10.526 | 7.1266 | 2.3424 | -0.39043 | 5.194% | -5.194%
3 | 7.407 | 2.4346 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.73403 | 0.98407 | -2.657 | -10.526 | 10.526 | 7.0223 | 2.3081 | -0.38467 | 5.193% | -5.193%
4 | 7.398 | 2.4316 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.73284 | 0.98412 | -2.6534 | -10.526 | 10.526 | 7.0138 | 2.3053 | -0.3842 | 5.193% | -5.193%
5 | 7.563 | 2.4858 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.013 | -0.75474 | 0.98317 | -2.7205 | -10.526 | 10.526 | 7.1702 | 2.3567 | -0.39284 | 5.194% | -5.194%
6 | 7.986 | 2.6249 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.811 | 0.9807 | -2.8932 | -10.526 | 10.526 | 7.571 | 2.4885 | -0.41501 | 5.197% | -5.197%
7 | 8.626 | 2.8352 | 0.95 | Z | very sunny | 10.526 | 10.5049 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.89703 | 0.97698 | -3.1569 | -10.5049 | 10.5049 | 8.1783 | 2.6881 | -0.44768 | 5.19% | -5.19%
8 | 9.059 | 2.9775 | 0.95 | Z | very sunny | 10.526 | 10.2313 | 3 | 1.038 | -1.241 | 1.0007 | -3.6222 | 1.0114 | -0.96275 | 0.97511 | -3.3439 | -10.2313 | 10.2313 | 8.6011 | 2.8271 | -0.45788 | 5.054% | -5.054%
9 | 9.181 | 3.0176 | 0.95 | Z | very sunny | 10.526 | 9.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6734 | 1.0134 | -1.0023 | 0.9765 | -3.4178 | -9.4102 | 9.4102 | 8.755 | 2.8776 | -0.42602 | 4.64% | -4.64%
10 | 9.23 | 3.0338 | 0.95 | Z | very sunny | 10.526 | 8.284 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.694 | 1.0163 | -1.0407 | 0.97913 | -3.47 | -8.284 | 8.284 | 8.8544 | 2.9103 | -0.37563 | 4.07% | -4.07%
11 | 9.261 | 3.0439 | 0.95 | Z | very sunny | 10.526 | 7.1472 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0192 | -1.0755 | 0.98175 | -3.5136 | -7.1472 | 7.1472 | 8.9352 | 2.9369 | -0.3258 | 3.518% | -3.518%
12 | 9.292 | 3.0541 | 0.95 | Z | very sunny | 10.526 | 6.5156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0208 | -1.0972 | 0.98316 | -3.544 | -6.5156 | 6.5156 | 8.9944 | 2.9563 | -0.29761 | 3.203% | -3.203%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 10.526 | 6.7051 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0204 | -1.097 | 0.98259 | -3.5523 | -6.7051 | 6.7051 | 9.0163 | 2.9635 | -0.30574 | 3.28% | -3.28%
14 | 9.338 | 3.0693 | 0.95 | Z | very sunny | 10.526 | 7.0103 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0195 | -1.0908 | 0.98172 | -3.5506 | -7.0103 | 7.0103 | 9.0176 | 2.9639 | -0.32043 | 3.431% | -3.431%
15 | 9.404 | 3.0909 | 0.95 | Z | very sunny | 10.526 | 7.884 | 3 | 1.0374 | -1.2888 | 0.99861 | -3.7672 | 1.0174 | -1.0783 | 0.97935 | -3.5567 | -7.7495 | 7.884 | 9.0449 | 2.9729 | -0.35911 | 3.819% | -3.819%
16 | 9.594 | 3.1534 | 0.95 | Z | very sunny | 10.526 | 8.9155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.104 | 0.9782 | -3.6363 | -7.7501 | 8.9155 | 9.2275 | 3.0329 | -0.36647 | 3.82% | -3.82%
17 | 9.883 | 3.2484 | 0.95 | Z | very sunny | 10.526 | 9.8418 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1433 | 0.97642 | -3.7578 | -7.751 | 9.8418 | 9.5053 | 3.1242 | -0.37769 | 3.822% | -3.822%
18 | 10 | 3.2868 | 0.95 | Z | very sunny | 10.526 | 10.3786 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1592 | 0.9757 | -3.8072 | -7.7514 | 10.3786 | 9.6178 | 3.1612 | -0.38224 | 3.822% | -3.822%
19 | 9.966 | 3.2757 | 0.95 | Z | very sunny | 10.526 | 10.5155 | 3 | 1.0364 | -1.3669 | 0.99511 | -4.0051 | 1.0164 | -1.1546 | 0.97591 | -3.7928 | -7.7513 | 10.5155 | 9.5851 | 3.1505 | -0.38092 | 3.822% | -3.822%
20 | 9.857 | 3.2398 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.9958 | -3.9588 | 1.0166 | -1.1398 | 0.97658 | -3.7469 | -7.7509 | 10.526 | 9.4803 | 3.116 | -0.37668 | 3.821% | -3.821%
21 | 9.62 | 3.1619 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1076 | 0.97804 | -3.6472 | -7.7502 | 10.526 | 9.2525 | 3.0412 | -0.36748 | 3.82% | -3.82%
22 | 9.139 | 3.0038 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -0.9652 | 0.97387 | -3.3689 | -10.526 | 10.526 | 8.6634 | 2.8475 | -0.47556 | 5.204% | -5.204%
23 | 8.547 | 2.8093 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0114 | -0.88587 | 0.9774 | -3.1237 | -10.526 | 10.526 | 8.1025 | 2.6632 | -0.44445 | 5.2% | -5.2%
24 | 8.047 | 2.6449 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.81913 | 0.98035 | -2.9181 | -10.526 | 10.526 | 7.6288 | 2.5075 | -0.41821 | 5.197% | -5.197%
1 | 7.716 | 2.5361 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0128 | -0.77507 | 0.98228 | -2.7828 | -10.526 | 10.526 | 7.3151 | 2.4044 | -0.40086 | 5.195% | -5.195%
2 | 7.517 | 2.4707 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.74863 | 0.98343 | -2.7017 | -10.526 | 10.526 | 7.1266 | 2.3424 | -0.39043 | 5.194% | -5.194%
3 | 7.407 | 2.4346 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.73403 | 0.98407 | -2.657 | -10.526 | 10.526 | 7.0223 | 2.3081 | -0.38467 | 5.193% | -5.193%
4 | 7.398 | 2.4316 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.73284 | 0.98412 | -2.6534 | -10.526 | 10.526 | 7.0138 | 2.3053 | -0.3842 | 5.193% | -5.193%
5 | 7.563 | 2.4858 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.013 | -0.75474 | 0.98317 | -2.7205 | -10.526 | 10.526 | 7.1702 | 2.3567 | -0.39284 | 5.194% | -5.194%
6 | 7.986 | 2.6249 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.811 | 0.9807 | -2.8932 | -10.526 | 10.526 | 7.571 | 2.4885 | -0.41501 | 5.197% | -5.197%
7 | 8.626 | 2.8352 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0113 | -0.89644 | 0.97693 | -3.1563 | -10.526 | 10.526 | 8.1774 | 2.6878 | -0.4486 | 5.201% | -5.201%
8 | 9.059 | 2.9775 | 0.95 | Z | moderate sun | 10.526 | 10.5155 | 3 | 1.038 | -1.241 | 1.0007 | -3.6222 | 1.0106 | -0.95476 | 0.97437 | -3.3359 | -10.5155 | 10.5155 | 8.5881 | 2.8228 | -0.47087 | 5.198% | -5.198%
9 | 9.181 | 3.0176 | 0.95 | Z | moderate sun | 10.526 | 10.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6734 | 1.0107 | -0.9741 | 0.97391 | -3.3896 | -10.4102 | 10.4102 | 8.7086 | 2.8624 | -0.47241 | 5.145% | -5.145%
10 | 9.23 | 3.0338 | 0.95 | Z | moderate sun | 10.526 | 10.1892 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.694 | 1.0112 | -0.98692 | 0.97419 | -3.4162 | -10.1892 | 10.1892 | 8.7653 | 2.881 | -0.46466 | 5.034% | -5.034%
11 | 9.261 | 3.0439 | 0.95 | Z | moderate sun | 10.526 | 9.9576 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0118 | -0.99763 | 0.9746 | -3.4357 | -9.9576 | 9.9576 | 8.8056 | 2.8943 | -0.4554 | 4.917% | -4.917%
12 | 9.292 | 3.0541 | 0.95 | Z | moderate sun | 10.526 | 9.8313 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0121 | -1.0054 | 0.97474 | -3.4522 | -9.8313 | 9.8313 | 8.841 | 2.9059 | -0.45101 | 4.854% | -4.854%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 10.526 | 9.9681 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0175 | -1.0671 | 0.97985 | -3.5224 | -7.7491 | 9.9681 | 8.9661 | 2.947 | -0.35593 | 3.818% | -3.818%
14 | 9.338 | 3.0693 | 0.95 | Z | moderate sun | 10.526 | 10.0313 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0693 | 0.97976 | -3.5291 | -7.7493 | 10.0313 | 8.9815 | 2.9521 | -0.35655 | 3.818% | -3.818%
15 | 9.404 | 3.0909 | 0.95 | Z | moderate sun | 10.526 | 10.2944 | 3 | 1.0374 | -1.2888 | 0.99861 | -3.7672 | 1.0174 | -1.0783 | 0.97935 | -3.5567 | -7.7495 | 10.2944 | 9.0449 | 2.9729 | -0.35911 | 3.819% | -3.819%
16 | 9.594 | 3.1534 | 0.95 | Z | moderate sun | 10.526 | 10.4734 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.104 | 0.9782 | -3.6363 | -7.7501 | 10.4734 | 9.2275 | 3.0329 | -0.36647 | 3.82% | -3.82%
17 | 9.883 | 3.2484 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1433 | 0.97642 | -3.7578 | -7.751 | 10.526 | 9.5053 | 3.1242 | -0.37769 | 3.822% | -3.822%
18 | 10 | 3.2868 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1592 | 0.9757 | -3.8072 | -7.7514 | 10.526 | 9.6178 | 3.1612 | -0.38224 | 3.822% | -3.822%
19 | 9.966 | 3.2757 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3669 | 0.99511 | -4.0051 | 1.0164 | -1.1546 | 0.97591 | -3.7928 | -7.7513 | 10.526 | 9.5851 | 3.1505 | -0.38092 | 3.822% | -3.822%
20 | 9.857 | 3.2398 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.9958 | -3.9588 | 1.0166 | -1.1398 | 0.97658 | -3.7469 | -7.7509 | 10.526 | 9.4803 | 3.116 | -0.37668 | 3.821% | -3.821%
21 | 9.62 | 3.1619 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1076 | 0.97804 | -3.6472 | -7.7502 | 10.526 | 9.2525 | 3.0412 | -0.36748 | 3.82% | -3.82%
22 | 9.139 | 3.0038 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -0.9652 | 0.97387 | -3.3689 | -10.526 | 10.526 | 8.6634 | 2.8475 | -0.47556 | 5.204% | -5.204%
23 | 8.547 | 2.8093 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0114 | -0.88587 | 0.9774 | -3.1237 | -10.526 | 10.526 | 8.1025 | 2.6632 | -0.44445 | 5.2% | -5.2%
24 | 8.047 | 2.6449 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.81913 | 0.98035 | -2.9181 | -10.526 | 10.526 | 7.6288 | 2.5075 | -0.41821 | 5.197% | -5.197%
1 | 7.716 | 2.5361 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0128 | -0.77507 | 0.98228 | -2.7828 | -10.526 | 10.526 | 7.3151 | 2.4044 | -0.40086 | 5.195% | -5.195%
2 | 7.517 | 2.4707 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.74863 | 0.98343 | -2.7017 | -10.526 | 10.526 | 7.1266 | 2.3424 | -0.39043 | 5.194% | -5.194%
3 | 7.407 | 2.4346 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.73403 | 0.98407 | -2.657 | -10.526 | 10.526 | 7.0223 | 2.3081 | -0.38467 | 5.193% | -5.193%
4 | 7.398 | 2.4316 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.73284 | 0.98412 | -2.6534 | -10.526 | 10.526 | 7.0138 | 2.3053 | -0.3842 | 5.193% | -5.193%
5 | 7.563 | 2.4858 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.013 | -0.75474 | 0.98317 | -2.7205 | -10.526 | 10.526 | 7.1702 | 2.3567 | -0.39284 | 5.194% | -5.194%
6 | 7.986 | 2.6249 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.811 | 0.9807 | -2.8932 | -10.526 | 10.526 | 7.571 | 2.4885 | -0.41501 | 5.197% | -5.197%
7 | 8.626 | 2.8352 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0113 | -0.89644 | 0.97693 | -3.1563 | -10.526 | 10.526 | 8.1774 | 2.6878 | -0.4486 | 5.201% | -5.201%
8 | 9.059 | 2.9775 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.0007 | -3.6222 | 1.0106 | -0.95446 | 0.97435 | -3.3356 | -10.526 | 10.526 | 8.5876 | 2.8226 | -0.47136 | 5.203% | -5.203%
9 | 9.181 | 3.0176 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6734 | 1.0104 | -0.97084 | 0.97361 | -3.3863 | -10.526 | 10.526 | 8.7032 | 2.8606 | -0.47777 | 5.204% | -5.204%
10 | 9.23 | 3.0338 | 0.95 | Z | cloudy | 10.526 | 10.5155 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.694 | 1.0103 | -0.97772 | 0.97335 | -3.407 | -10.5155 | 10.5155 | 8.7501 | 2.876 | -0.47986 | 5.199% | -5.199%
11 | 9.261 | 3.0439 | 0.95 | Z | cloudy | 10.526 | 10.4839 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0104 | -0.98278 | 0.97324 | -3.4208 | -10.4839 | 10.4839 | 8.781 | 2.8862 | -0.48001 | 5.183% | -5.183%
12 | 9.292 | 3.0541 | 0.95 | Z | cloudy | 10.526 | 10.4523 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0104 | -0.98784 | 0.97314 | -3.4346 | -10.4523 | 10.4523 | 8.8118 | 2.8963 | -0.48016 | 5.167% | -5.167%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 10.526 | 10.4523 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0175 | -1.0671 | 0.97985 | -3.5224 | -7.7491 | 10.4523 | 8.9661 | 2.947 | -0.35593 | 3.818% | -3.818%
14 | 9.338 | 3.0693 | 0.95 | Z | cloudy | 10.526 | 10.4734 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0693 | 0.97976 | -3.5291 | -7.7493 | 10.4734 | 8.9815 | 2.9521 | -0.35655 | 3.818% | -3.818%
15 | 9.404 | 3.0909 | 0.95 | Z | cloudy | 10.526 | 10.5049 | 3 | 1.0374 | -1.2888 | 0.99861 | -3.7672 | 1.0174 | -1.0783 | 0.97935 | -3.5567 | -7.7495 | 10.5049 | 9.0449 | 2.9729 | -0.35911 | 3.819% | -3.819%
16 | 9.594 | 3.1534 | 0.95 | Z | cloudy | 10.526 | 10.5155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.104 | 0.9782 | -3.6363 | -7.7501 | 10.5155 | 9.2275 | 3.0329 | -0.36647 | 3.82% | -3.82%
17 | 9.883 | 3.2484 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1433 | 0.97642 | -3.7578 | -7.751 | 10.526 | 9.5053 | 3.1242 | -0.37769 | 3.822% | -3.822%
18 | 10 | 3.2868 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1592 | 0.9757 | -3.8072 | -7.7514 | 10.526 | 9.6178 | 3.1612 | -0.38224 | 3.822% | -3.822%
19 | 9.966 | 3.2757 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3669 | 0.99511 | -4.0051 | 1.0164 | -1.1546 | 0.97591 | -3.7928 | -7.7513 | 10.526 | 9.5851 | 3.1505 | -0.38092 | 3.822% | -3.822%
20 | 9.857 | 3.2398 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.9958 | -3.9588 | 1.0166 | -1.1398 | 0.97658 | -3.7469 | -7.7509 | 10.526 | 9.4803 | 3.116 | -0.37668 | 3.821% | -3.821%
21 | 9.62 | 3.1619 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1076 | 0.97804 | -3.6472 | -7.7502 | 10.526 | 9.2525 | 3.0412 | -0.36748 | 3.82% | -3.82%
22 | 9.139 | 3.0038 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -0.9652 | 0.97387 | -3.3689 | -10.526 | 10.526 | 8.6634 | 2.8475 | -0.47556 | 5.204% | -5.204%
23 | 8.547 | 2.8093 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0114 | -0.88587 | 0.9774 | -3.1237 | -10.526 | 10.526 | 8.1025 | 2.6632 | -0.44445 | 5.2% | -5.2%
24 | 8.047 | 2.6449 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.81913 | 0.98035 | -2.9181 | -10.526 | 10.526 | 7.6288 | 2.5075 | -0.41821 | 5.197% | -5.197%
1 | 7.716 | 2.5361 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0639 | 0.99677 | -1.5421 | 0.98165 | -2.5608 | -5.263 | 5.263 | 7.3058 | 2.4013 | -0.41016 | 5.316% | -5.316%
2 | 7.517 | 2.4707 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99752 | -1.4902 | 0.98282 | -2.4808 | -5.263 | 5.263 | 7.1176 | 2.3394 | -0.39941 | 5.313% | -5.313%
3 | 7.407 | 2.4346 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.99793 | -1.4615 | 0.98346 | -2.4366 | -5.263 | 5.263 | 7.0135 | 2.3052 | -0.39347 | 5.312% | -5.312%
4 | 7.398 | 2.4316 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99796 | -1.4592 | 0.98351 | -2.433 | -5.263 | 5.263 | 7.005 | 2.3024 | -0.39298 | 5.312% | -5.312%
5 | 7.563 | 2.4858 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99734 | -1.5022 | 0.98255 | -2.4992 | -5.263 | 5.263 | 7.1611 | 2.3537 | -0.40189 | 5.314% | -5.314%
6 | 7.986 | 2.6249 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99574 | -1.6126 | 0.98007 | -2.6698 | -5.263 | 5.263 | 7.5612 | 2.4853 | -0.42478 | 5.319% | -5.319%
7 | 8.626 | 2.8352 | 0.95 | Z | very sunny | 5.263 | 5.2525 | 4 | 1.0209 | -2.2921 | 1.0034 | -3.4411 | 0.99335 | -1.7816 | 0.97634 | -2.9306 | -5.2525 | 5.2525 | 8.1674 | 2.6845 | -0.45855 | 5.316% | -5.316%
8 | 9.059 | 2.9775 | 0.95 | Z | very sunny | 5.263 | 5.1156 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6222 | 0.99241 | -1.9097 | 0.97447 | -3.1215 | -5.1156 | 5.1156 | 8.5898 | 2.8233 | -0.46922 | 5.18% | -5.18%
9 | 9.181 | 3.0176 | 0.95 | Z | very sunny | 5.263 | 4.7051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99415 | -1.9837 | 0.97592 | -3.2133 | -4.7051 | 4.7051 | 8.7444 | 2.8742 | -0.43658 | 4.755% | -4.755%
10 | 9.23 | 3.0338 | 0.95 | Z | very sunny | 5.263 | 4.142 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99701 | -2.0539 | 0.97861 | -3.2907 | -4.142 | 4.142 | 8.8451 | 2.9073 | -0.38488 | 4.17% | -4.17%
11 | 9.261 | 3.0439 | 0.95 | Z | very sunny | 5.263 | 3.5736 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99983 | -2.1174 | 0.98131 | -3.3588 | -3.5736 | 3.5736 | 8.9272 | 2.9342 | -0.3338 | 3.604% | -3.604%
12 | 9.292 | 3.0541 | 0.95 | Z | very sunny | 5.263 | 3.2578 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.7201 | 1.0014 | -2.1572 | 0.98277 | -3.4031 | -3.2578 | 3.2578 | 8.9871 | 2.9539 | -0.30491 | 3.281% | -3.281%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 5.263 | 3.3525 | 4 | 1.0181 | -2.4824 | 0.99911 | -3.7327 | 1.0009 | -2.1576 | 0.98219 | -3.4079 | -3.3525 | 3.3525 | 9.0088 | 2.9611 | -0.31316 | 3.359% | -3.359%
14 | 9.338 | 3.0693 | 0.95 | Z | very sunny | 5.263 | 3.5052 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99999 | -2.1467 | 0.9813 | -3.3994 | -3.5052 | 3.5052 | 9.0098 | 2.9614 | -0.32823 | 3.515% | -3.515%
15 | 9.404 | 3.0909 | 0.95 | Z | very sunny | 5.263 | 3.942 | 4 | 1.0178 | -2.5049 | 0.99861 | -3.7672 | 0.99778 | -2.1278 | 0.97898 | -3.3902 | -3.8533 | 3.942 | 9.038 | 2.9707 | -0.36595 | 3.891% | -3.891%
16 | 9.594 | 3.1534 | 0.95 | Z | very sunny | 5.263 | 4.4578 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.1786 | 0.97782 | -3.469 | -3.8544 | 4.4578 | 9.2204 | 3.0306 | -0.37362 | 3.894% | -3.894%
17 | 9.883 | 3.2484 | 0.95 | Z | very sunny | 5.263 | 4.9209 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.2561 | 0.97603 | -3.5892 | -3.8561 | 4.9209 | 9.4977 | 3.1217 | -0.38532 | 3.899% | -3.899%
18 | 10 | 3.2868 | 0.95 | Z | very sunny | 5.263 | 5.1893 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.2875 | 0.97531 | -3.638 | -3.8567 | 5.1893 | 9.6099 | 3.1586 | -0.39006 | 3.901% | -3.901%
19 | 9.966 | 3.2757 | 0.95 | Z | very sunny | 5.263 | 5.2577 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99553 | -2.2784 | 0.97552 | -3.6238 | -3.8565 | 5.2577 | 9.5773 | 3.1479 | -0.38868 | 3.9% | -3.9%
20 | 9.857 | 3.2398 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.9958 | -3.9588 | 0.99597 | -2.2491 | 0.97619 | -3.5784 | -3.8559 | 5.263 | 9.4727 | 3.1135 | -0.38426 | 3.898% | -3.898%
21 | 9.62 | 3.1619 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.1856 | 0.97766 | -3.4798 | -3.8545 | 5.263 | 9.2453 | 3.0388 | -0.37468 | 3.895% | -3.895%
22 | 9.139 | 3.0038 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99129 | -1.9159 | 0.9732 | -3.1394 | -5.263 | 5.263 | 8.6516 | 2.8436 | -0.4874 | 5.333% | -5.333%
23 | 8.547 | 2.8093 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.9936 | -1.7598 | 0.97675 | -2.8974 | -5.263 | 5.263 | 8.0918 | 2.6596 | -0.45521 | 5.326% | -5.326%
24 | 8.047 | 2.6449 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99551 | -1.6286 | 0.97971 | -2.6944 | -5.263 | 5.263 | 7.6189 | 2.5042 | -0.42808 | 5.32% | -5.32%
1 | 7.716 | 2.5361 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0639 | 0.99677 | -1.5421 | 0.98165 | -2.5608 | -5.263 | 5.263 | 7.3058 | 2.4013 | -0.41017 | 5.316% | -5.316%
2 | 7.517 | 2.4707 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99752 | -1.4902 | 0.98282 | -2.4808 | -5.263 | 5.263 | 7.1176 | 2.3394 | -0.39941 | 5.313% | -5.313%
3 | 7.407 | 2.4346 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.99793 | -1.4615 | 0.98346 | -2.4366 | -5.263 | 5.263 | 7.0135 | 2.3052 | -0.39347 | 5.312% | -5.312%
4 | 7.398 | 2.4316 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99796 | -1.4592 | 0.98351 | -2.433 | -5.263 | 5.263 | 7.005 | 2.3024 | -0.39298 | 5.312% | -5.312%
5 | 7.563 | 2.4858 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99734 | -1.5022 | 0.98255 | -2.4992 | -5.263 | 5.263 | 7.1611 | 2.3537 | -0.40189 | 5.314% | -5.314%
6 | 7.986 | 2.6249 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99574 | -1.6126 | 0.98007 | -2.6698 | -5.263 | 5.263 | 7.5612 | 2.4853 | -0.42478 | 5.319% | -5.319%
7 | 8.626 | 2.8352 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0209 | -2.2921 | 1.0034 | -3.4411 | 0.99329 | -1.7806 | 0.97628 | -2.9296 | -5.263 | 5.263 | 8.1665 | 2.6842 | -0.45949 | 5.327% | -5.327%
8 | 9.059 | 2.9775 | 0.95 | Z | moderate sun | 5.263 | 5.2577 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6222 | 0.99164 | -1.8953 | 0.97371 | -3.1072 | -5.2577 | 5.2577 | 8.5764 | 2.8189 | -0.48255 | 5.327% | -5.327%
9 | 9.181 | 3.0176 | 0.95 | Z | moderate sun | 5.263 | 5.2051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99144 | -1.9329 | 0.97325 | -3.1626 | -5.2051 | 5.2051 | 8.6968 | 2.8585 | -0.48419 | 5.274% | -5.274%
10 | 9.23 | 3.0338 | 0.95 | Z | moderate sun | 5.263 | 5.0946 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99185 | -1.9571 | 0.97355 | -3.1939 | -5.0946 | 5.0946 | 8.7537 | 2.8772 | -0.47626 | 5.16% | -5.16%
11 | 9.261 | 3.0439 | 0.95 | Z | moderate sun | 5.263 | 4.9788 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.0897 | 0.97986 | -3.331 | -3.8524 | 4.9788 | 8.9008 | 2.9256 | -0.36019 | 3.889% | -3.889%
12 | 9.292 | 3.0541 | 0.95 | Z | moderate sun | 5.263 | 4.9156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.7201 | 0.99823 | -2.0979 | 0.97967 | -3.3438 | -3.8527 | 4.9156 | 8.9306 | 2.9353 | -0.36144 | 3.89% | -3.89%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 5.263 | 4.9841 | 4 | 1.0181 | -2.4824 | 0.99911 | -3.7327 | 0.99811 | -2.1059 | 0.97949 | -3.3563 | -3.8528 | 4.9841 | 8.9593 | 2.9448 | -0.36265 | 3.89% | -3.89%
14 | 9.338 | 3.0693 | 0.95 | Z | moderate sun | 5.263 | 5.0156 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1102 | 0.97939 | -3.3629 | -3.8529 | 5.0156 | 8.9747 | 2.9498 | -0.3633 | 3.891% | -3.891%
15 | 9.404 | 3.0909 | 0.95 | Z | moderate sun | 5.263 | 5.1472 | 4 | 1.0178 | -2.5049 | 0.99861 | -3.7672 | 0.99778 | -2.1278 | 0.97898 | -3.3902 | -3.8533 | 5.1472 | 9.038 | 2.9707 | -0.36596 | 3.892% | -3.892%
16 | 9.594 | 3.1534 | 0.95 | Z | moderate sun | 5.263 | 5.2367 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.1786 | 0.97782 | -3.469 | -3.8544 | 5.2367 | 9.2204 | 3.0306 | -0.37362 | 3.894% | -3.894%
17 | 9.883 | 3.2484 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.2561 | 0.97603 | -3.5892 | -3.8561 | 5.263 | 9.4977 | 3.1217 | -0.38532 | 3.899% | -3.899%
18 | 10 | 3.2868 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.2875 | 0.97531 | -3.638 | -3.8567 | 5.263 | 9.6099 | 3.1586 | -0.39006 | 3.901% | -3.901%
19 | 9.966 | 3.2757 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99553 | -2.2784 | 0.97552 | -3.6238 | -3.8565 | 5.263 | 9.5773 | 3.1479 | -0.38868 | 3.9% | -3.9%
20 | 9.857 | 3.2398 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.9958 | -3.9588 | 0.99597 | -2.2491 | 0.97619 | -3.5784 | -3.8559 | 5.263 | 9.4727 | 3.1135 | -0.38426 | 3.898% | -3.898%
21 | 9.62 | 3.1619 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.1856 | 0.97766 | -3.4798 | -3.8545 | 5.263 | 9.2453 | 3.0388 | -0.37468 | 3.895% | -3.895%
22 | 9.139 | 3.0038 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99129 | -1.9159 | 0.9732 | -3.1394 | -5.263 | 5.263 | 8.6516 | 2.8436 | -0.4874 | 5.333% | -5.333%
23 | 8.547 | 2.8093 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.9936 | -1.7598 | 0.97675 | -2.8974 | -5.263 | 5.263 | 8.0918 | 2.6596 | -0.45521 | 5.326% | -5.326%
24 | 8.047 | 2.6449 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99551 | -1.6286 | 0.97971 | -2.6944 | -5.263 | 5.263 | 7.6189 | 2.5042 | -0.42808 | 5.32% | -5.32%
1 | 7.716 | 2.5361 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0639 | 0.99677 | -1.5421 | 0.98165 | -2.5608 | -5.263 | 5.263 | 7.3058 | 2.4013 | -0.41017 | 5.316% | -5.316%
2 | 7.517 | 2.4707 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99752 | -1.4902 | 0.98282 | -2.4808 | -5.263 | 5.263 | 7.1176 | 2.3394 | -0.39941 | 5.313% | -5.313%
3 | 7.407 | 2.4346 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.99793 | -1.4615 | 0.98346 | -2.4366 | -5.263 | 5.263 | 7.0135 | 2.3052 | -0.39347 | 5.312% | -5.312%
4 | 7.398 | 2.4316 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99796 | -1.4592 | 0.98351 | -2.433 | -5.263 | 5.263 | 7.005 | 2.3024 | -0.39298 | 5.312% | -5.312%
5 | 7.563 | 2.4858 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99734 | -1.5022 | 0.98255 | -2.4992 | -5.263 | 5.263 | 7.1611 | 2.3537 | -0.40189 | 5.314% | -5.314%
6 | 7.986 | 2.6249 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99574 | -1.6126 | 0.98007 | -2.6698 | -5.263 | 5.263 | 7.5612 | 2.4853 | -0.42478 | 5.319% | -5.319%
7 | 8.626 | 2.8352 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0209 | -2.2921 | 1.0034 | -3.4411 | 0.99329 | -1.7806 | 0.97628 | -2.9296 | -5.263 | 5.263 | 8.1665 | 2.6842 | -0.45949 | 5.327% | -5.327%
8 | 9.059 | 2.9775 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6222 | 0.99161 | -1.8948 | 0.97368 | -3.1066 | -5.263 | 5.263 | 8.576 | 2.8188 | -0.48305 | 5.332% | -5.332%
9 | 9.181 | 3.0176 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99113 | -1.927 | 0.97295 | -3.1567 | -5.263 | 5.263 | 8.6913 | 2.8567 | -0.48969 | 5.334% | -5.334%
10 | 9.23 | 3.0338 | 0.95 | Z | cloudy | 5.263 | 5.2577 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99097 | -1.9405 | 0.97268 | -3.1774 | -5.2577 | 5.2577 | 8.7381 | 2.8721 | -0.49187 | 5.329% | -5.329%
11 | 9.261 | 3.0439 | 0.95 | Z | cloudy | 5.263 | 5.2419 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.0897 | 0.97986 | -3.331 | -3.8524 | 5.2419 | 8.9008 | 2.9256 | -0.36019 | 3.889% | -3.889%
12 | 9.292 | 3.0541 | 0.95 | Z | cloudy | 5.263 | 5.2262 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.7201 | 0.99823 | -2.0979 | 0.97967 | -3.3438 | -3.8527 | 5.2262 | 8.9306 | 2.9353 | -0.36144 | 3.89% | -3.89%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 5.263 | 5.2262 | 4 | 1.0181 | -2.4824 | 0.99911 | -3.7327 | 0.99811 | -2.1059 | 0.97949 | -3.3563 | -3.8528 | 5.2262 | 8.9593 | 2.9448 | -0.36265 | 3.89% | -3.89%
14 | 9.338 | 3.0693 | 0.95 | Z | cloudy | 5.263 | 5.2367 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1102 | 0.97939 | -3.3629 | -3.8529 | 5.2367 | 8.9747 | 2.9498 | -0.3633 | 3.891% | -3.891%
15 | 9.404 | 3.0909 | 0.95 | Z | cloudy | 5.263 | 5.2525 | 4 | 1.0178 | -2.5049 | 0.99861 | -3.7672 | 0.99778 | -2.1278 | 0.97898 | -3.3902 | -3.8533 | 5.2525 | 9.038 | 2.9707 | -0.36596 | 3.892% | -3.892%
16 | 9.594 | 3.1534 | 0.95 | Z | cloudy | 5.263 | 5.2577 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.1786 | 0.97782 | -3.469 | -3.8544 | 5.2577 | 9.2204 | 3.0306 | -0.37362 | 3.894% | -3.894%
17 | 9.883 | 3.2484 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.2561 | 0.97603 | -3.5892 | -3.8561 | 5.263 | 9.4977 | 3.1217 | -0.38532 | 3.899% | -3.899%
18 | 10 | 3.2868 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.2875 | 0.97531 | -3.638 | -3.8567 | 5.263 | 9.6099 | 3.1586 | -0.39006 | 3.901% | -3.901%
19 | 9.966 | 3.2757 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99553 | -2.2784 | 0.97552 | -3.6238 | -3.8565 | 5.263 | 9.5773 | 3.1479 | -0.38868 | 3.9% | -3.9%
20 | 9.857 | 3.2398 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.9958 | -3.9588 | 0.99597 | -2.2491 | 0.97619 | -3.5784 | -3.8559 | 5.263 | 9.4727 | 3.1135 | -0.38426 | 3.898% | -3.898%
21 | 9.62 | 3.1619 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.1856 | 0.97766 | -3.4798 | -3.8545 | 5.263 | 9.2453 | 3.0388 | -0.37468 | 3.895% | -3.895%
22 | 9.139 | 3.0038 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99129 | -1.9159 | 0.9732 | -3.1394 | -5.263 | 5.263 | 8.6516 | 2.8436 | -0.4874 | 5.333% | -5.333%
23 | 8.547 | 2.8093 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.9936 | -1.7598 | 0.97675 | -2.8974 | -5.263 | 5.263 | 8.0918 | 2.6596 | -0.45521 | 5.326% | -5.326%
24 | 8.047 | 2.6449 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99551 | -1.6286 | 0.97971 | -2.6944 | -5.263 | 5.263 | 7.6189 | 2.5042 | -0.42808 | 5.32% | -5.32%
1 | 7.716 | 2.5361 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0639 | 0.99437 | -1.4984 | 0.97929 | -2.5171 | -5.7053 | 10.526 | 7.2707 | 2.3898 | -0.44533 | 5.772% | -5.772%
2 | 7.517 | 2.4707 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.2656 | 0.9706 | -2.2562 | -7.5247 | 10.526 | 6.9418 | 2.2817 | -0.57518 | 7.652% | -7.652%
3 | 7.407 | 2.4346 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9369 | 0.98554 | -1.2376 | 0.97125 | -2.2126 | -7.5231 | 10.526 | 6.8405 | 2.2484 | -0.56653 | 7.649% | -7.649%
4 | 7.398 | 2.4316 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0256 | -1.9594 | 1.0107 | -2.9332 | 0.98558 | -1.2353 | 0.9713 | -2.2091 | -7.5231 | 10.526 | 6.8322 | 2.2456 | -0.56583 | 7.648% | -7.648%
5 | 7.563 | 2.4858 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.0039 | 1.0097 | -3.0009 | 0.98495 | -1.2774 | 0.97034 | -2.2745 | -7.5247 | 10.526 | 6.9842 | 2.2956 | -0.57879 | 7.653% | -7.653%
6 | 7.986 | 2.6249 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1754 | 0.99333 | -1.5685 | 0.9777 | -2.6257 | -5.7069 | 10.526 | 7.5246 | 2.4732 | -0.46137 | 5.777% | -5.777%
7 | 8.626 | 2.8352 | 0.95 | Z | very sunny | 10.526 | 10.5049 | 4 | 1.0209 | -2.2921 | 1.0034 | -3.4411 | 0.99085 | -1.7354 | 0.97388 | -2.8844 | -5.7125 | 10.5049 | 8.1265 | 2.671 | -0.49954 | 5.791% | -5.791%
8 | 9.059 | 2.9775 | 0.95 | Z | very sunny | 10.526 | 10.2313 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6222 | 0.98915 | -1.8489 | 0.97127 | -3.0607 | -5.7159 | 10.2313 | 8.5335 | 2.8048 | -0.52548 | 5.801% | -5.801%
9 | 9.181 | 3.0176 | 0.95 | Z | very sunny | 10.526 | 9.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.8809 | 0.97053 | -3.1106 | -5.7169 | 9.4102 | 8.6482 | 2.8425 | -0.5328 | 5.803% | -5.803%
10 | 9.23 | 3.0338 | 0.95 | Z | very sunny | 10.526 | 8.284 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.8938 | 0.97023 | -3.1307 | -5.7173 | 8.284 | 8.6943 | 2.8577 | -0.53574 | 5.804% | -5.804%
11 | 9.261 | 3.0439 | 0.95 | Z | very sunny | 10.526 | 7.1472 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.0897 | 0.97986 | -3.331 | -3.8523 | 7.1472 | 8.9008 | 2.9256 | -0.36019 | 3.889% | -3.889%
12 | 9.292 | 3.0541 | 0.95 | Z | very sunny | 10.526 | 6.5156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.7201 | 0.99823 | -2.0979 | 0.97967 | -3.3438 | -3.8527 | 6.5156 | 8.9306 | 2.9353 | -0.36144 | 3.89% | -3.89%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 10.526 | 6.7051 | 4 | 1.0181 | -2.4824 | 0.99911 | -3.7327 | 0.99811 | -2.1059 | 0.97949 | -3.3563 | -3.8528 | 6.7051 | 8.9593 | 2.9448 | -0.36265 | 3.89% | -3.89%
14 | 9.338 | 3.0693 | 0.95 | Z | very sunny | 10.526 | 7.0103 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1102 | 0.97939 | -3.3629 | -3.8529 | 7.0103 | 8.9747 | 2.9498 | -0.3633 | 3.891% | -3.891%
15 | 9.404 | 3.0909 | 0.95 | Z | very sunny | 10.526 | 7.884 | 4 | 1.0178 | -2.5049 | 0.99861 | -3.7672 | 0.99778 | -2.1278 | 0.97898 | -3.3902 | -3.8533 | 7.884 | 9.038 | 2.9707 | -0.36596 | 3.892% | -3.892%
16 | 9.594 | 3.1534 | 0.95 | Z | very sunny | 10.526 | 8.9155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.1786 | 0.97782 | -3.469 | -3.8544 | 8.9155 | 9.2204 | 3.0306 | -0.37362 | 3.894% | -3.894%
17 | 9.883 | 3.2484 | 0.95 | Z | very sunny | 10.526 | 9.8418 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.2561 | 0.97603 | -3.5892 | -3.8561 | 9.8418 | 9.4977 | 3.1217 | -0.38532 | 3.899% | -3.899%
18 | 10 | 3.2868 | 0.95 | Z | very sunny | 10.526 | 10.3786 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.2875 | 0.97531 | -3.638 | -3.8567 | 10.3786 | 9.6099 | 3.1586 | -0.39006 | 3.901% | -3.901%
19 | 9.966 | 3.2757 | 0.95 | Z | very sunny | 10.526 | 10.5155 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99553 | -2.2784 | 0.97552 | -3.6238 | -3.8565 | 10.5155 | 9.5773 | 3.1479 | -0.38868 | 3.9% | -3.9%
20 | 9.857 | 3.2398 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.9958 | -3.9588 | 0.99597 | -2.2491 | 0.97619 | -3.5784 | -3.8559 | 10.526 | 9.4727 | 3.1135 | -0.38426 | 3.898% | -3.898%
21 | 9.62 | 3.1619 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.1856 | 0.97766 | -3.4798 | -3.8545 | 10.526 | 9.2453 | 3.0388 | -0.37468 | 3.895% | -3.895%
22 | 9.139 | 3.0038 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.8699 | 0.97079 | -3.0934 | -5.7167 | 10.526 | 8.6087 | 2.8295 | -0.53028 | 5.802% | -5.802%
23 | 8.547 | 2.8093 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7148 | 0.97436 | -2.8523 | -5.7118 | 10.526 | 8.0522 | 2.6466 | -0.49482 | 5.789% | -5.789%
24 | 8.047 | 2.6449 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.5844 | 0.97734 | -2.6502 | -5.7078 | 10.526 | 7.582 | 2.4921 | -0.465 | 5.779% | -5.779%
1 | 7.716 | 2.5361 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0639 | 0.99437 | -1.4984 | 0.97929 | -2.5171 | -5.7052 | 10.526 | 7.2707 | 2.3898 | -0.44533 | 5.772% | -5.772%
2 | 7.517 | 2.4707 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.2656 | 0.9706 | -2.2562 | -7.5247 | 10.526 | 6.9418 | 2.2817 | -0.57518 | 7.652% | -7.652%
3 | 7.407 | 2.4346 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9369 | 0.98554 | -1.2376 | 0.97125 | -2.2126 | -7.5231 | 10.526 | 6.8405 | 2.2484 | -0.56653 | 7.649% | -7.649%
4 | 7.398 | 2.4316 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0256 | -1.9594 | 1.0107 | -2.9332 | 0.98558 | -1.2353 | 0.9713 | -2.2091 | -7.5231 | 10.526 | 6.8322 | 2.2456 | -0.56583 | 7.648% | -7.648%
5 | 7.563 | 2.4858 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.0039 | 1.0097 | -3.0009 | 0.98495 | -1.2774 | 0.97034 | -2.2745 | -7.5247 | 10.526 | 6.9842 | 2.2956 | -0.57879 | 7.653% | -7.653%
6 | 7.986 | 2.6249 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1754 | 0.99333 | -1.5685 | 0.9777 | -2.6257 | -5.7069 | 10.526 | 7.5246 | 2.4732 | -0.46137 | 5.777% | -5.777%
7 | 8.626 | 2.8352 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0209 | -2.2921 | 1.0034 | -3.4411 | 0.99085 | -1.7354 | 0.97388 | -2.8844 | -5.7125 | 10.526 | 8.1265 | 2.671 | -0.49954 | 5.791% | -5.791%
8 | 9.059 | 2.9775 | 0.95 | Z | moderate sun | 10.526 | 10.5155 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6222 | 0.98915 | -1.8489 | 0.97127 | -3.0607 | -5.7159 | 10.5155 | 8.5335 | 2.8048 | -0.52548 | 5.801% | -5.801%
9 | 9.181 | 3.0176 | 0.95 | Z | moderate sun | 10.526 | 10.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.8809 | 0.97053 | -3.1106 | -5.7169 | 10.4102 | 8.6482 | 2.8425 | -0.5328 | 5.803% | -5.803%
10 | 9.23 | 3.0338 | 0.95 | Z | moderate sun | 10.526 | 10.1892 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.8938 | 0.97023 | -3.1307 | -5.7173 | 10.1892 | 8.6943 | 2.8577 | -0.53574 | 5.804% | -5.804%
11 | 9.261 | 3.0439 | 0.95 | Z | moderate sun | 10.526 | 9.9576 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.0897 | 0.97986 | -3.331 | -3.8523 | 9.9576 | 8.9008 | 2.9256 | -0.36019 | 3.889% | -3.889%
12 | 9.292 | 3.0541 | 0.95 | Z | moderate sun | 10.526 | 9.8313 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.7201 | 0.99823 | -2.0979 | 0.97967 | -3.3438 | -3.8527 | 9.8313 | 8.9306 | 2.9353 | -0.36144 | 3.89% | -3.89%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 10.526 | 9.9681 | 4 | 1.0181 | -2.4824 | 0.99911 | -3.7327 | 0.99811 | -2.1059 | 0.97949 | -3.3563 | -3.8528 | 9.9681 | 8.9593 | 2.9448 | -0.36265 | 3.89% | -3.89%
14 | 9.338 | 3.0693 | 0.95 | Z | moderate sun | 10.526 | 10.0313 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1102 | 0.97939 | -3.3629 | -3.8529 | 10.0313 | 8.9747 | 2.9498 | -0.3633 | 3.891% | -3.891%
15 | 9.404 | 3.0909 | 0.95 | Z | moderate sun | 10.526 | 10.2944 | 4 | 1.0178 | -2.5049 | 0.99861 | -3.7672 | 0.99778 | -2.1278 | 0.97898 | -3.3902 | -3.8533 | 10.2944 | 9.038 | 2.9707 | -0.36596 | 3.892% | -3.892%
16 | 9.594 | 3.1534 | 0.95 | Z | moderate sun | 10.526 | 10.4734 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.1786 | 0.97782 | -3.469 | -3.8544 | 10.4734 | 9.2204 | 3.0306 | -0.37362 | 3.894% | -3.894%
17 | 9.883 | 3.2484 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.2561 | 0.97603 | -3.5892 | -3.8561 | 10.526 | 9.4977 | 3.1217 | -0.38532 | 3.899% | -3.899%
18 | 10 | 3.2868 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.2875 | 0.97531 | -3.638 | -3.8567 | 10.526 | 9.6099 | 3.1586 | -0.39006 | 3.901% | -3.901%
19 | 9.966 | 3.2757 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99553 | -2.2784 | 0.97552 | -3.6238 | -3.8565 | 10.526 | 9.5773 | 3.1479 | -0.38868 | 3.9% | -3.9%
20 | 9.857 | 3.2398 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.9958 | -3.9588 | 0.99597 | -2.2491 | 0.97619 | -3.5784 | -3.8559 | 10.526 | 9.4727 | 3.1135 | -0.38426 | 3.898% | -3.898%
21 | 9.62 | 3.1619 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.1856 | 0.97766 | -3.4798 | -3.8545 | 10.526 | 9.2453 | 3.0388 | -0.37468 | 3.895% | -3.895%
22 | 9.139 | 3.0038 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.8699 | 0.97079 | -3.0934 | -5.7167 | 10.526 | 8.6087 | 2.8295 | -0.53028 | 5.802% | -5.802%
23 | 8.547 | 2.8093 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7148 | 0.97436 | -2.8523 | -5.7118 | 10.526 | 8.0522 | 2.6466 | -0.49482 | 5.789% | -5.789%
24 | 8.047 | 2.6449 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.5844 | 0.97734 | -2.6502 | -5.7078 | 10.526 | 7.582 | 2.4921 | -0.465 | 5.779% | -5.779%
1 | 7.716 | 2.5361 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0639 | 0.99437 | -1.4984 | 0.97929 | -2.5171 | -5.7052 | 10.526 | 7.2707 | 2.3898 | -0.44533 | 5.772% | -5.772%
2 | 7.517 | 2.4707 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.2656 | 0.9706 | -2.2562 | -7.5247 | 10.526 | 6.9418 | 2.2817 | -0.57518 | 7.652% | -7.652%
3 | 7.407 | 2.4346 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9369 | 0.98554 | -1.2376 | 0.97125 | -2.2126 | -7.5231 | 10.526 | 6.8405 | 2.2484 | -0.56653 | 7.649% | -7.649%
4 | 7.398 | 2.4316 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0256 | -1.9594 | 1.0107 | -2.9332 | 0.98558 | -1.2353 | 0.9713 | -2.2091 | -7.5231 | 10.526 | 6.8322 | 2.2456 | -0.56583 | 7.648% | -7.648%
5 | 7.563 | 2.4858 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.0039 | 1.0097 | -3.0009 | 0.98495 | -1.2774 | 0.97034 | -2.2745 | -7.5247 | 10.526 | 6.9842 | 2.2956 | -0.57879 | 7.653% | -7.653%
6 | 7.986 | 2.6249 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1754 | 0.99333 | -1.5685 | 0.9777 | -2.6257 | -5.7069 | 10.526 | 7.5246 | 2.4732 | -0.46137 | 5.777% | -5.777%
7 | 8.626 | 2.8352 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0209 | -2.2921 | 1.0034 | -3.4411 | 0.99085 | -1.7354 | 0.97388 | -2.8844 | -5.7125 | 10.526 | 8.1265 | 2.671 | -0.49954 | 5.791% | -5.791%
8 | 9.059 | 2.9775 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6222 | 0.98915 | -1.8489 | 0.97127 | -3.0607 | -5.7159 | 10.526 | 8.5335 | 2.8048 | -0.52548 | 5.801% | -5.801%
9 | 9.181 | 3.0176 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.8809 | 0.97053 | -3.1106 | -5.7169 | 10.526 | 8.6482 | 2.8425 | -0.5328 | 5.803% | -5.803%
10 | 9.23 | 3.0338 | 0.95 | Z | cloudy | 10.526 | 10.5155 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.8938 | 0.97023 | -3.1307 | -5.7173 | 10.5155 | 8.6943 | 2.8577 | -0.53574 | 5.804% | -5.804%
11 | 9.261 | 3.0439 | 0.95 | Z | cloudy | 10.526 | 10.4839 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.0897 | 0.97986 | -3.331 | -3.8523 | 10.4839 | 8.9008 | 2.9256 | -0.36019 | 3.889% | -3.889%
12 | 9.292 | 3.0541 | 0.95 | Z | cloudy | 10.526 | 10.4523 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.7201 | 0.99823 | -2.0979 | 0.97967 | -3.3438 | -3.8527 | 10.4523 | 8.9306 | 2.9353 | -0.36144 | 3.89% | -3.89%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 10.526 | 10.4523 | 4 | 1.0181 | -2.4824 | 0.99911 | -3.7327 | 0.99811 | -2.1059 | 0.97949 | -3.3563 | -3.8528 | 10.4523 | 8.9593 | 2.9448 | -0.36265 | 3.89% | -3.89%
14 | 9.338 | 3.0693 | 0.95 | Z | cloudy | 10.526 | 10.4734 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1102 | 0.97939 | -3.3629 | -3.8529 | 10.4734 | 8.9747 | 2.9498 | -0.3633 | 3.891% | -3.891%
15 | 9.404 | 3.0909 | 0.95 | Z | cloudy | 10.526 | 10.5049 | 4 | 1.0178 | -2.5049 | 0.99861 | -3.7672 | 0.99778 | -2.1278 | 0.97898 | -3.3902 | -3.8533 | 10.5049 | 9.038 | 2.9707 | -0.36596 | 3.892% | -3.892%
16 | 9.594 | 3.1534 | 0.95 | Z | cloudy | 10.526 | 10.5155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.1786 | 0.97782 | -3.469 | -3.8544 | 10.5155 | 9.2204 | 3.0306 | -0.37362 | 3.894% | -3.894%
17 | 9.883 | 3.2484 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.2561 | 0.97603 | -3.5892 | -3.8561 | 10.526 | 9.4977 | 3.1217 | -0.38532 | 3.899% | -3.899%
18 | 10 | 3.2868 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.2875 | 0.97531 | -3.638 | -3.8567 | 10.526 | 9.6099 | 3.1586 | -0.39006 | 3.901% | -3.901%
19 | 9.966 | 3.2757 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99553 | -2.2784 | 0.97552 | -3.6238 | -3.8565 | 10.526 | 9.5773 | 3.1479 | -0.38868 | 3.9% | -3.9%
20 | 9.857 | 3.2398 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.9958 | -3.9588 | 0.99597 | -2.2491 | 0.97619 | -3.5784 | -3.8559 | 10.526 | 9.4727 | 3.1135 | -0.38426 | 3.898% | -3.898%
21 | 9.62 | 3.1619 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.1856 | 0.97766 | -3.4798 | -3.8545 | 10.526 | 9.2453 | 3.0388 | -0.37468 | 3.895% | -3.895%
22 | 9.139 | 3.0038 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.8699 | 0.97079 | -3.0934 | -5.7167 | 10.526 | 8.6087 | 2.8295 | -0.53028 | 5.802% | -5.802%
23 | 8.547 | 2.8093 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7148 | 0.97436 | -2.8523 | -5.7118 | 10.526 | 8.0522 | 2.6466 | -0.49482 | 5.789% | -5.789%
24 | 8.047 | 2.6449 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.5844 | 0.97734 | -2.6502 | -5.7078 | 10.526 | 7.582 | 2.4921 | -0.465 | 5.779% | -5.779%
1 | 7.716 | 2.5361 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.2132 | 0.97 | -2.2132 | -4.8877 | 5.263 | 7.1334 | 2.3446 | -0.58262 | 7.551% | -7.551%
2 | 7.517 | 2.4707 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.1102 | 0.97 | -2.1102 | -5.0273 | 5.263 | 6.9331 | 2.2788 | -0.58387 | 7.767% | -7.767%
3 | 7.407 | 2.4346 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.0536 | 0.97 | -2.0536 | -5.1041 | 5.263 | 6.8229 | 2.2426 | -0.58412 | 7.886% | -7.886%
4 | 7.398 | 2.4316 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.049 | 0.97 | -2.049 | -5.1103 | 5.263 | 6.8139 | 2.2396 | -0.58413 | 7.896% | -7.896%
5 | 7.563 | 2.4858 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0097 | -3.001 | 1.0097 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.9952 | 5.263 | 6.9793 | 2.294 | -0.58368 | 7.718% | -7.718%
6 | 7.986 | 2.6249 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0072 | -3.1754 | 1.0072 | -3.1754 | 0.97 | -2.3538 | 0.97 | -2.3538 | -4.6965 | 5.263 | 7.4066 | 2.4344 | -0.57942 | 7.255% | -7.255%
7 | 8.626 | 2.8352 | 0.95 | Z | very sunny | 5.263 | 5.2525 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.6915 | 0.97 | -2.6915 | -4.2348 | 5.2525 | 8.0618 | 2.6498 | -0.56424 | 6.541% | -6.541%
8 | 9.059 | 2.9775 | 0.95 | Z | very sunny | 5.263 | 5.1156 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -2.9235 | 0.97 | -2.9235 | -3.9156 | 5.1156 | 8.5112 | 2.7975 | -0.54782 | 6.047% | -6.047%
9 | 9.181 | 3.0176 | 0.95 | Z | very sunny | 5.263 | 4.7051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -2.9895 | 0.97 | -2.9895 | -3.8246 | 4.7051 | 8.6387 | 2.8394 | -0.54228 | 5.907% | -5.907%
10 | 9.23 | 3.0338 | 0.95 | Z | very sunny | 5.263 | 4.142 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.7879 | 4.142 | 8.6901 | 2.8563 | -0.53993 | 5.85% | -5.85%
11 | 9.261 | 3.0439 | 0.95 | Z | very sunny | 5.263 | 3.5736 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97155 | -3.0681 | 0.97155 | -3.0681 | -3.5736 | 3.5736 | 8.7504 | 2.8761 | -0.51057 | 5.513% | -5.513%
12 | 9.292 | 3.0541 | 0.95 | Z | very sunny | 5.263 | 3.2578 | 5 | 0.9993 | -3.7201 | 0.9993 | -3.7201 | 0.97391 | -3.139 | 0.97391 | -3.139 | -3.2578 | 3.2578 | 8.8259 | 2.9009 | -0.46607 | 5.016% | -5.016%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 5.263 | 3.3525 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97296 | -3.1337 | 0.97296 | -3.1337 | -3.3525 | 3.3525 | 8.8404 | 2.9057 | -0.48158 | 5.166% | -5.166%
14 | 9.338 | 3.0693 | 0.95 | Z | very sunny | 5.263 | 3.5052 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97163 | -3.1119 | 0.97163 | -3.1119 | -3.5052 | 3.5052 | 8.8331 | 2.9033 | -0.50491 | 5.407% | -5.407%
15 | 9.404 | 3.0909 | 0.95 | Z | very sunny | 5.263 | 3.942 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.1106 | 0.97 | -3.1106 | -3.6571 | 3.942 | 8.8729 | 2.9164 | -0.53108 | 5.647% | -5.647%
16 | 9.594 | 3.1534 | 0.95 | Z | very sunny | 5.263 | 4.4578 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.2144 | 0.97 | -3.2144 | -3.5132 | 4.4578 | 9.0735 | 2.9823 | -0.52046 | 5.425% | -5.425%
17 | 9.883 | 3.2484 | 0.95 | Z | very sunny | 5.263 | 4.9209 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.3736 | 0.97 | -3.3736 | -3.292 | 4.9209 | 9.3807 | 3.0833 | -0.50234 | 5.083% | -5.083%
18 | 10 | 3.2868 | 0.95 | Z | very sunny | 5.263 | 5.1893 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.4384 | 0.97 | -3.4384 | -3.2017 | 5.1893 | 9.5057 | 3.1244 | -0.49433 | 4.943% | -4.943%
19 | 9.966 | 3.2757 | 0.95 | Z | very sunny | 5.263 | 5.2577 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.4195 | 0.97 | -3.4195 | -3.228 | 5.2577 | 9.4693 | 3.1124 | -0.4967 | 4.984% | -4.984%
20 | 9.857 | 3.2398 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 0.9958 | -3.9588 | 0.9958 | -3.9588 | 0.97 | -3.3592 | 0.97 | -3.3592 | -3.312 | 5.263 | 9.3529 | 3.0742 | -0.50407 | 5.114% | -5.114%
21 | 9.62 | 3.1619 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.2287 | 0.97 | -3.2287 | -3.4934 | 5.263 | 9.1011 | 2.9914 | -0.51893 | 5.394% | -5.394%
22 | 9.139 | 3.0038 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -2.9668 | 0.97 | -2.9668 | -3.8559 | 5.263 | 8.5948 | 2.825 | -0.54423 | 5.955% | -5.955%
23 | 8.547 | 2.8093 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.6495 | 0.97 | -2.6495 | -4.2924 | 5.263 | 7.9803 | 2.623 | -0.56668 | 6.63% | -6.63%
24 | 8.047 | 2.6449 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0069 | -3.2006 | 1.0069 | -3.2006 | 0.97 | -2.3857 | 0.97 | -2.3857 | -4.653 | 5.263 | 7.4686 | 2.4548 | -0.57841 | 7.188% | -7.188%
1 | 7.716 | 2.5361 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.2132 | 0.97 | -2.2132 | -4.8877 | 5.263 | 7.1334 | 2.3446 | -0.58265 | 7.551% | -7.551%
2 | 7.517 | 2.4707 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.1102 | 0.97 | -2.1102 | -5.0273 | 5.263 | 6.9331 | 2.2788 | -0.58387 | 7.767% | -7.767%
3 | 7.407 | 2.4346 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.0536 | 0.97 | -2.0536 | -5.1041 | 5.263 | 6.8229 | 2.2426 | -0.58412 | 7.886% | -7.886%
4 | 7.398 | 2.4316 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.049 | 0.97 | -2.049 | -5.1103 | 5.263 | 6.8139 | 2.2396 | -0.58413 | 7.896% | -7.896%
5 | 7.563 | 2.4858 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0097 | -3.001 | 1.0097 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.9952 | 5.263 | 6.9793 | 2.294 | -0.58368 | 7.718% | -7.718%
6 | 7.986 | 2.6249 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0072 | -3.1754 | 1.0072 | -3.1754 | 0.97 | -2.3538 | 0.97 | -2.3538 | -4.6965 | 5.263 | 7.4066 | 2.4344 | -0.57942 | 7.255% | -7.255%
7 | 8.626 | 2.8352 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.6915 | 0.97 | -2.6915 | -4.2348 | 5.263 | 8.0618 | 2.6498 | -0.56424 | 6.541% | -6.541%
8 | 9.059 | 2.9775 | 0.95 | Z | moderate sun | 5.263 | 5.2577 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -2.9235 | 0.97 | -2.9235 | -3.9156 | 5.2577 | 8.5112 | 2.7975 | -0.54782 | 6.047% | -6.047%
9 | 9.181 | 3.0176 | 0.95 | Z | moderate sun | 5.263 | 5.2051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -2.9895 | 0.97 | -2.9895 | -3.8246 | 5.2051 | 8.6387 | 2.8394 | -0.54228 | 5.907% | -5.907%
10 | 9.23 | 3.0338 | 0.95 | Z | moderate sun | 5.263 | 5.0946 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.7879 | 5.0946 | 8.6901 | 2.8563 | -0.53993 | 5.85% | -5.85%
11 | 9.261 | 3.0439 | 0.95 | Z | moderate sun | 5.263 | 4.9788 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.0328 | 0.97 | -3.0328 | -3.7647 | 4.9788 | 8.7226 | 2.867 | -0.53842 | 5.814% | -5.814%
12 | 9.292 | 3.0541 | 0.95 | Z | moderate sun | 5.263 | 4.9156 | 5 | 0.9993 | -3.7201 | 0.9993 | -3.7201 | 0.97 | -3.0497 | 0.97 | -3.0497 | -3.7414 | 4.9156 | 8.7551 | 2.8777 | -0.53688 | 5.778% | -5.778%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 5.263 | 4.9841 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.066 | 0.97 | -3.066 | -3.7189 | 4.9841 | 8.7866 | 2.888 | -0.53536 | 5.743% | -5.743%
14 | 9.338 | 3.0693 | 0.95 | Z | moderate sun | 5.263 | 5.0156 | 5 | 0.99902 | -3.7394 | 0.99902 | -3.7394 | 0.97 | -3.0747 | 0.97 | -3.0747 | -3.7068 | 5.0156 | 8.8035 | 2.8936 | -0.53454 | 5.724% | -5.724%
15 | 9.404 | 3.0909 | 0.95 | Z | moderate sun | 5.263 | 5.1472 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.1106 | 0.97 | -3.1106 | -3.6571 | 5.1472 | 8.8729 | 2.9164 | -0.53109 | 5.647% | -5.647%
16 | 9.594 | 3.1534 | 0.95 | Z | moderate sun | 5.263 | 5.2367 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.2144 | 0.97 | -3.2144 | -3.5132 | 5.2367 | 9.0735 | 2.9823 | -0.52046 | 5.425% | -5.425%
17 | 9.883 | 3.2484 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.3736 | 0.97 | -3.3736 | -3.292 | 5.263 | 9.3807 | 3.0833 | -0.50234 | 5.083% | -5.083%
18 | 10 | 3.2868 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.4384 | 0.97 | -3.4384 | -3.2017 | 5.263 | 9.5057 | 3.1244 | -0.49433 | 4.943% | -4.943%
19 | 9.966 | 3.2757 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.4195 | 0.97 | -3.4195 | -3.228 | 5.263 | 9.4693 | 3.1124 | -0.4967 | 4.984% | -4.984%
20 | 9.857 | 3.2398 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.9958 | -3.9588 | 0.9958 | -3.9588 | 0.97 | -3.3592 | 0.97 | -3.3592 | -3.312 | 5.263 | 9.3529 | 3.0742 | -0.50407 | 5.114% | -5.114%
21 | 9.62 | 3.1619 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.2287 | 0.97 | -3.2287 | -3.4934 | 5.263 | 9.1011 | 2.9914 | -0.51893 | 5.394% | -5.394%
22 | 9.139 | 3.0038 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -2.9668 | 0.97 | -2.9668 | -3.8559 | 5.263 | 8.5948 | 2.825 | -0.54423 | 5.955% | -5.955%
23 | 8.547 | 2.8093 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.6495 | 0.97 | -2.6495 | -4.2924 | 5.263 | 7.9803 | 2.623 | -0.56668 | 6.63% | -6.63%
24 | 8.047 | 2.6449 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0069 | -3.2006 | 1.0069 | -3.2006 | 0.97 | -2.3857 | 0.97 | -2.3857 | -4.653 | 5.263 | 7.4686 | 2.4548 | -0.57841 | 7.188% | -7.188%
1 | 7.716 | 2.5361 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.2132 | 0.97 | -2.2132 | -4.8877 | 5.263 | 7.1334 | 2.3446 | -0.58265 | 7.551% | -7.551%
2 | 7.517 | 2.4707 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.1102 | 0.97 | -2.1102 | -5.0273 | 5.263 | 6.9331 | 2.2788 | -0.58387 | 7.767% | -7.767%
3 | 7.407 | 2.4346 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.0536 | 0.97 | -2.0536 | -5.1041 | 5.263 | 6.8229 | 2.2426 | -0.58412 | 7.886% | -7.886%
4 | 7.398 | 2.4316 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.049 | 0.97 | -2.049 | -5.1103 | 5.263 | 6.8139 | 2.2396 | -0.58413 | 7.896% | -7.896%
5 | 7.563 | 2.4858 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0097 | -3.001 | 1.0097 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.9952 | 5.263 | 6.9793 | 2.294 | -0.58368 | 7.718% | -7.718%
6 | 7.986 | 2.6249 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0072 | -3.1754 | 1.0072 | -3.1754 | 0.97 | -2.3538 | 0.97 | -2.3538 | -4.6965 | 5.263 | 7.4066 | 2.4344 | -0.57942 | 7.255% | -7.255%
7 | 8.626 | 2.8352 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.6915 | 0.97 | -2.6915 | -4.2348 | 5.263 | 8.0618 | 2.6498 | -0.56424 | 6.541% | -6.541%
8 | 9.059 | 2.9775 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -2.9235 | 0.97 | -2.9235 | -3.9156 | 5.263 | 8.5112 | 2.7975 | -0.54782 | 6.047% | -6.047%
9 | 9.181 | 3.0176 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -2.9895 | 0.97 | -2.9895 | -3.8246 | 5.263 | 8.6387 | 2.8394 | -0.54228 | 5.907% | -5.907%
10 | 9.23 | 3.0338 | 0.95 | Z | cloudy | 5.263 | 5.2577 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.7879 | 5.2577 | 8.6901 | 2.8563 | -0.53993 | 5.85% | -5.85%
11 | 9.261 | 3.0439 | 0.95 | Z | cloudy | 5.263 | 5.2419 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.0328 | 0.97 | -3.0328 | -3.7647 | 5.2419 | 8.7226 | 2.867 | -0.53842 | 5.814% | -5.814%
12 | 9.292 | 3.0541 | 0.95 | Z | cloudy | 5.263 | 5.2262 | 5 | 0.9993 | -3.7201 | 0.9993 | -3.7201 | 0.97 | -3.0497 | 0.97 | -3.0497 | -3.7414 | 5.2262 | 8.7551 | 2.8777 | -0.53688 | 5.778% | -5.778%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 5.263 | 5.2262 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.066 | 0.97 | -3.066 | -3.7189 | 5.2262 | 8.7866 | 2.888 | -0.53536 | 5.743% | -5.743%
14 | 9.338 | 3.0693 | 0.95 | Z | cloudy | 5.263 | 5.2367 | 5 | 0.99902 | -3.7394 | 0.99902 | -3.7394 | 0.97 | -3.0747 | 0.97 | -3.0747 | -3.7068 | 5.2367 | 8.8035 | 2.8936 | -0.53454 | 5.724% | -5.724%
15 | 9.404 | 3.0909 | 0.95 | Z | cloudy | 5.263 | 5.2525 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.1106 | 0.97 | -3.1106 | -3.6571 | 5.2525 | 8.8729 | 2.9164 | -0.53109 | 5.647% | -5.647%
16 | 9.594 | 3.1534 | 0.95 | Z | cloudy | 5.263 | 5.2577 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.2144 | 0.97 | -3.2144 | -3.5132 | 5.2577 | 9.0735 | 2.9823 | -0.52046 | 5.425% | -5.425%
17 | 9.883 | 3.2484 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.3736 | 0.97 | -3.3736 | -3.292 | 5.263 | 9.3807 | 3.0833 | -0.50234 | 5.083% | -5.083%
18 | 10 | 3.2868 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.4384 | 0.97 | -3.4384 | -3.2017 | 5.263 | 9.5057 | 3.1244 | -0.49433 | 4.943% | -4.943%
19 | 9.966 | 3.2757 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.4195 | 0.97 | -3.4195 | -3.228 | 5.263 | 9.4693 | 3.1124 | -0.4967 | 4.984% | -4.984%
20 | 9.857 | 3.2398 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.9958 | -3.9588 | 0.9958 | -3.9588 | 0.97 | -3.3592 | 0.97 | -3.3592 | -3.312 | 5.263 | 9.3529 | 3.0742 | -0.50407 | 5.114% | -5.114%
21 | 9.62 | 3.1619 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.2287 | 0.97 | -3.2287 | -3.4934 | 5.263 | 9.1011 | 2.9914 | -0.51893 | 5.394% | -5.394%
22 | 9.139 | 3.0038 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -2.9668 | 0.97 | -2.9668 | -3.8559 | 5.263 | 8.5948 | 2.825 | -0.54423 | 5.955% | -5.955%
23 | 8.547 | 2.8093 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.6495 | 0.97 | -2.6495 | -4.2924 | 5.263 | 7.9803 | 2.623 | -0.56668 | 6.63% | -6.63%
24 | 8.047 | 2.6449 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0069 | -3.2006 | 1.0069 | -3.2006 | 0.97 | -2.3857 | 0.97 | -2.3857 | -4.653 | 5.263 | 7.4686 | 2.4548 | -0.57841 | 7.188% | -7.188%
1 | 7.716 | 2.5361 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.2132 | 0.97 | -2.2132 | -4.8877 | 10.526 | 7.1334 | 2.3446 | -0.58265 | 7.551% | -7.551%
2 | 7.517 | 2.4707 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.1102 | 0.97 | -2.1102 | -5.0273 | 10.526 | 6.9331 | 2.2788 | -0.58387 | 7.767% | -7.767%
3 | 7.407 | 2.4346 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.0536 | 0.97 | -2.0536 | -5.1041 | 10.526 | 6.8229 | 2.2426 | -0.58412 | 7.886% | -7.886%
4 | 7.398 | 2.4316 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.049 | 0.97 | -2.049 | -5.1103 | 10.526 | 6.8139 | 2.2396 | -0.58413 | 7.896% | -7.896%
5 | 7.563 | 2.4858 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0097 | -3.001 | 1.0097 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.9952 | 10.526 | 6.9793 | 2.294 | -0.58368 | 7.718% | -7.718%
6 | 7.986 | 2.6249 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0072 | -3.1754 | 1.0072 | -3.1754 | 0.97 | -2.3538 | 0.97 | -2.3538 | -4.6965 | 10.526 | 7.4066 | 2.4344 | -0.57942 | 7.255% | -7.255%
7 | 8.626 | 2.8352 | 0.95 | Z | very sunny | 10.526 | 10.5049 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.6915 | 0.97 | -2.6915 | -4.2348 | 10.5049 | 8.0618 | 2.6498 | -0.56424 | 6.541% | -6.541%
8 | 9.059 | 2.9775 | 0.95 | Z | very sunny | 10.526 | 10.2313 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -2.9235 | 0.97 | -2.9235 | -3.9156 | 10.2313 | 8.5112 | 2.7975 | -0.54782 | 6.047% | -6.047%
9 | 9.181 | 3.0176 | 0.95 | Z | very sunny | 10.526 | 9.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -2.9895 | 0.97 | -2.9895 | -3.8246 | 9.4102 | 8.6387 | 2.8394 | -0.54228 | 5.907% | -5.907%
10 | 9.23 | 3.0338 | 0.95 | Z | very sunny | 10.526 | 8.284 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.7879 | 8.284 | 8.6901 | 2.8563 | -0.53993 | 5.85% | -5.85%
11 | 9.261 | 3.0439 | 0.95 | Z | very sunny | 10.526 | 7.1472 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.0328 | 0.97 | -3.0328 | -3.7647 | 7.1472 | 8.7226 | 2.867 | -0.53842 | 5.814% | -5.814%
12 | 9.292 | 3.0541 | 0.95 | Z | very sunny | 10.526 | 6.5156 | 5 | 0.9993 | -3.7201 | 0.9993 | -3.7201 | 0.97 | -3.0497 | 0.97 | -3.0497 | -3.7414 | 6.5156 | 8.7551 | 2.8777 | -0.53688 | 5.778% | -5.778%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 10.526 | 6.7051 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.066 | 0.97 | -3.066 | -3.7189 | 6.7051 | 8.7866 | 2.888 | -0.53536 | 5.743% | -5.743%
14 | 9.338 | 3.0693 | 0.95 | Z | very sunny | 10.526 | 7.0103 | 5 | 0.99902 | -3.7394 | 0.99902 | -3.7394 | 0.97 | -3.0747 | 0.97 | -3.0747 | -3.7068 | 7.0103 | 8.8035 | 2.8936 | -0.53454 | 5.724% | -5.724%
15 | 9.404 | 3.0909 | 0.95 | Z | very sunny | 10.526 | 7.884 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.1106 | 0.97 | -3.1106 | -3.6571 | 7.884 | 8.8729 | 2.9164 | -0.53109 | 5.647% | -5.647%
16 | 9.594 | 3.1534 | 0.95 | Z | very sunny | 10.526 | 8.9155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.2144 | 0.97 | -3.2144 | -3.5132 | 8.9155 | 9.0735 | 2.9823 | -0.52046 | 5.425% | -5.425%
17 | 9.883 | 3.2484 | 0.95 | Z | very sunny | 10.526 | 9.8418 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.3736 | 0.97 | -3.3736 | -3.292 | 9.8418 | 9.3807 | 3.0833 | -0.50234 | 5.083% | -5.083%
18 | 10 | 3.2868 | 0.95 | Z | very sunny | 10.526 | 10.3786 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.4384 | 0.97 | -3.4384 | -3.2017 | 10.3786 | 9.5057 | 3.1244 | -0.49433 | 4.943% | -4.943%
19 | 9.966 | 3.2757 | 0.95 | Z | very sunny | 10.526 | 10.5155 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.4195 | 0.97 | -3.4195 | -3.228 | 10.5155 | 9.4693 | 3.1124 | -0.4967 | 4.984% | -4.984%
20 | 9.857 | 3.2398 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 0.9958 | -3.9588 | 0.9958 | -3.9588 | 0.97 | -3.3592 | 0.97 | -3.3592 | -3.312 | 10.526 | 9.3529 | 3.0742 | -0.50407 | 5.114% | -5.114%
21 | 9.62 | 3.1619 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.2287 | 0.97 | -3.2287 | -3.4934 | 10.526 | 9.1011 | 2.9914 | -0.51893 | 5.394% | -5.394%
22 | 9.139 | 3.0038 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -2.9668 | 0.97 | -2.9668 | -3.8559 | 10.526 | 8.5948 | 2.825 | -0.54423 | 5.955% | -5.955%
23 | 8.547 | 2.8093 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.6495 | 0.97 | -2.6495 | -4.2924 | 10.526 | 7.9803 | 2.623 | -0.56668 | 6.63% | -6.63%
24 | 8.047 | 2.6449 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0069 | -3.2006 | 1.0069 | -3.2006 | 0.97 | -2.3857 | 0.97 | -2.3857 | -4.653 | 10.526 | 7.4686 | 2.4548 | -0.57841 | 7.188% | -7.188%
1 | 7.716 | 2.5361 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.2132 | 0.97 | -2.2132 | -4.8877 | 10.526 | 7.1334 | 2.3446 | -0.58265 | 7.551% | -7.551%
2 | 7.517 | 2.4707 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.1102 | 0.97 | -2.1102 | -5.0273 | 10.526 | 6.9331 | 2.2788 | -0.58387 | 7.767% | -7.767%
3 | 7.407 | 2.4346 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.0536 | 0.97 | -2.0536 | -5.1041 | 10.526 | 6.8229 | 2.2426 | -0.58412 | 7.886% | -7.886%
4 | 7.398 | 2.4316 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.049 | 0.97 | -2.049 | -5.1103 | 10.526 | 6.8139 | 2.2396 | -0.58413 | 7.896% | -7.896%
5 | 7.563 | 2.4858 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0097 | -3.001 | 1.0097 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.9952 | 10.526 | 6.9793 | 2.294 | -0.58368 | 7.718% | -7.718%
6 | 7.986 | 2.6249 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0072 | -3.1754 | 1.0072 | -3.1754 | 0.97 | -2.3538 | 0.97 | -2.3538 | -4.6965 | 10.526 | 7.4066 | 2.4344 | -0.57942 | 7.255% | -7.255%
7 | 8.626 | 2.8352 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.6915 | 0.97 | -2.6915 | -4.2348 | 10.526 | 8.0618 | 2.6498 | -0.56424 | 6.541% | -6.541%
8 | 9.059 | 2.9775 | 0.95 | Z | moderate sun | 10.526 | 10.5155 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -2.9235 | 0.97 | -2.9235 | -3.9156 | 10.5155 | 8.5112 | 2.7975 | -0.54782 | 6.047% | -6.047%
9 | 9.181 | 3.0176 | 0.95 | Z | moderate sun | 10.526 | 10.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -2.9895 | 0.97 | -2.9895 | -3.8246 | 10.4102 | 8.6387 | 2.8394 | -0.54228 | 5.907% | -5.907%
10 | 9.23 | 3.0338 | 0.95 | Z | moderate sun | 10.526 | 10.1892 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.7879 | 10.1892 | 8.6901 | 2.8563 | -0.53993 | 5.85% | -5.85%
11 | 9.261 | 3.0439 | 0.95 | Z | moderate sun | 10.526 | 9.9576 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.0328 | 0.97 | -3.0328 | -3.7647 | 9.9576 | 8.7226 | 2.867 | -0.53842 | 5.814% | -5.814%
12 | 9.292 | 3.0541 | 0.95 | Z | moderate sun | 10.526 | 9.8313 | 5 | 0.9993 | -3.7201 | 0.9993 | -3.7201 | 0.97 | -3.0497 | 0.97 | -3.0497 | -3.7414 | 9.8313 | 8.7551 | 2.8777 | -0.53688 | 5.778% | -5.778%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 10.526 | 9.9681 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.066 | 0.97 | -3.066 | -3.7189 | 9.9681 | 8.7866 | 2.888 | -0.53536 | 5.743% | -5.743%
14 | 9.338 | 3.0693 | 0.95 | Z | moderate sun | 10.526 | 10.0313 | 5 | 0.99902 | -3.7394 | 0.99902 | -3.7394 | 0.97 | -3.0747 | 0.97 | -3.0747 | -3.7068 | 10.0313 | 8.8035 | 2.8936 | -0.53454 | 5.724% | -5.724%
15 | 9.404 | 3.0909 | 0.95 | Z | moderate sun | 10.526 | 10.2944 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.1106 | 0.97 | -3.1106 | -3.6571 | 10.2944 | 8.8729 | 2.9164 | -0.53109 | 5.647% | -5.647%
16 | 9.594 | 3.1534 | 0.95 | Z | moderate sun | 10.526 | 10.4734 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.2144 | 0.97 | -3.2144 | -3.5132 | 10.4734 | 9.0735 | 2.9823 | -0.52046 | 5.425% | -5.425%
17 | 9.883 | 3.2484 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.3736 | 0.97 | -3.3736 | -3.292 | 10.526 | 9.3807 | 3.0833 | -0.50234 | 5.083% | -5.083%
18 | 10 | 3.2868 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.4384 | 0.97 | -3.4384 | -3.2017 | 10.526 | 9.5057 | 3.1244 | -0.49433 | 4.943% | -4.943%
19 | 9.966 | 3.2757 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.4195 | 0.97 | -3.4195 | -3.228 | 10.526 | 9.4693 | 3.1124 | -0.4967 | 4.984% | -4.984%
20 | 9.857 | 3.2398 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.9958 | -3.9588 | 0.9958 | -3.9588 | 0.97 | -3.3592 | 0.97 | -3.3592 | -3.312 | 10.526 | 9.3529 | 3.0742 | -0.50407 | 5.114% | -5.114%
21 | 9.62 | 3.1619 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.2287 | 0.97 | -3.2287 | -3.4934 | 10.526 | 9.1011 | 2.9914 | -0.51893 | 5.394% | -5.394%
22 | 9.139 | 3.0038 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -2.9668 | 0.97 | -2.9668 | -3.8559 | 10.526 | 8.5948 | 2.825 | -0.54423 | 5.955% | -5.955%
23 | 8.547 | 2.8093 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.6495 | 0.97 | -2.6495 | -4.2924 | 10.526 | 7.9803 | 2.623 | -0.56668 | 6.63% | -6.63%
24 | 8.047 | 2.6449 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0069 | -3.2006 | 1.0069 | -3.2006 | 0.97 | -2.3857 | 0.97 | -2.3857 | -4.653 | 10.526 | 7.4686 | 2.4548 | -0.57841 | 7.188% | -7.188%
1 | 7.716 | 2.5361 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.2132 | 0.97 | -2.2132 | -4.8877 | 10.526 | 7.1334 | 2.3446 | -0.58265 | 7.551% | -7.551%
2 | 7.517 | 2.4707 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.1102 | 0.97 | -2.1102 | -5.0273 | 10.526 | 6.9331 | 2.2788 | -0.58387 | 7.767% | -7.767%
3 | 7.407 | 2.4346 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.0536 | 0.97 | -2.0536 | -5.1041 | 10.526 | 6.8229 | 2.2426 | -0.58412 | 7.886% | -7.886%
4 | 7.398 | 2.4316 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.049 | 0.97 | -2.049 | -5.1103 | 10.526 | 6.8139 | 2.2396 | -0.58413 | 7.896% | -7.896%
5 | 7.563 | 2.4858 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0097 | -3.001 | 1.0097 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.9952 | 10.526 | 6.9793 | 2.294 | -0.58368 | 7.718% | -7.718%
6 | 7.986 | 2.6249 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0072 | -3.1754 | 1.0072 | -3.1754 | 0.97 | -2.3538 | 0.97 | -2.3538 | -4.6965 | 10.526 | 7.4066 | 2.4344 | -0.57942 | 7.255% | -7.255%
7 | 8.626 | 2.8352 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.6915 | 0.97 | -2.6915 | -4.2348 | 10.526 | 8.0618 | 2.6498 | -0.56424 | 6.541% | -6.541%
8 | 9.059 | 2.9775 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -2.9235 | 0.97 | -2.9235 | -3.9156 | 10.526 | 8.5112 | 2.7975 | -0.54782 | 6.047% | -6.047%
9 | 9.181 | 3.0176 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -2.9895 | 0.97 | -2.9895 | -3.8246 | 10.526 | 8.6387 | 2.8394 | -0.54228 | 5.907% | -5.907%
10 | 9.23 | 3.0338 | 0.95 | Z | cloudy | 10.526 | 10.5155 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.7879 | 10.5155 | 8.6901 | 2.8563 | -0.53993 | 5.85% | -5.85%
11 | 9.261 | 3.0439 | 0.95 | Z | cloudy | 10.526 | 10.4839 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.0328 | 0.97 | -3.0328 | -3.7647 | 10.4839 | 8.7226 | 2.867 | -0.53842 | 5.814% | -5.814%
12 | 9.292 | 3.0541 | 0.95 | Z | cloudy | 10.526 | 10.4523 | 5 | 0.9993 | -3.7201 | 0.9993 | -3.7201 | 0.97 | -3.0497 | 0.97 | -3.0497 | -3.7414 | 10.4523 | 8.7551 | 2.8777 | -0.53688 | 5.778% | -5.778%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 10.526 | 10.4523 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.066 | 0.97 | -3.066 | -3.7189 | 10.4523 | 8.7866 | 2.888 | -0.53536 | 5.743% | -5.743%
14 | 9.338 | 3.0693 | 0.95 | Z | cloudy | 10.526 | 10.4734 | 5 | 0.99902 | -3.7394 | 0.99902 | -3.7394 | 0.97 | -3.0747 | 0.97 | -3.0747 | -3.7068 | 10.4734 | 8.8035 | 2.8936 | -0.53454 | 5.724% | -5.724%
15 | 9.404 | 3.0909 | 0.95 | Z | cloudy | 10.526 | 10.5049 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.1106 | 0.97 | -3.1106 | -3.6571 | 10.5049 | 8.8729 | 2.9164 | -0.53109 | 5.647% | -5.647%
16 | 9.594 | 3.1534 | 0.95 | Z | cloudy | 10.526 | 10.5155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.2144 | 0.97 | -3.2144 | -3.5132 | 10.5155 | 9.0735 | 2.9823 | -0.52046 | 5.425% | -5.425%
17 | 9.883 | 3.2484 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.3736 | 0.97 | -3.3736 | -3.292 | 10.526 | 9.3807 | 3.0833 | -0.50234 | 5.083% | -5.083%
18 | 10 | 3.2868 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.4384 | 0.97 | -3.4384 | -3.2017 | 10.526 | 9.5057 | 3.1244 | -0.49433 | 4.943% | -4.943%
19 | 9.966 | 3.2757 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.4195 | 0.97 | -3.4195 | -3.228 | 10.526 | 9.4693 | 3.1124 | -0.4967 | 4.984% | -4.984%
20 | 9.857 | 3.2398 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.9958 | -3.9588 | 0.9958 | -3.9588 | 0.97 | -3.3592 | 0.97 | -3.3592 | -3.312 | 10.526 | 9.3529 | 3.0742 | -0.50407 | 5.114% | -5.114%
21 | 9.62 | 3.1619 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.2287 | 0.97 | -3.2287 | -3.4934 | 10.526 | 9.1011 | 2.9914 | -0.51893 | 5.394% | -5.394%
22 | 9.139 | 3.0038 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -2.9668 | 0.97 | -2.9668 | -3.8559 | 10.526 | 8.5948 | 2.825 | -0.54423 | 5.955% | -5.955%
23 | 8.547 | 2.8093 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.6495 | 0.97 | -2.6495 | -4.2924 | 10.526 | 7.9803 | 2.623 | -0.56668 | 6.63% | -6.63%
24 | 8.047 | 2.6449 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0069 | -3.2006 | 1.0069 | -3.2006 | 0.97 | -2.3857 | 0.97 | -2.3857 | -4.653 | 10.526 | 7.4686 | 2.4548 | -0.57841 | 7.188% | -7.188%
1 | 7.716 | 1.5668 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1789 | 1.0293 | -0.93727 | 1.0037 | -3.0407 | -5.263 | 5.263 | 7.518 | 1.5266 | -0.19797 | 2.566% | -2.566%
2 | 7.517 | 1.5264 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0295 | -0.91002 | 1.0046 | -2.9568 | -5.263 | 5.263 | 7.3242 | 1.4872 | -0.19279 | 2.565% | -2.565%
3 | 7.407 | 1.5041 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.89497 | 1.0052 | -2.9105 | -5.263 | 5.263 | 7.217 | 1.4655 | -0.18995 | 2.565% | -2.565%
4 | 7.398 | 1.5022 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.89374 | 1.0052 | -2.9067 | -5.263 | 5.263 | 7.2083 | 1.4637 | -0.18972 | 2.565% | -2.565%
5 | 7.563 | 1.5357 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.91632 | 1.0044 | -2.9762 | -5.263 | 5.263 | 7.369 | 1.4963 | -0.19398 | 2.565% | -2.565%
6 | 7.986 | 1.6216 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.97432 | 1.0024 | -3.1548 | -5.263 | 5.263 | 7.7811 | 1.58 | -0.20489 | 2.566% | -2.566%
7 | 8.626 | 1.7516 | 0.98 | Z | very sunny | 5.263 | 5.2525 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0632 | 0.99938 | -3.4275 | -5.2525 | 5.2525 | 8.406 | 1.7069 | -0.22004 | 2.551% | -2.551%
8 | 9.059 | 1.8395 | 0.98 | Z | very sunny | 5.263 | 5.1156 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.028 | -1.1267 | 0.9976 | -3.6163 | -5.1156 | 5.1156 | 8.8339 | 1.7938 | -0.22505 | 2.484% | -2.484%
9 | 9.181 | 1.8643 | 0.98 | Z | very sunny | 5.263 | 4.7051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0289 | -1.1547 | 0.99803 | -3.6798 | -4.7051 | 4.7051 | 8.9715 | 1.8217 | -0.20955 | 2.282% | -2.282%
10 | 9.23 | 1.8742 | 0.98 | Z | very sunny | 5.263 | 4.142 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0303 | -1.1767 | 0.99919 | -3.716 | -4.142 | 4.142 | 9.0447 | 1.8366 | -0.18528 | 2.007% | -2.007%
11 | 9.261 | 1.8805 | 0.98 | Z | very sunny | 5.263 | 3.5736 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0316 | -1.1954 | 1.0004 | -3.7438 | -3.5736 | 3.5736 | 9.0994 | 1.8477 | -0.16163 | 1.745% | -1.745%
12 | 9.292 | 1.8868 | 0.98 | Z | very sunny | 5.263 | 3.2578 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0324 | -1.2083 | 1.001 | -3.7656 | -3.2578 | 3.2578 | 9.1443 | 1.8568 | -0.14775 | 1.59% | -1.59%
13 | 9.322 | 1.8929 | 0.98 | Z | very sunny | 5.263 | 3.3525 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0322 | -1.2109 | 1.0007 | -3.777 | -3.3525 | 3.3525 | 9.1712 | 1.8623 | -0.15085 | 1.618% | -1.618%
14 | 9.338 | 1.8962 | 0.98 | Z | very sunny | 5.263 | 3.5052 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0318 | -1.209 | 1.0003 | -3.7798 | -3.5052 | 3.5052 | 9.1799 | 1.8641 | -0.1581 | 1.693% | -1.693%
15 | 9.404 | 1.9096 | 0.98 | Z | very sunny | 5.263 | 3.942 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0306 | -1.2063 | 0.99883 | -3.7963 | -3.942 | 3.942 | 9.2246 | 1.8731 | -0.17938 | 1.907% | -1.907%
16 | 9.594 | 1.9481 | 0.98 | Z | very sunny | 5.263 | 4.4578 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.029 | -1.2187 | 0.99659 | -3.8642 | -4.4578 | 4.4578 | 9.3866 | 1.906 | -0.20737 | 2.161% | -2.161%
17 | 9.883 | 2.0068 | 0.98 | Z | very sunny | 5.263 | 4.9209 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1088 | 1.0274 | -1.2457 | 0.99394 | -3.9759 | -4.9209 | 4.9209 | 9.646 | 1.9587 | -0.23704 | 2.398% | -2.398%
18 | 10 | 2.0306 | 0.98 | Z | very sunny | 5.263 | 5.1893 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0265 | -1.2545 | 0.99267 | -4.019 | -5.1893 | 5.1893 | 9.7467 | 1.9792 | -0.25329 | 2.533% | -2.533%
19 | 9.966 | 2.0237 | 0.98 | Z | very sunny | 5.263 | 5.2577 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2479 | 0.99266 | -4.0024 | -5.2577 | 5.2577 | 9.7102 | 1.9717 | -0.25583 | 2.567% | -2.567%
20 | 9.857 | 2.0015 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.0062 | -4.0975 | 1.0265 | -1.2326 | 0.9932 | -3.9551 | -5.263 | 5.263 | 9.6037 | 1.9501 | -0.25327 | 2.569% | -2.569%
21 | 9.62 | 1.9534 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.1997 | 0.99439 | -3.8528 | -5.263 | 5.263 | 9.3729 | 1.9032 | -0.24713 | 2.569% | -2.569%
22 | 9.139 | 1.8558 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1331 | 0.99677 | -3.646 | -5.263 | 5.263 | 8.9043 | 1.8081 | -0.23468 | 2.568% | -2.568%
23 | 8.547 | 1.7355 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0515 | 0.99968 | -3.393 | -5.263 | 5.263 | 8.3276 | 1.691 | -0.21938 | 2.567% | -2.567%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.98269 | 1.0021 | -3.1807 | -5.263 | 5.263 | 7.8405 | 1.5921 | -0.20647 | 2.566% | -2.566%
1 | 7.716 | 1.5668 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.93728 | 1.0037 | -3.0407 | -5.263 | 5.263 | 7.5181 | 1.5266 | -0.19792 | 2.565% | -2.565%
2 | 7.517 | 1.5264 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0295 | -0.91002 | 1.0046 | -2.9568 | -5.263 | 5.263 | 7.3242 | 1.4872 | -0.19279 | 2.565% | -2.565%
3 | 7.407 | 1.5041 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.89497 | 1.0052 | -2.9105 | -5.263 | 5.263 | 7.217 | 1.4655 | -0.18995 | 2.565% | -2.565%
4 | 7.398 | 1.5022 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.89374 | 1.0052 | -2.9067 | -5.263 | 5.263 | 7.2083 | 1.4637 | -0.18972 | 2.565% | -2.565%
5 | 7.563 | 1.5357 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.91632 | 1.0044 | -2.9762 | -5.263 | 5.263 | 7.369 | 1.4963 | -0.19398 | 2.565% | -2.565%
6 | 7.986 | 1.6216 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.97432 | 1.0024 | -3.1548 | -5.263 | 5.263 | 7.7811 | 1.58 | -0.20489 | 2.566% | -2.566%
7 | 8.626 | 1.7516 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0281 | -1.0623 | 0.9993 | -3.4267 | -5.263 | 5.263 | 8.4046 | 1.7066 | -0.22142 | 2.567% | -2.567%
8 | 9.059 | 1.8395 | 0.98 | Z | moderate sun | 5.263 | 5.2577 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1222 | 0.99718 | -3.6118 | -5.2577 | 5.2577 | 8.8266 | 1.7923 | -0.23237 | 2.565% | -2.565%
9 | 9.181 | 1.8643 | 0.98 | Z | moderate sun | 5.263 | 5.2051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0276 | -1.1405 | 0.99672 | -3.6656 | -5.2051 | 5.2051 | 8.9479 | 1.8169 | -0.23311 | 2.539% | -2.539%
10 | 9.23 | 1.8742 | 0.98 | Z | moderate sun | 5.263 | 5.0946 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0278 | -1.1509 | 0.9968 | -3.6902 | -5.0946 | 5.0946 | 9.0016 | 1.8279 | -0.22837 | 2.474% | -2.474%
11 | 9.261 | 1.8805 | 0.98 | Z | moderate sun | 5.263 | 4.9788 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0281 | -1.1583 | 0.99694 | -3.7067 | -4.9788 | 4.9788 | 9.0371 | 1.8351 | -0.22386 | 2.417% | -2.417%
12 | 9.292 | 1.8868 | 0.98 | Z | moderate sun | 5.263 | 4.9156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0282 | -1.1643 | 0.99695 | -3.7217 | -4.9156 | 4.9156 | 9.0703 | 1.8418 | -0.22173 | 2.386% | -2.386%
13 | 9.322 | 1.8929 | 0.98 | Z | moderate sun | 5.263 | 4.9841 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.028 | -1.1666 | 0.99663 | -3.7327 | -4.9841 | 4.9841 | 9.0964 | 1.8471 | -0.22559 | 2.42% | -2.42%
14 | 9.338 | 1.8962 | 0.98 | Z | moderate sun | 5.263 | 5.0156 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0279 | -1.168 | 0.99647 | -3.7387 | -5.0156 | 5.0156 | 9.1106 | 1.85 | -0.22743 | 2.436% | -2.436%
15 | 9.404 | 1.9096 | 0.98 | Z | moderate sun | 5.263 | 5.1472 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0275 | -1.1735 | 0.99581 | -3.7635 | -5.1472 | 5.1472 | 9.1688 | 1.8618 | -0.23515 | 2.501% | -2.501%
16 | 9.594 | 1.9481 | 0.98 | Z | moderate sun | 5.263 | 5.2367 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.027 | -1.1974 | 0.99464 | -3.8429 | -5.2367 | 5.2367 | 9.3498 | 1.8986 | -0.24417 | 2.545% | -2.545%
17 | 9.883 | 2.0068 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1088 | 1.0265 | -1.2362 | 0.99307 | -3.9663 | -5.263 | 5.263 | 9.6291 | 1.9553 | -0.25394 | 2.569% | -2.569%
18 | 10 | 2.0306 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0263 | -1.2524 | 0.99248 | -4.017 | -5.263 | 5.263 | 9.743 | 1.9784 | -0.25697 | 2.57% | -2.57%
19 | 9.966 | 2.0237 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2477 | 0.99265 | -4.0022 | -5.263 | 5.263 | 9.7099 | 1.9717 | -0.25609 | 2.57% | -2.57%
20 | 9.857 | 2.0015 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.0062 | -4.0975 | 1.0265 | -1.2326 | 0.9932 | -3.9551 | -5.263 | 5.263 | 9.6037 | 1.9501 | -0.25327 | 2.569% | -2.569%
21 | 9.62 | 1.9534 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.1997 | 0.99439 | -3.8528 | -5.263 | 5.263 | 9.3729 | 1.9032 | -0.24713 | 2.569% | -2.569%
22 | 9.139 | 1.8558 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1331 | 0.99677 | -3.646 | -5.263 | 5.263 | 8.9043 | 1.8081 | -0.23468 | 2.568% | -2.568%
23 | 8.547 | 1.7355 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0515 | 0.99968 | -3.393 | -5.263 | 5.263 | 8.3276 | 1.691 | -0.21938 | 2.567% | -2.567%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.98269 | 1.0021 | -3.1807 | -5.263 | 5.263 | 7.8405 | 1.5921 | -0.20647 | 2.566% | -2.566%
1 | 7.716 | 1.5668 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.93728 | 1.0037 | -3.0407 | -5.263 | 5.263 | 7.5181 | 1.5266 | -0.19792 | 2.565% | -2.565%
2 | 7.517 | 1.5264 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0295 | -0.91002 | 1.0046 | -2.9568 | -5.263 | 5.263 | 7.3242 | 1.4872 | -0.19279 | 2.565% | -2.565%
3 | 7.407 | 1.5041 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.89497 | 1.0052 | -2.9105 | -5.263 | 5.263 | 7.217 | 1.4655 | -0.18995 | 2.565% | -2.565%
4 | 7.398 | 1.5022 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.89374 | 1.0052 | -2.9067 | -5.263 | 5.263 | 7.2083 | 1.4637 | -0.18972 | 2.565% | -2.565%
5 | 7.563 | 1.5357 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.91632 | 1.0044 | -2.9762 | -5.263 | 5.263 | 7.369 | 1.4963 | -0.19398 | 2.565% | -2.565%
6 | 7.986 | 1.6216 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.97432 | 1.0024 | -3.1548 | -5.263 | 5.263 | 7.7811 | 1.58 | -0.20489 | 2.566% | -2.566%
7 | 8.626 | 1.7516 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0281 | -1.0623 | 0.9993 | -3.4267 | -5.263 | 5.263 | 8.4046 | 1.7066 | -0.22142 | 2.567% | -2.567%
8 | 9.059 | 1.8395 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1221 | 0.99717 | -3.6117 | -5.263 | 5.263 | 8.8264 | 1.7923 | -0.23261 | 2.568% | -2.568%
9 | 9.181 | 1.8643 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0274 | -1.1389 | 0.99657 | -3.664 | -5.263 | 5.263 | 8.9452 | 1.8164 | -0.23577 | 2.568% | -2.568%
10 | 9.23 | 1.8742 | 0.98 | Z | cloudy | 5.263 | 5.2577 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0274 | -1.1459 | 0.99634 | -3.6852 | -5.2577 | 5.2577 | 8.9932 | 1.8261 | -0.23679 | 2.565% | -2.565%
11 | 9.261 | 1.8805 | 0.98 | Z | cloudy | 5.263 | 5.2419 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0274 | -1.1506 | 0.99623 | -3.6989 | -5.2419 | 5.2419 | 9.0241 | 1.8324 | -0.23686 | 2.558% | -2.558%
12 | 9.292 | 1.8868 | 0.98 | Z | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0274 | -1.1553 | 0.99611 | -3.7127 | -5.2262 | 5.2262 | 9.0551 | 1.8387 | -0.23693 | 2.55% | -2.55%
13 | 9.322 | 1.8929 | 0.98 | Z | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0273 | -1.1595 | 0.99596 | -3.7255 | -5.2262 | 5.2262 | 9.0843 | 1.8446 | -0.2377 | 2.55% | -2.55%
14 | 9.338 | 1.8962 | 0.98 | Z | cloudy | 5.263 | 5.2367 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0273 | -1.162 | 0.99591 | -3.7327 | -5.2367 | 5.2367 | 9.1004 | 1.8479 | -0.23761 | 2.544% | -2.544%
15 | 9.404 | 1.9096 | 0.98 | Z | cloudy | 5.263 | 5.2525 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0272 | -1.1707 | 0.99554 | -3.7607 | -5.2525 | 5.2525 | 9.164 | 1.8608 | -0.24003 | 2.552% | -2.552%
16 | 9.594 | 1.9481 | 0.98 | Z | cloudy | 5.263 | 5.2577 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0269 | -1.1962 | 0.99453 | -3.8417 | -5.2577 | 5.2577 | 9.3478 | 1.8982 | -0.2462 | 2.566% | -2.566%
17 | 9.883 | 2.0068 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1088 | 1.0265 | -1.2362 | 0.99307 | -3.9663 | -5.263 | 5.263 | 9.6291 | 1.9553 | -0.25394 | 2.569% | -2.569%
18 | 10 | 2.0306 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0263 | -1.2524 | 0.99248 | -4.017 | -5.263 | 5.263 | 9.743 | 1.9784 | -0.25697 | 2.57% | -2.57%
19 | 9.966 | 2.0237 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2477 | 0.99265 | -4.0022 | -5.263 | 5.263 | 9.7099 | 1.9717 | -0.25609 | 2.57% | -2.57%
20 | 9.857 | 2.0015 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.0062 | -4.0975 | 1.0265 | -1.2326 | 0.9932 | -3.9551 | -5.263 | 5.263 | 9.6037 | 1.9501 | -0.25327 | 2.569% | -2.569%
21 | 9.62 | 1.9534 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.1997 | 0.99439 | -3.8528 | -5.263 | 5.263 | 9.3729 | 1.9032 | -0.24713 | 2.569% | -2.569%
22 | 9.139 | 1.8558 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1331 | 0.99677 | -3.646 | -5.263 | 5.263 | 8.9043 | 1.8081 | -0.23468 | 2.568% | -2.568%
23 | 8.547 | 1.7355 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0515 | 0.99968 | -3.393 | -5.263 | 5.263 | 8.3276 | 1.691 | -0.21938 | 2.567% | -2.567%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.98269 | 1.0021 | -3.1807 | -5.263 | 5.263 | 7.8405 | 1.5921 | -0.20647 | 2.566% | -2.566%
1 | 7.716 | 1.5668 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.79458 | 0.99013 | -2.898 | -10.526 | 10.526 | 7.3162 | 1.4856 | -0.39982 | 5.182% | -5.182%
2 | 7.517 | 1.5264 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.76772 | 0.99107 | -2.8145 | -10.526 | 10.526 | 7.1275 | 1.4473 | -0.38946 | 5.181% | -5.181%
3 | 7.407 | 1.5041 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.75289 | 0.99158 | -2.7684 | -10.526 | 10.526 | 7.0233 | 1.4261 | -0.38373 | 5.181% | -5.181%
4 | 7.398 | 1.5022 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.75168 | 0.99163 | -2.7647 | -10.526 | 10.526 | 7.0147 | 1.4244 | -0.38326 | 5.181% | -5.181%
5 | 7.563 | 1.5357 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0429 | -1.0542 | 1.0176 | -3.114 | 1.0156 | -0.77392 | 0.99085 | -2.8338 | -10.526 | 10.526 | 7.1711 | 1.4562 | -0.39186 | 5.181% | -5.181%
6 | 7.986 | 1.6216 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.83106 | 0.98884 | -3.0116 | -10.526 | 10.526 | 7.5721 | 1.5376 | -0.41391 | 5.183% | -5.183%
7 | 8.626 | 1.7516 | 0.98 | Z | very sunny | 10.526 | 10.5049 | 3 | 1.0416 | -1.2023 | 1.0124 | -3.5666 | 1.0144 | -0.91934 | 0.98592 | -3.2837 | -10.5049 | 10.5049 | 8.1812 | 1.6613 | -0.44485 | 5.157% | -5.157%
8 | 9.059 | 1.8395 | 0.98 | Z | very sunny | 10.526 | 10.2313 | 3 | 1.041 | -1.2629 | 1.0102 | -3.7525 | 1.0145 | -0.98584 | 0.98453 | -3.4755 | -10.2313 | 10.2313 | 8.6041 | 1.7471 | -0.45495 | 5.022% | -5.022%
9 | 9.181 | 1.8643 | 0.98 | Z | very sunny | 10.526 | 9.4102 | 3 | 1.0409 | -1.28 | 1.0096 | -3.805 | 1.0166 | -1.0254 | 0.98606 | -3.5504 | -9.4102 | 9.4102 | 8.7575 | 1.7783 | -0.4235 | 4.613% | -4.613%
10 | 9.23 | 1.8742 | 0.98 | Z | very sunny | 10.526 | 8.284 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0195 | -1.0631 | 0.98868 | -3.6024 | -8.284 | 8.284 | 8.8555 | 1.7982 | -0.37447 | 4.057% | -4.057%
11 | 9.261 | 1.8805 | 0.98 | Z | very sunny | 10.526 | 7.1472 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0223 | -1.098 | 0.99136 | -3.6463 | -7.1472 | 7.1472 | 8.9362 | 1.8146 | -0.32478 | 3.507% | -3.507%
12 | 9.292 | 1.8868 | 0.98 | Z | very sunny | 10.526 | 6.5156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.024 | -1.1197 | 0.99282 | -3.677 | -6.5156 | 6.5156 | 8.9953 | 1.8266 | -0.29668 | 3.193% | -3.193%
13 | 9.322 | 1.8929 | 0.98 | Z | very sunny | 10.526 | 6.7051 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0235 | -1.1195 | 0.99228 | -3.6856 | -6.7051 | 6.7051 | 9.0172 | 1.831 | -0.30479 | 3.27% | -3.27%
14 | 9.338 | 1.8962 | 0.98 | Z | very sunny | 10.526 | 7.0103 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0227 | -1.1133 | 0.99142 | -3.6841 | -7.0103 | 7.0103 | 9.0186 | 1.8313 | -0.31943 | 3.421% | -3.421%
15 | 9.404 | 1.9096 | 0.98 | Z | very sunny | 10.526 | 7.884 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0203 | -1.0982 | 0.98887 | -3.6882 | -7.884 | 7.884 | 9.0415 | 1.8359 | -0.36254 | 3.855% | -3.855%
16 | 9.594 | 1.9481 | 0.98 | Z | very sunny | 10.526 | 8.9155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0173 | -1.0957 | 0.98529 | -3.7412 | -8.9155 | 8.9155 | 9.175 | 1.8631 | -0.41904 | 4.368% | -4.368%
17 | 9.883 | 2.0068 | 0.98 | Z | very sunny | 10.526 | 9.8418 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1088 | 1.0144 | -1.1085 | 0.9814 | -3.8386 | -9.8418 | 9.8418 | 9.4041 | 1.9096 | -0.47895 | 4.846% | -4.846%
18 | 10 | 2.0306 | 0.98 | Z | very sunny | 10.526 | 10.3786 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0128 | -1.1092 | 0.97942 | -3.8738 | -10.3786 | 10.3786 | 9.4883 | 1.9267 | -0.51172 | 5.117% | -5.117%
19 | 9.966 | 2.0237 | 0.98 | Z | very sunny | 10.526 | 10.5155 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0125 | -1.1007 | 0.97923 | -3.8552 | -10.5155 | 10.5155 | 9.4492 | 1.9187 | -0.51683 | 5.186% | -5.186%
20 | 9.857 | 2.0015 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.0062 | -4.0975 | 1.0126 | -1.0855 | 0.97975 | -3.808 | -10.526 | 10.526 | 9.3453 | 1.8977 | -0.51165 | 5.191% | -5.191%
21 | 9.62 | 1.9534 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0129 | -1.0531 | 0.98092 | -3.7062 | -10.526 | 10.526 | 9.1207 | 1.852 | -0.49925 | 5.19% | -5.19%
22 | 9.139 | 1.8558 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -0.98751 | 0.98328 | -3.5004 | -10.526 | 10.526 | 8.6649 | 1.7595 | -0.4741 | 5.188% | -5.188%
23 | 8.547 | 1.7355 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0143 | -0.90705 | 0.98616 | -3.2486 | -10.526 | 10.526 | 8.1038 | 1.6456 | -0.44318 | 5.185% | -5.185%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.83931 | 0.98855 | -3.0373 | -10.526 | 10.526 | 7.6299 | 1.5493 | -0.41709 | 5.183% | -5.183%
1 | 7.716 | 1.5668 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.79457 | 0.99013 | -2.898 | -10.526 | 10.526 | 7.3162 | 1.4856 | -0.39983 | 5.182% | -5.182%
2 | 7.517 | 1.5264 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.76772 | 0.99107 | -2.8145 | -10.526 | 10.526 | 7.1275 | 1.4473 | -0.38946 | 5.181% | -5.181%
3 | 7.407 | 1.5041 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.75289 | 0.99158 | -2.7684 | -10.526 | 10.526 | 7.0233 | 1.4261 | -0.38373 | 5.181% | -5.181%
4 | 7.398 | 1.5022 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.75168 | 0.99163 | -2.7647 | -10.526 | 10.526 | 7.0147 | 1.4244 | -0.38326 | 5.181% | -5.181%
5 | 7.563 | 1.5357 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0429 | -1.0542 | 1.0176 | -3.114 | 1.0156 | -0.77392 | 0.99085 | -2.8338 | -10.526 | 10.526 | 7.1711 | 1.4562 | -0.39186 | 5.181% | -5.181%
6 | 7.986 | 1.6216 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.83106 | 0.98884 | -3.0116 | -10.526 | 10.526 | 7.5721 | 1.5376 | -0.41391 | 5.183% | -5.183%
7 | 8.626 | 1.7516 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0416 | -1.2023 | 1.0124 | -3.5666 | 1.0142 | -0.91777 | 0.98578 | -3.2821 | -10.526 | 10.526 | 8.1787 | 1.6608 | -0.4473 | 5.185% | -5.185%
8 | 9.059 | 1.8395 | 0.98 | Z | moderate sun | 10.526 | 10.5155 | 3 | 1.041 | -1.2629 | 1.0102 | -3.7525 | 1.0137 | -0.97692 | 0.9837 | -3.4665 | -10.5155 | 10.5155 | 8.5896 | 1.7442 | -0.46944 | 5.182% | -5.182%
9 | 9.181 | 1.8643 | 0.98 | Z | moderate sun | 10.526 | 10.4102 | 3 | 1.0409 | -1.28 | 1.0096 | -3.805 | 1.0138 | -0.99649 | 0.98338 | -3.5215 | -10.4102 | 10.4102 | 8.7101 | 1.7687 | -0.47095 | 5.13% | -5.13%
10 | 9.23 | 1.8742 | 0.98 | Z | moderate sun | 10.526 | 10.1892 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0144 | -1.0103 | 0.9838 | -3.5496 | -10.1892 | 10.1892 | 8.7683 | 1.7805 | -0.46166 | 5.002% | -5.002%
11 | 9.261 | 1.8805 | 0.98 | Z | moderate sun | 10.526 | 9.9576 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.015 | -1.021 | 0.98425 | -3.5694 | -9.9576 | 9.9576 | 8.8085 | 1.7886 | -0.45251 | 4.886% | -4.886%
12 | 9.292 | 1.8868 | 0.98 | Z | moderate sun | 10.526 | 9.8313 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0153 | -1.0288 | 0.98442 | -3.5861 | -9.8313 | 9.8313 | 8.8438 | 1.7958 | -0.44817 | 4.823% | -4.823%
13 | 9.322 | 1.8929 | 0.98 | Z | moderate sun | 10.526 | 9.9681 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0149 | -1.0291 | 0.98392 | -3.5951 | -9.9681 | 9.9681 | 8.866 | 1.8003 | -0.456 | 4.892% | -4.892%
14 | 9.338 | 1.8962 | 0.98 | Z | moderate sun | 10.526 | 10.0313 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0147 | -1.0295 | 0.98368 | -3.6002 | -10.0313 | 10.0313 | 8.8783 | 1.8028 | -0.45973 | 4.923% | -4.923%
15 | 9.404 | 1.9096 | 0.98 | Z | moderate sun | 10.526 | 10.2944 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0139 | -1.0311 | 0.98268 | -3.6211 | -10.2944 | 10.2944 | 8.9286 | 1.813 | -0.47537 | 5.055% | -5.055%
16 | 9.594 | 1.9481 | 0.98 | Z | moderate sun | 10.526 | 10.4734 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0132 | -1.052 | 0.98128 | -3.6975 | -10.4734 | 10.4734 | 9.1004 | 1.8479 | -0.49364 | 5.145% | -5.145%
17 | 9.883 | 2.0068 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1088 | 1.0126 | -1.089 | 0.97962 | -3.8192 | -10.526 | 10.526 | 9.37 | 1.9027 | -0.51301 | 5.191% | -5.191%
18 | 10 | 2.0306 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0124 | -1.105 | 0.97903 | -3.8696 | -10.526 | 10.526 | 9.4809 | 1.9252 | -0.51914 | 5.191% | -5.191%
19 | 9.966 | 2.0237 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0125 | -1.1004 | 0.9792 | -3.8549 | -10.526 | 10.526 | 9.4486 | 1.9186 | -0.51736 | 5.191% | -5.191%
20 | 9.857 | 2.0015 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.0062 | -4.0975 | 1.0126 | -1.0855 | 0.97975 | -3.808 | -10.526 | 10.526 | 9.3453 | 1.8977 | -0.51165 | 5.191% | -5.191%
21 | 9.62 | 1.9534 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0129 | -1.0531 | 0.98092 | -3.7062 | -10.526 | 10.526 | 9.1207 | 1.852 | -0.49925 | 5.19% | -5.19%
22 | 9.139 | 1.8558 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -0.98751 | 0.98328 | -3.5004 | -10.526 | 10.526 | 8.6649 | 1.7595 | -0.4741 | 5.188% | -5.188%
23 | 8.547 | 1.7355 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0143 | -0.90705 | 0.98616 | -3.2486 | -10.526 | 10.526 | 8.1038 | 1.6456 | -0.44318 | 5.185% | -5.185%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.83931 | 0.98855 | -3.0373 | -10.526 | 10.526 | 7.6299 | 1.5493 | -0.41709 | 5.183% | -5.183%
1 | 7.716 | 1.5668 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.79457 | 0.99013 | -2.898 | -10.526 | 10.526 | 7.3162 | 1.4856 | -0.39983 | 5.182% | -5.182%
2 | 7.517 | 1.5264 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.76772 | 0.99107 | -2.8145 | -10.526 | 10.526 | 7.1275 | 1.4473 | -0.38946 | 5.181% | -5.181%
3 | 7.407 | 1.5041 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.75289 | 0.99158 | -2.7684 | -10.526 | 10.526 | 7.0233 | 1.4261 | -0.38373 | 5.181% | -5.181%
4 | 7.398 | 1.5022 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.75168 | 0.99163 | -2.7647 | -10.526 | 10.526 | 7.0147 | 1.4244 | -0.38326 | 5.181% | -5.181%
5 | 7.563 | 1.5357 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0429 | -1.0542 | 1.0176 | -3.114 | 1.0156 | -0.77392 | 0.99085 | -2.8338 | -10.526 | 10.526 | 7.1711 | 1.4562 | -0.39186 | 5.181% | -5.181%
6 | 7.986 | 1.6216 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.83106 | 0.98884 | -3.0116 | -10.526 | 10.526 | 7.5721 | 1.5376 | -0.41391 | 5.183% | -5.183%
7 | 8.626 | 1.7516 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0416 | -1.2023 | 1.0124 | -3.5666 | 1.0142 | -0.91777 | 0.98578 | -3.2821 | -10.526 | 10.526 | 8.1787 | 1.6608 | -0.4473 | 5.185% | -5.185%
8 | 9.059 | 1.8395 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.2629 | 1.0102 | -3.7525 | 1.0137 | -0.97662 | 0.98367 | -3.4662 | -10.526 | 10.526 | 8.5891 | 1.7441 | -0.46992 | 5.187% | -5.187%
9 | 9.181 | 1.8643 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.28 | 1.0096 | -3.805 | 1.0135 | -0.99323 | 0.98308 | -3.5183 | -10.526 | 10.526 | 8.7047 | 1.7676 | -0.47629 | 5.188% | -5.188%
10 | 9.23 | 1.8742 | 0.98 | Z | cloudy | 10.526 | 10.5155 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0135 | -1.0002 | 0.98287 | -3.5395 | -10.5155 | 10.5155 | 8.7516 | 1.7771 | -0.47837 | 5.183% | -5.183%
11 | 9.261 | 1.8805 | 0.98 | Z | cloudy | 10.526 | 10.4839 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0135 | -1.0053 | 0.9828 | -3.5536 | -10.4839 | 10.4839 | 8.7825 | 1.7834 | -0.47851 | 5.167% | -5.167%
12 | 9.292 | 1.8868 | 0.98 | Z | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0136 | -1.0104 | 0.98273 | -3.5678 | -10.4523 | 10.4523 | 8.8133 | 1.7896 | -0.47865 | 5.151% | -5.151%
13 | 9.322 | 1.8929 | 0.98 | Z | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0135 | -1.0145 | 0.98258 | -3.5806 | -10.4523 | 10.4523 | 8.8418 | 1.7954 | -0.48021 | 5.151% | -5.151%
14 | 9.338 | 1.8962 | 0.98 | Z | cloudy | 10.526 | 10.4734 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0135 | -1.0171 | 0.98254 | -3.5878 | -10.4734 | 10.4734 | 8.8576 | 1.7986 | -0.48037 | 5.144% | -5.144%
15 | 9.404 | 1.9096 | 0.98 | Z | cloudy | 10.526 | 10.5049 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0134 | -1.0252 | 0.98213 | -3.6152 | -10.5049 | 10.5049 | 8.9187 | 1.811 | -0.48527 | 5.16% | -5.16%
16 | 9.594 | 1.9481 | 0.98 | Z | cloudy | 10.526 | 10.5155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.013 | -1.0498 | 0.98108 | -3.6953 | -10.5155 | 10.5155 | 9.0966 | 1.8471 | -0.49738 | 5.184% | -5.184%
17 | 9.883 | 2.0068 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1088 | 1.0126 | -1.089 | 0.97962 | -3.8192 | -10.526 | 10.526 | 9.37 | 1.9027 | -0.51301 | 5.191% | -5.191%
18 | 10 | 2.0306 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0124 | -1.105 | 0.97903 | -3.8696 | -10.526 | 10.526 | 9.4809 | 1.9252 | -0.51914 | 5.191% | -5.191%
19 | 9.966 | 2.0237 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0125 | -1.1004 | 0.9792 | -3.8549 | -10.526 | 10.526 | 9.4486 | 1.9186 | -0.51736 | 5.191% | -5.191%
20 | 9.857 | 2.0015 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.0062 | -4.0975 | 1.0126 | -1.0855 | 0.97975 | -3.808 | -10.526 | 10.526 | 9.3453 | 1.8977 | -0.51165 | 5.191% | -5.191%
21 | 9.62 | 1.9534 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0129 | -1.0531 | 0.98092 | -3.7062 | -10.526 | 10.526 | 9.1207 | 1.852 | -0.49925 | 5.19% | -5.19%
22 | 9.139 | 1.8558 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -0.98751 | 0.98328 | -3.5004 | -10.526 | 10.526 | 8.6649 | 1.7595 | -0.4741 | 5.188% | -5.188%
23 | 8.547 | 1.7355 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0143 | -0.90705 | 0.98616 | -3.2486 | -10.526 | 10.526 | 8.1038 | 1.6456 | -0.44318 | 5.185% | -5.185%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.83931 | 0.98855 | -3.0373 | -10.526 | 10.526 | 7.6299 | 1.5493 | -0.41709 | 5.183% | -5.183%
1 | 7.716 | 1.5668 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.002 | -1.6121 | 0.98958 | -2.6766 | -5.263 | 5.263 | 7.3081 | 1.484 | -0.40787 | 5.286% | -5.286%
2 | 7.517 | 1.5264 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.5586 | 0.99052 | -2.5941 | -5.263 | 5.263 | 7.1198 | 1.4457 | -0.39724 | 5.285% | -5.285%
3 | 7.407 | 1.5041 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5291 | 0.99104 | -2.5485 | -5.263 | 5.263 | 7.0156 | 1.4246 | -0.39136 | 5.284% | -5.284%
4 | 7.398 | 1.5022 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.003 | -1.5267 | 0.99109 | -2.5448 | -5.263 | 5.263 | 7.0071 | 1.4229 | -0.39088 | 5.284% | -5.284%
5 | 7.563 | 1.5357 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0025 | -1.571 | 0.99031 | -2.6131 | -5.263 | 5.263 | 7.1633 | 1.4546 | -0.3997 | 5.285% | -5.285%
6 | 7.986 | 1.6216 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0012 | -1.6848 | 0.9883 | -2.7888 | -5.263 | 5.263 | 7.5637 | 1.5359 | -0.42231 | 5.288% | -5.288%
7 | 8.626 | 1.7516 | 0.98 | Z | very sunny | 5.263 | 5.2525 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.9994 | -1.8605 | 0.98537 | -3.059 | -5.2525 | 5.2525 | 8.172 | 1.6594 | -0.45401 | 5.263% | -5.263%
8 | 9.059 | 1.8395 | 0.98 | Z | very sunny | 5.263 | 5.1156 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.99877 | -1.9917 | 0.98399 | -3.2547 | -5.1156 | 5.1156 | 8.5946 | 1.7452 | -0.46444 | 5.127% | -5.127%
9 | 9.181 | 1.8643 | 0.98 | Z | very sunny | 5.263 | 4.7051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 1.0006 | -2.066 | 0.98556 | -3.3473 | -4.7051 | 4.7051 | 8.7487 | 1.7765 | -0.43232 | 4.709% | -4.709%
10 | 9.23 | 1.8742 | 0.98 | Z | very sunny | 5.263 | 4.142 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 1.0034 | -2.1352 | 0.98825 | -3.4238 | -4.142 | 4.142 | 8.8477 | 1.7966 | -0.38228 | 4.142% | -4.142%
11 | 9.261 | 1.8805 | 0.98 | Z | very sunny | 5.263 | 3.5736 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 1.0062 | -2.1988 | 0.99099 | -3.4921 | -3.5736 | 3.5736 | 8.9295 | 1.8132 | -0.33154 | 3.58% | -3.58%
12 | 9.292 | 1.8868 | 0.98 | Z | very sunny | 5.263 | 3.2578 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 1.0078 | -2.2387 | 0.99248 | -3.5366 | -3.2578 | 3.2578 | 8.9892 | 1.8253 | -0.30283 | 3.259% | -3.259%
13 | 9.322 | 1.8929 | 0.98 | Z | very sunny | 5.263 | 3.3525 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 1.0073 | -2.2393 | 0.99193 | -3.5418 | -3.3525 | 3.3525 | 9.011 | 1.8298 | -0.31104 | 3.337% | -3.337%
14 | 9.338 | 1.8962 | 0.98 | Z | very sunny | 5.263 | 3.5052 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 1.0065 | -2.2286 | 0.99106 | -3.5335 | -3.5052 | 3.5052 | 9.012 | 1.83 | -0.32599 | 3.491% | -3.491%
15 | 9.404 | 1.9096 | 0.98 | Z | very sunny | 5.263 | 3.942 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 1.0039 | -2.2032 | 0.98845 | -3.518 | -3.942 | 3.942 | 9.0339 | 1.8344 | -0.3701 | 3.936% | -3.936%
16 | 9.594 | 1.9481 | 0.98 | Z | very sunny | 5.263 | 4.4578 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 1.0006 | -2.2038 | 0.98482 | -3.5473 | -4.4578 | 4.4578 | 9.1661 | 1.8613 | -0.42786 | 4.46% | -4.46%
17 | 9.883 | 2.0068 | 0.98 | Z | very sunny | 5.263 | 4.9209 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1088 | 0.99709 | -2.2347 | 0.98086 | -3.6218 | -4.9209 | 4.9209 | 9.3937 | 1.9075 | -0.48931 | 4.951% | -4.951%
18 | 10 | 2.0306 | 0.98 | Z | very sunny | 5.263 | 5.1893 | 4 | 1.0224 | -2.7547 | 1.0055 | -4.1596 | 0.99526 | -2.2392 | 0.97884 | -3.6441 | -5.1893 | 5.1893 | 9.4771 | 1.9244 | -0.52287 | 5.229% | -5.229%
19 | 9.966 | 2.0237 | 0.98 | Z | very sunny | 5.263 | 5.2577 | 4 | 1.0225 | -2.7451 | 1.0057 | -4.1448 | 0.995 | -2.2228 | 0.97865 | -3.6226 | -5.2577 | 5.2577 | 9.4379 | 1.9164 | -0.52809 | 5.299% | -5.299%
20 | 9.857 | 2.0015 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0975 | 0.99533 | -2.1925 | 0.97916 | -3.5757 | -5.263 | 5.263 | 9.3342 | 1.8954 | -0.52276 | 5.303% | -5.303%
21 | 9.62 | 1.9534 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99609 | -2.1278 | 0.98034 | -3.4751 | -5.263 | 5.263 | 9.11 | 1.8499 | -0.51 | 5.301% | -5.301%
22 | 9.139 | 1.8558 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99762 | -1.9968 | 0.98271 | -3.2718 | -5.263 | 5.263 | 8.6549 | 1.7574 | -0.48414 | 5.297% | -5.297%
23 | 8.547 | 1.7355 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5328 | 0.99949 | -1.8362 | 0.9856 | -3.023 | -5.263 | 5.263 | 8.0946 | 1.6437 | -0.45237 | 5.293% | -5.293%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 1.001 | -1.7012 | 0.988 | -2.8142 | -5.263 | 5.263 | 7.6214 | 1.5476 | -0.42558 | 5.289% | -5.289%
1 | 7.716 | 1.5668 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.002 | -1.6121 | 0.98958 | -2.6766 | -5.263 | 5.263 | 7.3081 | 1.484 | -0.40788 | 5.286% | -5.286%
2 | 7.517 | 1.5264 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.5586 | 0.99052 | -2.5941 | -5.263 | 5.263 | 7.1198 | 1.4457 | -0.39724 | 5.285% | -5.285%
3 | 7.407 | 1.5041 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5291 | 0.99104 | -2.5485 | -5.263 | 5.263 | 7.0156 | 1.4246 | -0.39136 | 5.284% | -5.284%
4 | 7.398 | 1.5022 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.003 | -1.5267 | 0.99109 | -2.5448 | -5.263 | 5.263 | 7.0071 | 1.4229 | -0.39088 | 5.284% | -5.284%
5 | 7.563 | 1.5357 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0025 | -1.571 | 0.99031 | -2.6131 | -5.263 | 5.263 | 7.1633 | 1.4546 | -0.3997 | 5.285% | -5.285%
6 | 7.986 | 1.6216 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0012 | -1.6848 | 0.9883 | -2.7888 | -5.263 | 5.263 | 7.5637 | 1.5359 | -0.42231 | 5.288% | -5.288%
7 | 8.626 | 1.7516 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99924 | -1.8576 | 0.98522 | -3.0561 | -5.263 | 5.263 | 8.1694 | 1.6589 | -0.4566 | 5.293% | -5.293%
8 | 9.059 | 1.8395 | 0.98 | Z | moderate sun | 5.263 | 5.2577 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.99791 | -1.9756 | 0.98313 | -3.2386 | -5.2577 | 5.2577 | 8.5797 | 1.7422 | -0.47935 | 5.291% | -5.291%
9 | 9.181 | 1.8643 | 0.98 | Z | moderate sun | 5.263 | 5.2051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99781 | -2.0141 | 0.98282 | -3.2954 | -5.2051 | 5.2051 | 8.7001 | 1.7666 | -0.48092 | 5.238% | -5.238%
10 | 9.23 | 1.8742 | 0.98 | Z | moderate sun | 5.263 | 5.0946 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99834 | -2.0403 | 0.98326 | -3.3289 | -5.0946 | 5.0946 | 8.7587 | 1.7785 | -0.47134 | 5.107% | -5.107%
11 | 9.261 | 1.8805 | 0.98 | Z | moderate sun | 5.263 | 4.9788 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99887 | -2.0604 | 0.98372 | -3.3537 | -4.9788 | 4.9788 | 8.799 | 1.7867 | -0.462 | 4.989% | -4.989%
12 | 9.292 | 1.8868 | 0.98 | Z | moderate sun | 5.263 | 4.9156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99911 | -2.0752 | 0.9839 | -3.3731 | -4.9156 | 4.9156 | 8.8344 | 1.7939 | -0.45757 | 4.924% | -4.924%
13 | 9.322 | 1.8929 | 0.98 | Z | moderate sun | 5.263 | 4.9841 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99865 | -2.0765 | 0.98339 | -3.379 | -4.9841 | 4.9841 | 8.8564 | 1.7984 | -0.46558 | 4.994% | -4.994%
14 | 9.338 | 1.8962 | 0.98 | Z | moderate sun | 5.263 | 5.0156 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99842 | -2.0777 | 0.98315 | -3.3825 | -5.0156 | 5.0156 | 8.8686 | 1.8008 | -0.46941 | 5.027% | -5.027%
15 | 9.404 | 1.9096 | 0.98 | Z | moderate sun | 5.263 | 5.1472 | 4 | 1.0243 | -2.5865 | 1.0085 | -3.9012 | 0.99751 | -2.0824 | 0.98212 | -3.3972 | -5.1472 | 5.1472 | 8.9186 | 1.811 | -0.48542 | 5.162% | -5.162%
16 | 9.594 | 1.9481 | 0.98 | Z | moderate sun | 5.263 | 5.2367 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99642 | -2.1252 | 0.98071 | -3.4686 | -5.2367 | 5.2367 | 9.0898 | 1.8458 | -0.50415 | 5.255% | -5.255%
17 | 9.883 | 2.0068 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1088 | 0.99524 | -2.1996 | 0.97903 | -3.5868 | -5.263 | 5.263 | 9.3588 | 1.9004 | -0.52416 | 5.304% | -5.304%
18 | 10 | 2.0306 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0224 | -2.7547 | 1.0055 | -4.1596 | 0.99486 | -2.2316 | 0.97845 | -3.6365 | -5.263 | 5.263 | 9.4695 | 1.9229 | -0.53047 | 5.305% | -5.305%
19 | 9.966 | 2.0237 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0225 | -2.7451 | 1.0057 | -4.1448 | 0.99498 | -2.2223 | 0.97862 | -3.6221 | -5.263 | 5.263 | 9.4374 | 1.9163 | -0.52863 | 5.304% | -5.304%
20 | 9.857 | 2.0015 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0975 | 0.99533 | -2.1925 | 0.97916 | -3.5757 | -5.263 | 5.263 | 9.3342 | 1.8954 | -0.52276 | 5.303% | -5.303%
21 | 9.62 | 1.9534 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99609 | -2.1278 | 0.98034 | -3.4751 | -5.263 | 5.263 | 9.11 | 1.8499 | -0.51 | 5.301% | -5.301%
22 | 9.139 | 1.8558 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99762 | -1.9968 | 0.98271 | -3.2718 | -5.263 | 5.263 | 8.6549 | 1.7574 | -0.48414 | 5.297% | -5.297%
23 | 8.547 | 1.7355 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5328 | 0.99949 | -1.8362 | 0.9856 | -3.023 | -5.263 | 5.263 | 8.0946 | 1.6437 | -0.45237 | 5.293% | -5.293%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 1.001 | -1.7012 | 0.988 | -2.8142 | -5.263 | 5.263 | 7.6214 | 1.5476 | -0.42558 | 5.289% | -5.289%
1 | 7.716 | 1.5668 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.002 | -1.6121 | 0.98958 | -2.6766 | -5.263 | 5.263 | 7.3081 | 1.484 | -0.40788 | 5.286% | -5.286%
2 | 7.517 | 1.5264 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.5586 | 0.99052 | -2.5941 | -5.263 | 5.263 | 7.1198 | 1.4457 | -0.39724 | 5.285% | -5.285%
3 | 7.407 | 1.5041 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5291 | 0.99104 | -2.5485 | -5.263 | 5.263 | 7.0156 | 1.4246 | -0.39136 | 5.284% | -5.284%
4 | 7.398 | 1.5022 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.003 | -1.5267 | 0.99109 | -2.5448 | -5.263 | 5.263 | 7.0071 | 1.4229 | -0.39088 | 5.284% | -5.284%
5 | 7.563 | 1.5357 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0025 | -1.571 | 0.99031 | -2.6131 | -5.263 | 5.263 | 7.1633 | 1.4546 | -0.3997 | 5.285% | -5.285%
6 | 7.986 | 1.6216 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0012 | -1.6848 | 0.9883 | -2.7888 | -5.263 | 5.263 | 7.5637 | 1.5359 | -0.42231 | 5.288% | -5.288%
7 | 8.626 | 1.7516 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99924 | -1.8576 | 0.98522 | -3.0561 | -5.263 | 5.263 | 8.1694 | 1.6589 | -0.4566 | 5.293% | -5.293%
8 | 9.059 | 1.8395 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.99788 | -1.975 | 0.98311 | -3.2381 | -5.263 | 5.263 | 8.5792 | 1.7421 | -0.47984 | 5.297% | -5.297%
9 | 9.181 | 1.8643 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99749 | -2.0082 | 0.98251 | -3.2895 | -5.263 | 5.263 | 8.6946 | 1.7655 | -0.48639 | 5.298% | -5.298%
10 | 9.23 | 1.8742 | 0.98 | Z | cloudy | 5.263 | 5.2577 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99736 | -2.0221 | 0.9823 | -3.3107 | -5.2577 | 5.2577 | 8.7415 | 1.775 | -0.48852 | 5.293% | -5.293%
11 | 9.261 | 1.8805 | 0.98 | Z | cloudy | 5.263 | 5.2419 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99735 | -2.0321 | 0.98223 | -3.3254 | -5.2419 | 5.2419 | 8.7723 | 1.7813 | -0.48869 | 5.277% | -5.277%
12 | 9.292 | 1.8868 | 0.98 | Z | cloudy | 5.263 | 5.2262 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99734 | -2.0421 | 0.98216 | -3.3401 | -5.2262 | 5.2262 | 8.8032 | 1.7876 | -0.48883 | 5.261% | -5.261%
13 | 9.322 | 1.8929 | 0.98 | Z | cloudy | 5.263 | 5.2262 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99724 | -2.0503 | 0.98201 | -3.3527 | -5.2262 | 5.2262 | 8.8316 | 1.7933 | -0.49044 | 5.261% | -5.261%
14 | 9.338 | 1.8962 | 0.98 | Z | cloudy | 5.263 | 5.2367 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99724 | -2.0554 | 0.98198 | -3.3602 | -5.2367 | 5.2367 | 8.8475 | 1.7966 | -0.49051 | 5.253% | -5.253%
15 | 9.404 | 1.9096 | 0.98 | Z | cloudy | 5.263 | 5.2525 | 4 | 1.0243 | -2.5865 | 1.0085 | -3.9012 | 0.99694 | -2.0718 | 0.98157 | -3.3865 | -5.2525 | 5.2525 | 8.9085 | 1.8089 | -0.49554 | 5.269% | -5.269%
16 | 9.594 | 1.9481 | 0.98 | Z | cloudy | 5.263 | 5.2577 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.9962 | -2.1212 | 0.9805 | -3.4646 | -5.2577 | 5.2577 | 9.0859 | 1.845 | -0.50808 | 5.296% | -5.296%
17 | 9.883 | 2.0068 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1088 | 0.99524 | -2.1996 | 0.97903 | -3.5868 | -5.263 | 5.263 | 9.3588 | 1.9004 | -0.52416 | 5.304% | -5.304%
18 | 10 | 2.0306 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0224 | -2.7547 | 1.0055 | -4.1596 | 0.99486 | -2.2316 | 0.97845 | -3.6365 | -5.263 | 5.263 | 9.4695 | 1.9229 | -0.53047 | 5.305% | -5.305%
19 | 9.966 | 2.0237 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0225 | -2.7451 | 1.0057 | -4.1448 | 0.99498 | -2.2223 | 0.97862 | -3.6221 | -5.263 | 5.263 | 9.4374 | 1.9163 | -0.52863 | 5.304% | -5.304%
20 | 9.857 | 2.0015 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0975 | 0.99533 | -2.1925 | 0.97916 | -3.5757 | -5.263 | 5.263 | 9.3342 | 1.8954 | -0.52276 | 5.303% | -5.303%
21 | 9.62 | 1.9534 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99609 | -2.1278 | 0.98034 | -3.4751 | -5.263 | 5.263 | 9.11 | 1.8499 | -0.51 | 5.301% | -5.301%
22 | 9.139 | 1.8558 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99762 | -1.9968 | 0.98271 | -3.2718 | -5.263 | 5.263 | 8.6549 | 1.7574 | -0.48414 | 5.297% | -5.297%
23 | 8.547 | 1.7355 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5328 | 0.99949 | -1.8362 | 0.9856 | -3.023 | -5.263 | 5.263 | 8.0946 | 1.6437 | -0.45237 | 5.293% | -5.293%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 1.001 | -1.7012 | 0.988 | -2.8142 | -5.263 | 5.263 | 7.6214 | 1.5476 | -0.42558 | 5.289% | -5.289%
1 | 7.716 | 1.5668 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.3865 | 0.97732 | -2.451 | -7.5312 | 10.526 | 7.1281 | 1.4474 | -0.58787 | 7.619% | -7.619%
2 | 7.517 | 1.5264 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0302 | -2.0592 | 1.0178 | -3.0946 | 0.99025 | -1.3341 | 0.97827 | -2.3695 | -7.5286 | 10.526 | 6.9446 | 1.4102 | -0.57237 | 7.614% | -7.614%
3 | 7.407 | 1.5041 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0287 | 1.0183 | -3.0481 | 0.99058 | -1.3051 | 0.97879 | -2.3245 | -7.5275 | 10.526 | 6.8432 | 1.3896 | -0.56382 | 7.612% | -7.612%
4 | 7.398 | 1.5022 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0262 | 1.0184 | -3.0443 | 0.99061 | -1.3027 | 0.97883 | -2.3208 | -7.5274 | 10.526 | 6.8349 | 1.3879 | -0.56312 | 7.612% | -7.612%
5 | 7.563 | 1.5357 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.1141 | 0.9901 | -1.3462 | 0.97805 | -2.3883 | -7.5291 | 10.526 | 6.987 | 1.4188 | -0.57595 | 7.615% | -7.615%
6 | 7.986 | 1.6216 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.9888 | -1.4578 | 0.97603 | -2.5618 | -7.5336 | 10.526 | 7.3771 | 1.498 | -0.60892 | 7.625% | -7.625%
7 | 8.626 | 1.7516 | 0.98 | Z | very sunny | 10.526 | 10.5049 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5667 | 0.98679 | -1.6273 | 0.97294 | -2.8258 | -7.5404 | 10.5049 | 7.967 | 1.6178 | -0.65899 | 7.64% | -7.64%
8 | 9.059 | 1.8395 | 0.98 | Z | very sunny | 10.526 | 10.2313 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.7425 | 0.97082 | -3.0055 | -7.5451 | 10.2313 | 8.366 | 1.6988 | -0.69298 | 7.65% | -7.65%
9 | 9.181 | 1.8643 | 0.98 | Z | very sunny | 10.526 | 9.4102 | 4 | 1.025 | -2.5238 | 1.0096 | -3.8051 | 0.98502 | -1.775 | 0.97022 | -3.0563 | -7.5464 | 9.4102 | 8.4784 | 1.7216 | -0.70257 | 7.652% | -7.652%
10 | 9.23 | 1.8742 | 0.98 | Z | very sunny | 10.526 | 8.284 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8262 | 0.99486 | -1.9751 | 0.97983 | -3.2638 | -5.7206 | 8.284 | 8.6975 | 1.7661 | -0.53246 | 5.769% | -5.769%
11 | 9.261 | 1.8805 | 0.98 | Z | very sunny | 10.526 | 7.1472 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99476 | -1.9835 | 0.97967 | -3.2768 | -5.7213 | 7.1472 | 8.7267 | 1.772 | -0.5343 | 5.769% | -5.769%
12 | 9.292 | 1.8868 | 0.98 | Z | very sunny | 10.526 | 6.5156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99466 | -1.9918 | 0.97952 | -3.2898 | -5.7216 | 6.5156 | 8.7559 | 1.778 | -0.53614 | 5.77% | -5.77%
13 | 9.322 | 1.8929 | 0.98 | Z | very sunny | 10.526 | 6.7051 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2 | 0.97937 | -3.3024 | -5.7219 | 6.7051 | 8.7841 | 1.7837 | -0.53792 | 5.77% | -5.77%
14 | 9.338 | 1.8962 | 0.98 | Z | very sunny | 10.526 | 7.0103 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0043 | 0.97929 | -3.3092 | -5.722 | 7.0103 | 8.7991 | 1.7867 | -0.53887 | 5.771% | -5.771%
15 | 9.404 | 1.9096 | 0.98 | Z | very sunny | 10.526 | 7.884 | 4 | 1.0243 | -2.5865 | 1.0085 | -3.9012 | 0.99429 | -2.0221 | 0.97896 | -3.3369 | -5.7225 | 7.884 | 8.8612 | 1.7993 | -0.54279 | 5.772% | -5.772%
16 | 9.594 | 1.9481 | 0.98 | Z | very sunny | 10.526 | 8.9155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.0736 | 0.97801 | -3.417 | -5.7242 | 8.9155 | 9.0399 | 1.8356 | -0.55408 | 5.775% | -5.775%
17 | 9.883 | 2.0068 | 0.98 | Z | very sunny | 10.526 | 9.8418 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1088 | 0.99273 | -2.152 | 0.97657 | -3.5392 | -5.7267 | 9.8418 | 9.3117 | 1.8908 | -0.57129 | 5.781% | -5.781%
18 | 10 | 2.0306 | 0.98 | Z | very sunny | 10.526 | 10.3786 | 4 | 1.0224 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.1838 | 0.97598 | -3.5888 | -5.7277 | 10.3786 | 9.4217 | 1.9132 | -0.57827 | 5.783% | -5.783%
19 | 9.966 | 2.0237 | 0.98 | Z | very sunny | 10.526 | 10.5155 | 4 | 1.0225 | -2.7451 | 1.0057 | -4.1448 | 0.99246 | -2.1746 | 0.97615 | -3.5744 | -5.7274 | 10.5155 | 9.3898 | 1.9067 | -0.57624 | 5.782% | -5.782%
20 | 9.857 | 2.0015 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0975 | 0.99282 | -2.145 | 0.9767 | -3.5282 | -5.7265 | 10.526 | 9.2873 | 1.8859 | -0.56975 | 5.78% | -5.78%
21 | 9.62 | 1.9534 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99359 | -2.0807 | 0.97788 | -3.428 | -5.7244 | 10.526 | 9.0644 | 1.8406 | -0.55563 | 5.776% | -5.776%
22 | 9.139 | 1.8558 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.7638 | 0.97042 | -3.0388 | -7.5463 | 10.526 | 8.4397 | 1.7138 | -0.69927 | 7.651% | -7.651%
23 | 8.547 | 1.7355 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5328 | 0.98704 | -1.6064 | 0.97332 | -2.7932 | -7.5394 | 10.526 | 7.8942 | 1.603 | -0.6528 | 7.638% | -7.638%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.98861 | -1.4739 | 0.97574 | -2.5869 | -7.5341 | 10.526 | 7.4333 | 1.5094 | -0.61369 | 7.626% | -7.626%
1 | 7.716 | 1.5668 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1789 | 0.98963 | -1.3865 | 0.97732 | -2.451 | -7.5307 | 10.526 | 7.1281 | 1.4474 | -0.58787 | 7.619% | -7.619%
2 | 7.517 | 1.5264 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0302 | -2.0592 | 1.0178 | -3.0946 | 0.99025 | -1.3341 | 0.97827 | -2.3695 | -7.5286 | 10.526 | 6.9446 | 1.4102 | -0.57237 | 7.614% | -7.614%
3 | 7.407 | 1.5041 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0287 | 1.0183 | -3.0481 | 0.99058 | -1.3051 | 0.97879 | -2.3245 | -7.5275 | 10.526 | 6.8432 | 1.3896 | -0.56382 | 7.612% | -7.612%
4 | 7.398 | 1.5022 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0262 | 1.0184 | -3.0443 | 0.99061 | -1.3027 | 0.97883 | -2.3208 | -7.5274 | 10.526 | 6.8349 | 1.3879 | -0.56312 | 7.612% | -7.612%
5 | 7.563 | 1.5357 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.1141 | 0.9901 | -1.3462 | 0.97805 | -2.3883 | -7.5291 | 10.526 | 6.987 | 1.4188 | -0.57595 | 7.615% | -7.615%
6 | 7.986 | 1.6216 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.9888 | -1.4578 | 0.97603 | -2.5618 | -7.5336 | 10.526 | 7.3771 | 1.498 | -0.60892 | 7.625% | -7.625%
7 | 8.626 | 1.7516 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5667 | 0.98679 | -1.6273 | 0.97294 | -2.8258 | -7.5404 | 10.526 | 7.967 | 1.6178 | -0.65899 | 7.64% | -7.64%
8 | 9.059 | 1.8395 | 0.98 | Z | moderate sun | 10.526 | 10.5155 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.7425 | 0.97082 | -3.0055 | -7.5451 | 10.5155 | 8.366 | 1.6988 | -0.69298 | 7.65% | -7.65%
9 | 9.181 | 1.8643 | 0.98 | Z | moderate sun | 10.526 | 10.4102 | 4 | 1.025 | -2.5238 | 1.0096 | -3.8051 | 0.98502 | -1.775 | 0.97022 | -3.0563 | -7.5464 | 10.4102 | 8.4784 | 1.7216 | -0.70257 | 7.652% | -7.652%
10 | 9.23 | 1.8742 | 0.98 | Z | moderate sun | 10.526 | 10.1892 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8262 | 0.99486 | -1.9751 | 0.97983 | -3.2638 | -5.7206 | 10.1892 | 8.6975 | 1.7661 | -0.53246 | 5.769% | -5.769%
11 | 9.261 | 1.8805 | 0.98 | Z | moderate sun | 10.526 | 9.9576 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99476 | -1.9835 | 0.97967 | -3.2768 | -5.7213 | 9.9576 | 8.7267 | 1.772 | -0.5343 | 5.769% | -5.769%
12 | 9.292 | 1.8868 | 0.98 | Z | moderate sun | 10.526 | 9.8313 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99466 | -1.9918 | 0.97952 | -3.2898 | -5.7216 | 9.8313 | 8.7559 | 1.778 | -0.53614 | 5.77% | -5.77%
13 | 9.322 | 1.8929 | 0.98 | Z | moderate sun | 10.526 | 9.9681 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2 | 0.97937 | -3.3024 | -5.7219 | 9.9681 | 8.7841 | 1.7837 | -0.53792 | 5.77% | -5.77%
14 | 9.338 | 1.8962 | 0.98 | Z | moderate sun | 10.526 | 10.0313 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0043 | 0.97929 | -3.3092 | -5.722 | 10.0313 | 8.7991 | 1.7867 | -0.53887 | 5.771% | -5.771%
15 | 9.404 | 1.9096 | 0.98 | Z | moderate sun | 10.526 | 10.2944 | 4 | 1.0243 | -2.5865 | 1.0085 | -3.9012 | 0.99429 | -2.0221 | 0.97896 | -3.3369 | -5.7225 | 10.2944 | 8.8612 | 1.7993 | -0.54279 | 5.772% | -5.772%
16 | 9.594 | 1.9481 | 0.98 | Z | moderate sun | 10.526 | 10.4734 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.0736 | 0.97801 | -3.417 | -5.7242 | 10.4734 | 9.0399 | 1.8356 | -0.55408 | 5.775% | -5.775%
17 | 9.883 | 2.0068 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1088 | 0.99273 | -2.152 | 0.97657 | -3.5392 | -5.7267 | 10.526 | 9.3117 | 1.8908 | -0.57129 | 5.781% | -5.781%
18 | 10 | 2.0306 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0224 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.1838 | 0.97598 | -3.5888 | -5.7277 | 10.526 | 9.4217 | 1.9132 | -0.57827 | 5.783% | -5.783%
19 | 9.966 | 2.0237 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0225 | -2.7451 | 1.0057 | -4.1448 | 0.99246 | -2.1746 | 0.97615 | -3.5744 | -5.7274 | 10.526 | 9.3898 | 1.9067 | -0.57624 | 5.782% | -5.782%
20 | 9.857 | 2.0015 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0975 | 0.99282 | -2.145 | 0.9767 | -3.5282 | -5.7265 | 10.526 | 9.2873 | 1.8859 | -0.56975 | 5.78% | -5.78%
21 | 9.62 | 1.9534 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99359 | -2.0807 | 0.97788 | -3.428 | -5.7244 | 10.526 | 9.0644 | 1.8406 | -0.55563 | 5.776% | -5.776%
22 | 9.139 | 1.8558 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.7638 | 0.97042 | -3.0388 | -7.5463 | 10.526 | 8.4397 | 1.7138 | -0.69927 | 7.651% | -7.651%
23 | 8.547 | 1.7355 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5328 | 0.98704 | -1.6064 | 0.97332 | -2.7932 | -7.5394 | 10.526 | 7.8942 | 1.603 | -0.6528 | 7.638% | -7.638%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.98861 | -1.4739 | 0.97574 | -2.5869 | -7.5341 | 10.526 | 7.4333 | 1.5094 | -0.61369 | 7.626% | -7.626%
1 | 7.716 | 1.5668 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1789 | 0.98963 | -1.3865 | 0.97732 | -2.451 | -7.5307 | 10.526 | 7.1281 | 1.4474 | -0.58787 | 7.619% | -7.619%
2 | 7.517 | 1.5264 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0302 | -2.0592 | 1.0178 | -3.0946 | 0.99025 | -1.3341 | 0.97827 | -2.3695 | -7.5286 | 10.526 | 6.9446 | 1.4102 | -0.57237 | 7.614% | -7.614%
3 | 7.407 | 1.5041 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0287 | 1.0183 | -3.0481 | 0.99058 | -1.3051 | 0.97879 | -2.3245 | -7.5275 | 10.526 | 6.8432 | 1.3896 | -0.56382 | 7.612% | -7.612%
4 | 7.398 | 1.5022 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0262 | 1.0184 | -3.0443 | 0.99061 | -1.3027 | 0.97883 | -2.3208 | -7.5274 | 10.526 | 6.8349 | 1.3879 | -0.56312 | 7.612% | -7.612%
5 | 7.563 | 1.5357 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.1141 | 0.9901 | -1.3462 | 0.97805 | -2.3883 | -7.5291 | 10.526 | 6.987 | 1.4188 | -0.57595 | 7.615% | -7.615%
6 | 7.986 | 1.6216 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.9888 | -1.4578 | 0.97603 | -2.5618 | -7.5336 | 10.526 | 7.3771 | 1.498 | -0.60892 | 7.625% | -7.625%
7 | 8.626 | 1.7516 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5667 | 0.98679 | -1.6273 | 0.97294 | -2.8258 | -7.5404 | 10.526 | 7.967 | 1.6178 | -0.65899 | 7.64% | -7.64%
8 | 9.059 | 1.8395 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.7425 | 0.97082 | -3.0055 | -7.5451 | 10.526 | 8.366 | 1.6988 | -0.69298 | 7.65% | -7.65%
9 | 9.181 | 1.8643 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.5238 | 1.0096 | -3.8051 | 0.98502 | -1.775 | 0.97022 | -3.0563 | -7.5464 | 10.526 | 8.4784 | 1.7216 | -0.70257 | 7.652% | -7.652%
10 | 9.23 | 1.8742 | 0.98 | Z | cloudy | 10.526 | 10.5155 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8262 | 0.99486 | -1.9751 | 0.97983 | -3.2638 | -5.7206 | 10.5155 | 8.6975 | 1.7661 | -0.53246 | 5.769% | -5.769%
11 | 9.261 | 1.8805 | 0.98 | Z | cloudy | 10.526 | 10.4839 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99476 | -1.9835 | 0.97967 | -3.2768 | -5.7213 | 10.4839 | 8.7267 | 1.772 | -0.5343 | 5.769% | -5.769%
12 | 9.292 | 1.8868 | 0.98 | Z | cloudy | 10.526 | 10.4523 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99466 | -1.9918 | 0.97952 | -3.2898 | -5.7216 | 10.4523 | 8.7559 | 1.778 | -0.53614 | 5.77% | -5.77%
13 | 9.322 | 1.8929 | 0.98 | Z | cloudy | 10.526 | 10.4523 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2 | 0.97937 | -3.3024 | -5.7219 | 10.4523 | 8.7841 | 1.7837 | -0.53792 | 5.77% | -5.77%
14 | 9.338 | 1.8962 | 0.98 | Z | cloudy | 10.526 | 10.4734 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0043 | 0.97929 | -3.3092 | -5.722 | 10.4734 | 8.7991 | 1.7867 | -0.53887 | 5.771% | -5.771%
15 | 9.404 | 1.9096 | 0.98 | Z | cloudy | 10.526 | 10.5049 | 4 | 1.0243 | -2.5865 | 1.0085 | -3.9012 | 0.99429 | -2.0221 | 0.97896 | -3.3369 | -5.7225 | 10.5049 | 8.8612 | 1.7993 | -0.54279 | 5.772% | -5.772%
16 | 9.594 | 1.9481 | 0.98 | Z | cloudy | 10.526 | 10.5155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.0736 | 0.97801 | -3.417 | -5.7242 | 10.5155 | 9.0399 | 1.8356 | -0.55408 | 5.775% | -5.775%
17 | 9.883 | 2.0068 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1088 | 0.99273 | -2.152 | 0.97657 | -3.5392 | -5.7267 | 10.526 | 9.3117 | 1.8908 | -0.57129 | 5.781% | -5.781%
18 | 10 | 2.0306 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0224 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.1838 | 0.97598 | -3.5888 | -5.7277 | 10.526 | 9.4217 | 1.9132 | -0.57827 | 5.783% | -5.783%
19 | 9.966 | 2.0237 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0225 | -2.7451 | 1.0057 | -4.1448 | 0.99246 | -2.1746 | 0.97615 | -3.5744 | -5.7274 | 10.526 | 9.3898 | 1.9067 | -0.57624 | 5.782% | -5.782%
20 | 9.857 | 2.0015 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0975 | 0.99282 | -2.145 | 0.9767 | -3.5282 | -5.7265 | 10.526 | 9.2873 | 1.8859 | -0.56975 | 5.78% | -5.78%
21 | 9.62 | 1.9534 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99359 | -2.0807 | 0.97788 | -3.428 | -5.7244 | 10.526 | 9.0644 | 1.8406 | -0.55563 | 5.776% | -5.776%
22 | 9.139 | 1.8558 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.7638 | 0.97042 | -3.0388 | -7.5463 | 10.526 | 8.4397 | 1.7138 | -0.69927 | 7.651% | -7.651%
23 | 8.547 | 1.7355 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5328 | 0.98704 | -1.6064 | 0.97332 | -2.7932 | -7.5394 | 10.526 | 7.8942 | 1.603 | -0.6528 | 7.638% | -7.638%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.98861 | -1.4739 | 0.97574 | -2.5869 | -7.5341 | 10.526 | 7.4333 | 1.5094 | -0.61369 | 7.626% | -7.626%
1 | 7.716 | 1.5668 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97494 | -2.2632 | 0.97494 | -2.2632 | -5.263 | 5.263 | 7.0934 | 1.4404 | -0.62262 | 8.069% | -8.069%
2 | 7.517 | 1.5264 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97589 | -2.1835 | 0.97589 | -2.1835 | -5.263 | 5.263 | 6.9108 | 1.4033 | -0.60617 | 8.064% | -8.064%
3 | 7.407 | 1.5041 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97641 | -2.1395 | 0.97641 | -2.1395 | -5.263 | 5.263 | 6.8099 | 1.3828 | -0.59706 | 8.061% | -8.061%
4 | 7.398 | 1.5022 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97645 | -2.1359 | 0.97645 | -2.1359 | -5.263 | 5.263 | 6.8017 | 1.3811 | -0.59631 | 8.06% | -8.06%
5 | 7.563 | 1.5357 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97567 | -2.2019 | 0.97567 | -2.2019 | -5.263 | 5.263 | 6.953 | 1.4119 | -0.60997 | 8.065% | -8.065%
6 | 7.986 | 1.6216 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97364 | -2.3717 | 0.97364 | -2.3717 | -5.263 | 5.263 | 7.341 | 1.4907 | -0.64497 | 8.076% | -8.076%
7 | 8.626 | 1.7516 | 0.98 | Z | very sunny | 5.263 | 5.2525 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97065 | -2.6324 | 0.97065 | -2.6324 | -5.2525 | 5.2525 | 7.9296 | 1.6102 | -0.69639 | 8.073% | -8.073%
8 | 9.059 | 1.8395 | 0.98 | Z | very sunny | 5.263 | 5.1156 | 5 | 1.0102 | -3.7526 | 1.0102 | -3.7526 | 0.97 | -2.8412 | 0.97 | -2.8412 | -5.0782 | 5.1156 | 8.3519 | 1.6959 | -0.70712 | 7.806% | -7.806%
9 | 9.181 | 1.8643 | 0.98 | Z | very sunny | 5.263 | 4.7051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97249 | -2.9611 | 0.97249 | -2.9611 | -4.7051 | 4.7051 | 8.5182 | 1.7297 | -0.66281 | 7.219% | -7.219%
10 | 9.23 | 1.8742 | 0.98 | Z | very sunny | 5.263 | 4.142 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97691 | -3.0868 | 0.97691 | -3.0868 | -4.142 | 4.142 | 8.6458 | 1.7556 | -0.58418 | 6.329% | -6.329%
11 | 9.261 | 1.8805 | 0.98 | Z | very sunny | 5.263 | 3.5736 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.98145 | -3.2063 | 0.98145 | -3.2063 | -3.5736 | 3.5736 | 8.7585 | 1.7785 | -0.50252 | 5.426% | -5.426%
12 | 9.292 | 1.8868 | 0.98 | Z | very sunny | 5.263 | 3.2578 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.98391 | -3.2784 | 0.98391 | -3.2784 | -3.2578 | 3.2578 | 8.8345 | 1.7939 | -0.45749 | 4.924% | -4.924%
13 | 9.322 | 1.8929 | 0.98 | Z | very sunny | 5.263 | 3.3525 | 5 | 1.0089 | -3.8658 | 1.0089 | -3.8658 | 0.98297 | -3.2731 | 0.98297 | -3.2731 | -3.3525 | 3.3525 | 8.8488 | 1.7968 | -0.47317 | 5.076% | -5.076%
14 | 9.338 | 1.8962 | 0.98 | Z | very sunny | 5.263 | 3.5052 | 5 | 1.0088 | -3.8727 | 1.0088 | -3.8727 | 0.98163 | -3.251 | 0.98163 | -3.251 | -3.5052 | 3.5052 | 8.8412 | 1.7953 | -0.49677 | 5.32% | -5.32%
15 | 9.404 | 1.9096 | 0.98 | Z | very sunny | 5.263 | 3.942 | 5 | 1.0085 | -3.9012 | 1.0085 | -3.9012 | 0.97769 | -3.1962 | 0.97769 | -3.1962 | -3.942 | 3.942 | 8.8382 | 1.7947 | -0.56579 | 6.016% | -6.016%
16 | 9.594 | 1.9481 | 0.98 | Z | very sunny | 5.263 | 4.4578 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97249 | -3.1777 | 0.97249 | -3.1777 | -4.4578 | 4.4578 | 8.9381 | 1.815 | -0.65593 | 6.837% | -6.837%
17 | 9.883 | 2.0068 | 0.98 | Z | very sunny | 5.263 | 4.9209 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.2731 | 0.97 | -3.2731 | -4.5858 | 4.9209 | 9.1869 | 1.8655 | -0.69612 | 7.044% | -7.044%
18 | 10 | 2.0306 | 0.98 | Z | very sunny | 5.263 | 5.1893 | 5 | 1.0055 | -4.1597 | 1.0055 | -4.1597 | 0.97 | -3.3352 | 0.97 | -3.3352 | -4.5145 | 5.1893 | 9.3066 | 1.8898 | -0.69335 | 6.934% | -6.934%
19 | 9.966 | 2.0237 | 0.98 | Z | very sunny | 5.263 | 5.2577 | 5 | 1.0057 | -4.1449 | 1.0057 | -4.1449 | 0.97 | -3.3171 | 0.97 | -3.3171 | -4.5353 | 5.2577 | 9.2718 | 1.8827 | -0.69419 | 6.966% | -6.966%
20 | 9.857 | 2.0015 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.2594 | 0.97 | -3.2594 | -4.6015 | 5.263 | 9.1603 | 1.8601 | -0.6967 | 7.068% | -7.068%
21 | 9.62 | 1.9534 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.1343 | 0.97 | -3.1343 | -4.7447 | 5.263 | 8.9188 | 1.811 | -0.70124 | 7.289% | -7.289%
22 | 9.139 | 1.8558 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0098 | -3.787 | 1.0098 | -3.787 | 0.97 | -2.8828 | 0.97 | -2.8828 | -5.0311 | 5.263 | 8.4323 | 1.7123 | -0.70669 | 7.733% | -7.733%
23 | 8.547 | 1.7355 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97095 | -2.5983 | 0.97095 | -2.5983 | -5.263 | 5.263 | 7.8557 | 1.5952 | -0.69132 | 8.088% | -8.088%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97335 | -2.3963 | 0.97335 | -2.3963 | -5.263 | 5.263 | 7.397 | 1.502 | -0.65003 | 8.078% | -8.078%
1 | 7.716 | 1.5668 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97494 | -2.2632 | 0.97494 | -2.2632 | -5.263 | 5.263 | 7.0934 | 1.4404 | -0.62264 | 8.069% | -8.069%
2 | 7.517 | 1.5264 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97589 | -2.1835 | 0.97589 | -2.1835 | -5.263 | 5.263 | 6.9108 | 1.4033 | -0.60617 | 8.064% | -8.064%
3 | 7.407 | 1.5041 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97641 | -2.1395 | 0.97641 | -2.1395 | -5.263 | 5.263 | 6.8099 | 1.3828 | -0.59706 | 8.061% | -8.061%
4 | 7.398 | 1.5022 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97645 | -2.1359 | 0.97645 | -2.1359 | -5.263 | 5.263 | 6.8017 | 1.3811 | -0.59631 | 8.06% | -8.06%
5 | 7.563 | 1.5357 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97567 | -2.2019 | 0.97567 | -2.2019 | -5.263 | 5.263 | 6.953 | 1.4119 | -0.60997 | 8.065% | -8.065%
6 | 7.986 | 1.6216 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97364 | -2.3717 | 0.97364 | -2.3717 | -5.263 | 5.263 | 7.341 | 1.4907 | -0.64497 | 8.076% | -8.076%
7 | 8.626 | 1.7516 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97056 | -2.6304 | 0.97056 | -2.6304 | -5.263 | 5.263 | 7.9282 | 1.6099 | -0.69783 | 8.09% | -8.09%
8 | 9.059 | 1.8395 | 0.98 | Z | moderate sun | 5.263 | 5.2577 | 5 | 1.0102 | -3.7526 | 1.0102 | -3.7526 | 0.97 | -2.8412 | 0.97 | -2.8412 | -5.0782 | 5.2577 | 8.3519 | 1.6959 | -0.70712 | 7.806% | -7.806%
9 | 9.181 | 1.8643 | 0.98 | Z | moderate sun | 5.263 | 5.2051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -2.9046 | 0.97 | -2.9046 | -5.0063 | 5.2051 | 8.4746 | 1.7208 | -0.70642 | 7.694% | -7.694%
10 | 9.23 | 1.8742 | 0.98 | Z | moderate sun | 5.263 | 5.0946 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -2.9301 | 0.97 | -2.9301 | -4.9773 | 5.0946 | 8.524 | 1.7309 | -0.70605 | 7.65% | -7.65%
11 | 9.261 | 1.8805 | 0.98 | Z | moderate sun | 5.263 | 4.9788 | 5 | 1.0092 | -3.8396 | 1.0092 | -3.8396 | 0.97 | -2.9463 | 0.97 | -2.9463 | -4.9589 | 4.9788 | 8.5552 | 1.7372 | -0.70579 | 7.621% | -7.621%
12 | 9.292 | 1.8868 | 0.98 | Z | moderate sun | 5.263 | 4.9156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97021 | -2.9671 | 0.97021 | -2.9671 | -4.9156 | 4.9156 | 8.5901 | 1.7443 | -0.70186 | 7.553% | -7.553%
13 | 9.322 | 1.8929 | 0.98 | Z | moderate sun | 5.263 | 4.9841 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -2.9781 | 0.97 | -2.9781 | -4.9227 | 4.9841 | 8.6168 | 1.7497 | -0.70521 | 7.565% | -7.565%
14 | 9.338 | 1.8962 | 0.98 | Z | moderate sun | 5.263 | 5.0156 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -2.9865 | 0.97 | -2.9865 | -4.9132 | 5.0156 | 8.633 | 1.753 | -0.70505 | 7.55% | -7.55%
15 | 9.404 | 1.9096 | 0.98 | Z | moderate sun | 5.263 | 5.1472 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.021 | 0.97 | -3.021 | -4.8739 | 5.1472 | 8.6997 | 1.7665 | -0.70432 | 7.49% | -7.49%
16 | 9.594 | 1.9481 | 0.98 | Z | moderate sun | 5.263 | 5.2367 | 5 | 1.0075 | -3.9835 | 1.0075 | -3.9835 | 0.97 | -3.1206 | 0.97 | -3.1206 | -4.7603 | 5.2367 | 8.8923 | 1.8057 | -0.70167 | 7.314% | -7.314%
17 | 9.883 | 2.0068 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.2731 | 0.97 | -3.2731 | -4.5858 | 5.263 | 9.1869 | 1.8655 | -0.69613 | 7.044% | -7.044%
18 | 10 | 2.0306 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0055 | -4.1597 | 1.0055 | -4.1597 | 0.97 | -3.3352 | 0.97 | -3.3352 | -4.5145 | 5.263 | 9.3066 | 1.8898 | -0.69335 | 6.934% | -6.934%
19 | 9.966 | 2.0237 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0057 | -4.1449 | 1.0057 | -4.1449 | 0.97 | -3.3171 | 0.97 | -3.3171 | -4.5353 | 5.263 | 9.2718 | 1.8827 | -0.69419 | 6.966% | -6.966%
20 | 9.857 | 2.0015 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.2594 | 0.97 | -3.2594 | -4.6015 | 5.263 | 9.1603 | 1.8601 | -0.6967 | 7.068% | -7.068%
21 | 9.62 | 1.9534 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.1343 | 0.97 | -3.1343 | -4.7447 | 5.263 | 8.9188 | 1.811 | -0.70124 | 7.289% | -7.289%
22 | 9.139 | 1.8558 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0098 | -3.787 | 1.0098 | -3.787 | 0.97 | -2.8828 | 0.97 | -2.8828 | -5.0311 | 5.263 | 8.4323 | 1.7123 | -0.70669 | 7.733% | -7.733%
23 | 8.547 | 1.7355 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97095 | -2.5983 | 0.97095 | -2.5983 | -5.263 | 5.263 | 7.8557 | 1.5952 | -0.69132 | 8.088% | -8.088%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97335 | -2.3963 | 0.97335 | -2.3963 | -5.263 | 5.263 | 7.397 | 1.502 | -0.65003 | 8.078% | -8.078%
1 | 7.716 | 1.5668 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97494 | -2.2632 | 0.97494 | -2.2632 | -5.263 | 5.263 | 7.0934 | 1.4404 | -0.62264 | 8.069% | -8.069%
2 | 7.517 | 1.5264 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97589 | -2.1835 | 0.97589 | -2.1835 | -5.263 | 5.263 | 6.9108 | 1.4033 | -0.60617 | 8.064% | -8.064%
3 | 7.407 | 1.5041 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97641 | -2.1395 | 0.97641 | -2.1395 | -5.263 | 5.263 | 6.8099 | 1.3828 | -0.59706 | 8.061% | -8.061%
4 | 7.398 | 1.5022 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97645 | -2.1359 | 0.97645 | -2.1359 | -5.263 | 5.263 | 6.8017 | 1.3811 | -0.59631 | 8.06% | -8.06%
5 | 7.563 | 1.5357 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97567 | -2.2019 | 0.97567 | -2.2019 | -5.263 | 5.263 | 6.953 | 1.4119 | -0.60997 | 8.065% | -8.065%
6 | 7.986 | 1.6216 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97364 | -2.3717 | 0.97364 | -2.3717 | -5.263 | 5.263 | 7.341 | 1.4907 | -0.64497 | 8.076% | -8.076%
7 | 8.626 | 1.7516 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97056 | -2.6304 | 0.97056 | -2.6304 | -5.263 | 5.263 | 7.9282 | 1.6099 | -0.69783 | 8.09% | -8.09%
8 | 9.059 | 1.8395 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0102 | -3.7526 | 1.0102 | -3.7526 | 0.97 | -2.8412 | 0.97 | -2.8412 | -5.0782 | 5.263 | 8.3519 | 1.6959 | -0.70712 | 7.806% | -7.806%
9 | 9.181 | 1.8643 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -2.9046 | 0.97 | -2.9046 | -5.0063 | 5.263 | 8.4746 | 1.7208 | -0.70642 | 7.694% | -7.694%
10 | 9.23 | 1.8742 | 0.98 | Z | cloudy | 5.263 | 5.2577 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -2.9301 | 0.97 | -2.9301 | -4.9773 | 5.2577 | 8.524 | 1.7309 | -0.70605 | 7.65% | -7.65%
11 | 9.261 | 1.8805 | 0.98 | Z | cloudy | 5.263 | 5.2419 | 5 | 1.0092 | -3.8396 | 1.0092 | -3.8396 | 0.97 | -2.9463 | 0.97 | -2.9463 | -4.9589 | 5.2419 | 8.5552 | 1.7372 | -0.70579 | 7.621% | -7.621%
12 | 9.292 | 1.8868 | 0.98 | Z | cloudy | 5.263 | 5.2262 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -2.9625 | 0.97 | -2.9625 | -4.9405 | 5.2262 | 8.5865 | 1.7436 | -0.70551 | 7.593% | -7.593%
13 | 9.322 | 1.8929 | 0.98 | Z | cloudy | 5.263 | 5.2262 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -2.9781 | 0.97 | -2.9781 | -4.9227 | 5.2262 | 8.6168 | 1.7497 | -0.70522 | 7.565% | -7.565%
14 | 9.338 | 1.8962 | 0.98 | Z | cloudy | 5.263 | 5.2367 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -2.9865 | 0.97 | -2.9865 | -4.9132 | 5.2367 | 8.633 | 1.753 | -0.70505 | 7.55% | -7.55%
15 | 9.404 | 1.9096 | 0.98 | Z | cloudy | 5.263 | 5.2525 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.021 | 0.97 | -3.021 | -4.8739 | 5.2525 | 8.6997 | 1.7665 | -0.70432 | 7.49% | -7.49%
16 | 9.594 | 1.9481 | 0.98 | Z | cloudy | 5.263 | 5.2577 | 5 | 1.0075 | -3.9835 | 1.0075 | -3.9835 | 0.97 | -3.1206 | 0.97 | -3.1206 | -4.7603 | 5.2577 | 8.8923 | 1.8057 | -0.70167 | 7.314% | -7.314%
17 | 9.883 | 2.0068 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.2731 | 0.97 | -3.2731 | -4.5858 | 5.263 | 9.1869 | 1.8655 | -0.69613 | 7.044% | -7.044%
18 | 10 | 2.0306 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0055 | -4.1597 | 1.0055 | -4.1597 | 0.97 | -3.3352 | 0.97 | -3.3352 | -4.5145 | 5.263 | 9.3066 | 1.8898 | -0.69335 | 6.934% | -6.934%
19 | 9.966 | 2.0237 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0057 | -4.1449 | 1.0057 | -4.1449 | 0.97 | -3.3171 | 0.97 | -3.3171 | -4.5353 | 5.263 | 9.2718 | 1.8827 | -0.69419 | 6.966% | -6.966%
20 | 9.857 | 2.0015 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.2594 | 0.97 | -3.2594 | -4.6015 | 5.263 | 9.1603 | 1.8601 | -0.6967 | 7.068% | -7.068%
21 | 9.62 | 1.9534 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.1343 | 0.97 | -3.1343 | -4.7447 | 5.263 | 8.9188 | 1.811 | -0.70124 | 7.289% | -7.289%
22 | 9.139 | 1.8558 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0098 | -3.787 | 1.0098 | -3.787 | 0.97 | -2.8828 | 0.97 | -2.8828 | -5.0311 | 5.263 | 8.4323 | 1.7123 | -0.70669 | 7.733% | -7.733%
23 | 8.547 | 1.7355 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97095 | -2.5983 | 0.97095 | -2.5983 | -5.263 | 5.263 | 7.8557 | 1.5952 | -0.69132 | 8.088% | -8.088%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97335 | -2.3963 | 0.97335 | -2.3963 | -5.263 | 5.263 | 7.397 | 1.502 | -0.65003 | 8.078% | -8.078%
1 | 7.716 | 1.5668 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.1558 | 0.97 | -2.1558 | -5.8477 | 10.526 | 7.0217 | 1.4258 | -0.6943 | 8.998% | -8.998%
2 | 7.517 | 1.5264 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0178 | -3.0947 | 1.0178 | -3.0947 | 0.97 | -2.056 | 0.97 | -2.056 | -5.9585 | 10.526 | 6.8277 | 1.3864 | -0.68934 | 9.17% | -9.17%
3 | 7.407 | 1.5041 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0183 | -3.0482 | 1.0183 | -3.0482 | 0.97 | -2.0011 | 0.97 | -2.0011 | -6.0193 | 10.526 | 6.7208 | 1.3647 | -0.68625 | 9.265% | -9.265%
4 | 7.398 | 1.5022 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0184 | -3.0444 | 1.0184 | -3.0444 | 0.97 | -1.9966 | 0.97 | -1.9966 | -6.0243 | 10.526 | 6.712 | 1.3629 | -0.68599 | 9.273% | -9.273%
5 | 7.563 | 1.5357 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0176 | -3.1142 | 1.0176 | -3.1142 | 0.97 | -2.079 | 0.97 | -2.079 | -5.9329 | 10.526 | 6.8724 | 1.3955 | -0.69057 | 9.131% | -9.131%
6 | 7.986 | 1.6216 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.2918 | 0.97 | -2.2918 | -5.6962 | 10.526 | 7.2861 | 1.4795 | -0.69986 | 8.764% | -8.764%
7 | 8.626 | 1.7516 | 0.98 | Z | very sunny | 10.526 | 10.5049 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.6178 | 0.97 | -2.6178 | -5.3306 | 10.5049 | 7.9189 | 1.608 | -0.70707 | 8.197% | -8.197%
8 | 9.059 | 1.8395 | 0.98 | Z | very sunny | 10.526 | 10.2313 | 5 | 1.0102 | -3.7526 | 1.0102 | -3.7526 | 0.97 | -2.8412 | 0.97 | -2.8412 | -5.0782 | 10.2313 | 8.3519 | 1.6959 | -0.70713 | 7.806% | -7.806%
9 | 9.181 | 1.8643 | 0.98 | Z | very sunny | 10.526 | 9.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -2.9046 | 0.97 | -2.9046 | -5.0063 | 9.4102 | 8.4746 | 1.7208 | -0.70642 | 7.694% | -7.694%
10 | 9.23 | 1.8742 | 0.98 | Z | very sunny | 10.526 | 8.284 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -2.9301 | 0.97 | -2.9301 | -4.9773 | 8.284 | 8.524 | 1.7309 | -0.70605 | 7.65% | -7.65%
11 | 9.261 | 1.8805 | 0.98 | Z | very sunny | 10.526 | 7.1472 | 5 | 1.0092 | -3.8396 | 1.0092 | -3.8396 | 0.97 | -2.9463 | 0.97 | -2.9463 | -4.9589 | 7.1472 | 8.5552 | 1.7372 | -0.70579 | 7.621% | -7.621%
12 | 9.292 | 1.8868 | 0.98 | Z | very sunny | 10.526 | 6.5156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -2.9625 | 0.97 | -2.9625 | -4.9405 | 6.5156 | 8.5865 | 1.7436 | -0.70551 | 7.593% | -7.593%
13 | 9.322 | 1.8929 | 0.98 | Z | very sunny | 10.526 | 6.7051 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -2.9781 | 0.97 | -2.9781 | -4.9227 | 6.7051 | 8.6168 | 1.7497 | -0.70522 | 7.565% | -7.565%
14 | 9.338 | 1.8962 | 0.98 | Z | very sunny | 10.526 | 7.0103 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -2.9865 | 0.97 | -2.9865 | -4.9132 | 7.0103 | 8.633 | 1.753 | -0.70505 | 7.55% | -7.55%
15 | 9.404 | 1.9096 | 0.98 | Z | very sunny | 10.526 | 7.884 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.021 | 0.97 | -3.021 | -4.8739 | 7.884 | 8.6997 | 1.7665 | -0.70432 | 7.49% | -7.49%
16 | 9.594 | 1.9481 | 0.98 | Z | very sunny | 10.526 | 8.9155 | 5 | 1.0075 | -3.9835 | 1.0075 | -3.9835 | 0.97 | -3.1206 | 0.97 | -3.1206 | -4.7603 | 8.9155 | 8.8923 | 1.8057 | -0.70167 | 7.314% | -7.314%
17 | 9.883 | 2.0068 | 0.98 | Z | very sunny | 10.526 | 9.8418 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.2731 | 0.97 | -3.2731 | -4.5858 | 9.8418 | 9.1869 | 1.8655 | -0.69613 | 7.044% | -7.044%
18 | 10 | 2.0306 | 0.98 | Z | very sunny | 10.526 | 10.3786 | 5 | 1.0055 | -4.1597 | 1.0055 | -4.1597 | 0.97 | -3.3352 | 0.97 | -3.3352 | -4.5145 | 10.3786 | 9.3066 | 1.8898 | -0.69335 | 6.934% | -6.934%
19 | 9.966 | 2.0237 | 0.98 | Z | very sunny | 10.526 | 10.5155 | 5 | 1.0057 | -4.1449 | 1.0057 | -4.1449 | 0.97 | -3.3171 | 0.97 | -3.3171 | -4.5353 | 10.5155 | 9.2718 | 1.8827 | -0.69419 | 6.966% | -6.966%
20 | 9.857 | 2.0015 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.2594 | 0.97 | -3.2594 | -4.6015 | 10.526 | 9.1603 | 1.8601 | -0.6967 | 7.068% | -7.068%
21 | 9.62 | 1.9534 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.1343 | 0.97 | -3.1343 | -4.7447 | 10.526 | 8.9188 | 1.811 | -0.70124 | 7.289% | -7.289%
22 | 9.139 | 1.8558 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0098 | -3.787 | 1.0098 | -3.787 | 0.97 | -2.8828 | 0.97 | -2.8828 | -5.0311 | 10.526 | 8.4323 | 1.7123 | -0.70669 | 7.733% | -7.733%
23 | 8.547 | 1.7355 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.5773 | 0.97 | -2.5773 | -5.3762 | 10.526 | 7.8404 | 1.5921 | -0.70661 | 8.267% | -8.267%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.3227 | 0.97 | -2.3227 | -5.6617 | 10.526 | 7.3461 | 1.4917 | -0.70089 | 8.71% | -8.71%
1 | 7.716 | 1.5668 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.1558 | 0.97 | -2.1558 | -5.8477 | 10.526 | 7.0217 | 1.4258 | -0.69432 | 8.999% | -8.999%
2 | 7.517 | 1.5264 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0178 | -3.0947 | 1.0178 | -3.0947 | 0.97 | -2.056 | 0.97 | -2.056 | -5.9585 | 10.526 | 6.8277 | 1.3864 | -0.68934 | 9.17% | -9.17%
3 | 7.407 | 1.5041 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0183 | -3.0482 | 1.0183 | -3.0482 | 0.97 | -2.0011 | 0.97 | -2.0011 | -6.0193 | 10.526 | 6.7208 | 1.3647 | -0.68625 | 9.265% | -9.265%
4 | 7.398 | 1.5022 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0184 | -3.0444 | 1.0184 | -3.0444 | 0.97 | -1.9966 | 0.97 | -1.9966 | -6.0243 | 10.526 | 6.712 | 1.3629 | -0.68599 | 9.273% | -9.273%
5 | 7.563 | 1.5357 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0176 | -3.1142 | 1.0176 | -3.1142 | 0.97 | -2.079 | 0.97 | -2.079 | -5.9329 | 10.526 | 6.8724 | 1.3955 | -0.69057 | 9.131% | -9.131%
6 | 7.986 | 1.6216 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.2918 | 0.97 | -2.2918 | -5.6962 | 10.526 | 7.2861 | 1.4795 | -0.69986 | 8.764% | -8.764%
7 | 8.626 | 1.7516 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.6178 | 0.97 | -2.6178 | -5.3306 | 10.526 | 7.9189 | 1.608 | -0.70707 | 8.197% | -8.197%
8 | 9.059 | 1.8395 | 0.98 | Z | moderate sun | 10.526 | 10.5155 | 5 | 1.0102 | -3.7526 | 1.0102 | -3.7526 | 0.97 | -2.8412 | 0.97 | -2.8412 | -5.0782 | 10.5155 | 8.3519 | 1.6959 | -0.70713 | 7.806% | -7.806%
9 | 9.181 | 1.8643 | 0.98 | Z | moderate sun | 10.526 | 10.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -2.9046 | 0.97 | -2.9046 | -5.0063 | 10.4102 | 8.4746 | 1.7208 | -0.70642 | 7.694% | -7.694%
10 | 9.23 | 1.8742 | 0.98 | Z | moderate sun | 10.526 | 10.1892 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -2.9301 | 0.97 | -2.9301 | -4.9773 | 10.1892 | 8.524 | 1.7309 | -0.70605 | 7.65% | -7.65%
11 | 9.261 | 1.8805 | 0.98 | Z | moderate sun | 10.526 | 9.9576 | 5 | 1.0092 | -3.8396 | 1.0092 | -3.8396 | 0.97 | -2.9463 | 0.97 | -2.9463 | -4.9589 | 9.9576 | 8.5552 | 1.7372 | -0.70579 | 7.621% | -7.621%
12 | 9.292 | 1.8868 | 0.98 | Z | moderate sun | 10.526 | 9.8313 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -2.9625 | 0.97 | -2.9625 | -4.9405 | 9.8313 | 8.5865 | 1.7436 | -0.70551 | 7.593% | -7.593%
13 | 9.322 | 1.8929 | 0.98 | Z | moderate sun | 10.526 | 9.9681 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -2.9781 | 0.97 | -2.9781 | -4.9227 | 9.9681 | 8.6168 | 1.7497 | -0.70522 | 7.565% | -7.565%
14 | 9.338 | 1.8962 | 0.98 | Z | moderate sun | 10.526 | 10.0313 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -2.9865 | 0.97 | -2.9865 | -4.9132 | 10.0313 | 8.633 | 1.753 | -0.70505 | 7.55% | -7.55%
15 | 9.404 | 1.9096 | 0.98 | Z | moderate sun | 10.526 | 10.2944 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.021 | 0.97 | -3.021 | -4.8739 | 10.2944 | 8.6997 | 1.7665 | -0.70432 | 7.49% | -7.49%
16 | 9.594 | 1.9481 | 0.98 | Z | moderate sun | 10.526 | 10.4734 | 5 | 1.0075 | -3.9835 | 1.0075 | -3.9835 | 0.97 | -3.1206 | 0.97 | -3.1206 | -4.7603 | 10.4734 | 8.8923 | 1.8057 | -0.70167 | 7.314% | -7.314%
17 | 9.883 | 2.0068 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.2731 | 0.97 | -3.2731 | -4.5858 | 10.526 | 9.1869 | 1.8655 | -0.69613 | 7.044% | -7.044%
18 | 10 | 2.0306 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0055 | -4.1597 | 1.0055 | -4.1597 | 0.97 | -3.3352 | 0.97 | -3.3352 | -4.5145 | 10.526 | 9.3066 | 1.8898 | -0.69335 | 6.934% | -6.934%
19 | 9.966 | 2.0237 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0057 | -4.1449 | 1.0057 | -4.1449 | 0.97 | -3.3171 | 0.97 | -3.3171 | -4.5353 | 10.526 | 9.2718 | 1.8827 | -0.69419 | 6.966% | -6.966%
20 | 9.857 | 2.0015 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.2594 | 0.97 | -3.2594 | -4.6015 | 10.526 | 9.1603 | 1.8601 | -0.6967 | 7.068% | -7.068%
21 | 9.62 | 1.9534 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.1343 | 0.97 | -3.1343 | -4.7447 | 10.526 | 8.9188 | 1.811 | -0.70124 | 7.289% | -7.289%
22 | 9.139 | 1.8558 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0098 | -3.787 | 1.0098 | -3.787 | 0.97 | -2.8828 | 0.97 | -2.8828 | -5.0311 | 10.526 | 8.4323 | 1.7123 | -0.70669 | 7.733% | -7.733%
23 | 8.547 | 1.7355 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.5773 | 0.97 | -2.5773 | -5.3762 | 10.526 | 7.8404 | 1.5921 | -0.70661 | 8.267% | -8.267%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.3227 | 0.97 | -2.3227 | -5.6617 | 10.526 | 7.3461 | 1.4917 | -0.70089 | 8.71% | -8.71%
1 | 7.716 | 1.5668 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.1558 | 0.97 | -2.1558 | -5.8477 | 10.526 | 7.0217 | 1.4258 | -0.69432 | 8.999% | -8.999%
2 | 7.517 | 1.5264 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0178 | -3.0947 | 1.0178 | -3.0947 | 0.97 | -2.056 | 0.97 | -2.056 | -5.9585 | 10.526 | 6.8277 | 1.3864 | -0.68934 | 9.17% | -9.17%
3 | 7.407 | 1.5041 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0183 | -3.0482 | 1.0183 | -3.0482 | 0.97 | -2.0011 | 0.97 | -2.0011 | -6.0193 | 10.526 | 6.7208 | 1.3647 | -0.68625 | 9.265% | -9.265%
4 | 7.398 | 1.5022 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0184 | -3.0444 | 1.0184 | -3.0444 | 0.97 | -1.9966 | 0.97 | -1.9966 | -6.0243 | 10.526 | 6.712 | 1.3629 | -0.68599 | 9.273% | -9.273%
5 | 7.563 | 1.5357 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0176 | -3.1142 | 1.0176 | -3.1142 | 0.97 | -2.079 | 0.97 | -2.079 | -5.9329 | 10.526 | 6.8724 | 1.3955 | -0.69057 | 9.131% | -9.131%
6 | 7.986 | 1.6216 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.2918 | 0.97 | -2.2918 | -5.6962 | 10.526 | 7.2861 | 1.4795 | -0.69986 | 8.764% | -8.764%
7 | 8.626 | 1.7516 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.6178 | 0.97 | -2.6178 | -5.3306 | 10.526 | 7.9189 | 1.608 | -0.70707 | 8.197% | -8.197%
8 | 9.059 | 1.8395 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0102 | -3.7526 | 1.0102 | -3.7526 | 0.97 | -2.8412 | 0.97 | -2.8412 | -5.0782 | 10.526 | 8.3519 | 1.6959 | -0.70713 | 7.806% | -7.806%
9 | 9.181 | 1.8643 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -2.9046 | 0.97 | -2.9046 | -5.0063 | 10.526 | 8.4746 | 1.7208 | -0.70642 | 7.694% | -7.694%
10 | 9.23 | 1.8742 | 0.98 | Z | cloudy | 10.526 | 10.5155 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -2.9301 | 0.97 | -2.9301 | -4.9773 | 10.5155 | 8.524 | 1.7309 | -0.70605 | 7.65% | -7.65%
11 | 9.261 | 1.8805 | 0.98 | Z | cloudy | 10.526 | 10.4839 | 5 | 1.0092 | -3.8396 | 1.0092 | -3.8396 | 0.97 | -2.9463 | 0.97 | -2.9463 | -4.9589 | 10.4839 | 8.5552 | 1.7372 | -0.70579 | 7.621% | -7.621%
12 | 9.292 | 1.8868 | 0.98 | Z | cloudy | 10.526 | 10.4523 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -2.9625 | 0.97 | -2.9625 | -4.9405 | 10.4523 | 8.5865 | 1.7436 | -0.70551 | 7.593% | -7.593%
13 | 9.322 | 1.8929 | 0.98 | Z | cloudy | 10.526 | 10.4523 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -2.9781 | 0.97 | -2.9781 | -4.9227 | 10.4523 | 8.6168 | 1.7497 | -0.70522 | 7.565% | -7.565%
14 | 9.338 | 1.8962 | 0.98 | Z | cloudy | 10.526 | 10.4734 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -2.9865 | 0.97 | -2.9865 | -4.9132 | 10.4734 | 8.633 | 1.753 | -0.70505 | 7.55% | -7.55%
15 | 9.404 | 1.9096 | 0.98 | Z | cloudy | 10.526 | 10.5049 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.021 | 0.97 | -3.021 | -4.8739 | 10.5049 | 8.6997 | 1.7665 | -0.70432 | 7.49% | -7.49%
16 | 9.594 | 1.9481 | 0.98 | Z | cloudy | 10.526 | 10.5155 | 5 | 1.0075 | -3.9835 | 1.0075 | -3.9835 | 0.97 | -3.1206 | 0.97 | -3.1206 | -4.7603 | 10.5155 | 8.8923 | 1.8057 | -0.70167 | 7.314% | -7.314%
17 | 9.883 | 2.0068 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.2731 | 0.97 | -3.2731 | -4.5858 | 10.526 | 9.1869 | 1.8655 | -0.69613 | 7.044% | -7.044%
18 | 10 | 2.0306 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0055 | -4.1597 | 1.0055 | -4.1597 | 0.97 | -3.3352 | 0.97 | -3.3352 | -4.5145 | 10.526 | 9.3066 | 1.8898 | -0.69335 | 6.934% | -6.934%
19 | 9.966 | 2.0237 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0057 | -4.1449 | 1.0057 | -4.1449 | 0.97 | -3.3171 | 0.97 | -3.3171 | -4.5353 | 10.526 | 9.2718 | 1.8827 | -0.69419 | 6.966% | -6.966%
20 | 9.857 | 2.0015 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.2594 | 0.97 | -3.2594 | -4.6015 | 10.526 | 9.1603 | 1.8601 | -0.6967 | 7.068% | -7.068%
21 | 9.62 | 1.9534 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.1343 | 0.97 | -3.1343 | -4.7447 | 10.526 | 8.9188 | 1.811 | -0.70124 | 7.289% | -7.289%
22 | 9.139 | 1.8558 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0098 | -3.787 | 1.0098 | -3.787 | 0.97 | -2.8828 | 0.97 | -2.8828 | -5.0311 | 10.526 | 8.4323 | 1.7123 | -0.70669 | 7.733% | -7.733%
23 | 8.547 | 1.7355 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.5773 | 0.97 | -2.5773 | -5.3762 | 10.526 | 7.8404 | 1.5921 | -0.70661 | 8.267% | -8.267%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.3227 | 0.97 | -2.3227 | -5.6617 | 10.526 | 7.3461 | 1.4917 | -0.70089 | 8.71% | -8.71%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.92 | 1.023 | -0.9 | 0.985 | -2.797 | -5.263 | 5.263 | 7.613 | 3.687 | -0.103 | 1.335% | -1.335%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.873 | 0.987 | -2.718 | -5.263 | 5.263 | 7.417 | 3.592 | -0.1 | 1.33% | -1.33%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.859 | 0.988 | -2.675 | -5.263 | 5.263 | 7.309 | 3.54 | -0.098 | 1.323% | -1.323%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.857 | 0.988 | -2.671 | -5.263 | 5.263 | 7.3 | 3.535 | -0.098 | 1.325% | -1.325%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.879 | 0.987 | -2.737 | -5.263 | 5.263 | 7.463 | 3.614 | -0.1 | 1.322% | -1.322%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.936 | 0.983 | -2.904 | -5.263 | 5.263 | 7.88 | 3.816 | -0.106 | 1.327% | -1.327%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 5.263 | 5.252 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.021 | -1.022 | 0.979 | -3.161 | -5.252 | 5.252 | 8.511 | 4.122 | -0.115 | 1.333% | -1.333%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 5.263 | 5.116 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 5.116 | 8.968 | 4.343 | -0.091 | 1.005% | -1.005%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 5.263 | 4.705 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 4.705 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 5.263 | 4.142 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 4.142 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 5.263 | 3.574 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.155 | 0.978 | -3.471 | -3.574 | 3.574 | 9.175 | 4.443 | -0.086 | 0.9286% | -0.9286%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 5.263 | 3.258 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.025 | -1.166 | 0.979 | -3.486 | -3.258 | 3.258 | 9.214 | 4.462 | -0.078 | 0.8394% | -0.8394%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 5.263 | 3.353 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.025 | -1.168 | 0.978 | -3.497 | -3.353 | 3.353 | 9.241 | 4.476 | -0.081 | 0.8689% | -0.8689%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 5.263 | 3.505 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.024 | -1.167 | 0.978 | -3.503 | -3.505 | 3.505 | 9.253 | 4.481 | -0.085 | 0.9103% | -0.9103%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 5.263 | 3.942 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 3.942 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 5.263 | 4.458 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 4.458 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 5.263 | 4.921 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 4.921 | 9.783 | 4.738 | -0.1 | 1.012% | -1.012%
18 | 10 | 4.843 | 0.9 | I | very sunny | 5.263 | 5.189 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 5.189 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 5.263 | 5.258 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 5.258 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.011 | 0.979 | -3.129 | -5.263 | 5.263 | 8.433 | 4.084 | -0.114 | 1.334% | -1.334%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.944 | 0.983 | -2.929 | -5.263 | 5.263 | 7.94 | 3.845 | -0.107 | 1.33% | -1.33%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.023 | -0.9 | 0.985 | -2.797 | -5.263 | 5.263 | 7.613 | 3.687 | -0.103 | 1.335% | -1.335%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.873 | 0.987 | -2.718 | -5.263 | 5.263 | 7.417 | 3.592 | -0.1 | 1.33% | -1.33%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.859 | 0.988 | -2.675 | -5.263 | 5.263 | 7.309 | 3.54 | -0.098 | 1.323% | -1.323%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.857 | 0.988 | -2.671 | -5.263 | 5.263 | 7.3 | 3.535 | -0.098 | 1.325% | -1.325%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.879 | 0.987 | -2.737 | -5.263 | 5.263 | 7.463 | 3.614 | -0.1 | 1.322% | -1.322%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.936 | 0.983 | -2.904 | -5.263 | 5.263 | 7.88 | 3.816 | -0.106 | 1.327% | -1.327%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.021 | -1.021 | 0.979 | -3.161 | -5.263 | 5.263 | 8.511 | 4.122 | -0.115 | 1.333% | -1.333%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 5.263 | 5.258 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 5.258 | 8.968 | 4.343 | -0.091 | 1.005% | -1.005%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 5.263 | 5.205 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 5.205 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 5.263 | 5.095 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 5.095 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 5.263 | 4.979 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 4.979 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 5.263 | 4.916 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 4.916 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 5.263 | 4.984 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 4.984 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 5.263 | 5.016 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 5.016 | 9.244 | 4.477 | -0.094 | 1.007% | -1.007%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 5.263 | 5.147 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 5.147 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 5.263 | 5.237 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 5.237 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 5.263 | 9.783 | 4.738 | -0.1 | 1.012% | -1.012%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.011 | 0.979 | -3.129 | -5.263 | 5.263 | 8.433 | 4.084 | -0.114 | 1.334% | -1.334%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.944 | 0.983 | -2.929 | -5.263 | 5.263 | 7.94 | 3.845 | -0.107 | 1.33% | -1.33%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.023 | -0.9 | 0.985 | -2.797 | -5.263 | 5.263 | 7.613 | 3.687 | -0.103 | 1.335% | -1.335%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.873 | 0.987 | -2.718 | -5.263 | 5.263 | 7.417 | 3.592 | -0.1 | 1.33% | -1.33%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.859 | 0.988 | -2.675 | -5.263 | 5.263 | 7.309 | 3.54 | -0.098 | 1.323% | -1.323%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.857 | 0.988 | -2.671 | -5.263 | 5.263 | 7.3 | 3.535 | -0.098 | 1.325% | -1.325%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.879 | 0.987 | -2.737 | -5.263 | 5.263 | 7.463 | 3.614 | -0.1 | 1.322% | -1.322%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.936 | 0.983 | -2.904 | -5.263 | 5.263 | 7.88 | 3.816 | -0.106 | 1.327% | -1.327%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.021 | -1.021 | 0.979 | -3.161 | -5.263 | 5.263 | 8.511 | 4.122 | -0.115 | 1.333% | -1.333%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 5.263 | 8.968 | 4.343 | -0.091 | 1.005% | -1.005%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 5.263 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 5.263 | 5.258 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 5.258 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 5.263 | 5.242 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 5.242 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 5.263 | 5.226 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 5.226 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 5.263 | 5.226 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 5.226 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 5.263 | 5.237 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 5.237 | 9.244 | 4.477 | -0.094 | 1.007% | -1.007%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 5.263 | 5.252 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 5.252 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 5.263 | 5.258 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 5.258 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 5.263 | 9.783 | 4.738 | -0.1 | 1.012% | -1.012%
18 | 10 | 4.843 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.011 | 0.979 | -3.129 | -5.263 | 5.263 | 8.433 | 4.084 | -0.114 | 1.334% | -1.334%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.944 | 0.983 | -2.929 | -5.263 | 5.263 | 7.94 | 3.845 | -0.107 | 1.33% | -1.33%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.848 | 0.979 | -2.771 | -7.636 | 10.526 | 7.562 | 3.662 | -0.154 | 1.996% | -1.996%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.748 | 0.973 | -2.627 | -10.526 | 10.526 | 7.309 | 3.54 | -0.208 | 2.767% | -2.767%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.733 | 0.973 | -2.583 | -10.526 | 10.526 | 7.202 | 3.488 | -0.205 | 2.768% | -2.768%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.732 | 0.973 | -2.58 | -10.526 | 10.526 | 7.194 | 3.484 | -0.204 | 2.757% | -2.757%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.017 | -0.828 | 0.98 | -2.71 | -7.637 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.885 | 0.977 | -2.88 | -7.632 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 10.526 | 10.505 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.971 | 0.972 | -3.139 | -7.624 | 10.505 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 10.526 | 10.231 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 10.231 | 8.968 | 4.343 | -0.091 | 1.005% | -1.005%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 10.526 | 9.41 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 9.41 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 10.526 | 8.284 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 8.284 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 10.526 | 7.147 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 7.147 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 10.526 | 6.516 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 6.516 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 10.526 | 6.705 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 6.705 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 10.526 | 7.01 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 7.01 | 9.244 | 4.477 | -0.094 | 1.007% | -1.007%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 10.526 | 7.884 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 7.884 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 10.526 | 8.916 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 8.916 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 10.526 | 9.842 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 9.842 | 9.783 | 4.738 | -0.1 | 1.012% | -1.012%
18 | 10 | 4.843 | 0.9 | I | very sunny | 10.526 | 10.379 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 10.379 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 10.526 | 10.515 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 10.515 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.96 | 0.973 | -3.107 | -7.625 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.893 | 0.976 | -2.904 | -7.631 | 10.526 | 7.886 | 3.819 | -0.161 | 2.001% | -2.001%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.848 | 0.979 | -2.771 | -7.635 | 10.526 | 7.562 | 3.662 | -0.154 | 1.996% | -1.996%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.748 | 0.973 | -2.627 | -10.526 | 10.526 | 7.309 | 3.54 | -0.208 | 2.767% | -2.767%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.733 | 0.973 | -2.583 | -10.526 | 10.526 | 7.202 | 3.488 | -0.205 | 2.768% | -2.768%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.732 | 0.973 | -2.58 | -10.526 | 10.526 | 7.194 | 3.484 | -0.204 | 2.757% | -2.757%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.017 | -0.828 | 0.98 | -2.71 | -7.637 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.885 | 0.977 | -2.88 | -7.632 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.971 | 0.972 | -3.139 | -7.624 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 10.526 | 10.515 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 10.515 | 8.968 | 4.343 | -0.091 | 1.005% | -1.005%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 10.526 | 10.41 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 10.41 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 10.526 | 10.189 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 10.189 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 10.526 | 9.958 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 9.958 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 10.526 | 9.831 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 9.831 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 10.526 | 9.968 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 9.968 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 10.526 | 10.031 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 10.031 | 9.244 | 4.477 | -0.094 | 1.007% | -1.007%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 10.526 | 10.294 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 10.294 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 10.526 | 10.473 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 10.473 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 10.526 | 9.783 | 4.738 | -0.1 | 1.012% | -1.012%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.96 | 0.973 | -3.107 | -7.625 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.893 | 0.976 | -2.904 | -7.631 | 10.526 | 7.886 | 3.819 | -0.161 | 2.001% | -2.001%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.848 | 0.979 | -2.771 | -7.635 | 10.526 | 7.562 | 3.662 | -0.154 | 1.996% | -1.996%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.748 | 0.973 | -2.627 | -10.526 | 10.526 | 7.309 | 3.54 | -0.208 | 2.767% | -2.767%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.733 | 0.973 | -2.583 | -10.526 | 10.526 | 7.202 | 3.488 | -0.205 | 2.768% | -2.768%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.732 | 0.973 | -2.58 | -10.526 | 10.526 | 7.194 | 3.484 | -0.204 | 2.757% | -2.757%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.017 | -0.828 | 0.98 | -2.71 | -7.637 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.885 | 0.977 | -2.88 | -7.632 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.971 | 0.972 | -3.139 | -7.624 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 10.526 | 8.968 | 4.343 | -0.091 | 1.005% | -1.005%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 10.526 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 10.526 | 10.515 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 10.515 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 10.526 | 10.484 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 10.484 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 10.526 | 10.452 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 10.452 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 10.526 | 10.452 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 10.452 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 10.526 | 10.473 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 10.473 | 9.244 | 4.477 | -0.094 | 1.007% | -1.007%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 10.526 | 10.505 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 10.505 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 10.526 | 10.515 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 10.515 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 10.526 | 9.783 | 4.738 | -0.1 | 1.012% | -1.012%
18 | 10 | 4.843 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.96 | 0.973 | -3.107 | -7.625 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.893 | 0.976 | -2.904 | -7.631 | 10.526 | 7.886 | 3.819 | -0.161 | 2.001% | -2.001%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 5.263 | 7.561 | 3.662 | -0.155 | 2.009% | -2.009%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.99 | -1.451 | 0.972 | -2.41 | -5.263 | 5.263 | 7.303 | 3.537 | -0.214 | 2.847% | -2.847%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.991 | -1.423 | 0.973 | -2.366 | -5.263 | 5.263 | 7.196 | 3.485 | -0.211 | 2.849% | -2.849%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.991 | -1.421 | 0.973 | -2.363 | -5.263 | 5.263 | 7.188 | 3.481 | -0.21 | 2.839% | -2.839%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 5.263 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 5.263 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 5.263 | 5.252 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 5.252 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 5.263 | 5.116 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 5.116 | 8.967 | 4.343 | -0.092 | 1.016% | -1.016%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 5.263 | 4.705 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 4.705 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 5.263 | 4.142 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 4.142 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 5.263 | 3.574 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 3.574 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 5.263 | 3.258 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 3.258 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 5.263 | 3.353 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 3.353 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 5.263 | 3.505 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 3.505 | 9.243 | 4.477 | -0.095 | 1.017% | -1.017%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 5.263 | 3.942 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 3.942 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 5.263 | 4.458 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 4.458 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 5.263 | 4.921 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 4.921 | 9.782 | 4.738 | -0.101 | 1.022% | -1.022%
18 | 10 | 4.843 | 0.9 | I | very sunny | 5.263 | 5.189 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 5.189 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 5.263 | 5.258 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 5.258 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 5.263 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 5.263 | 7.885 | 3.819 | -0.162 | 2.013% | -2.013%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 5.263 | 7.561 | 3.662 | -0.155 | 2.009% | -2.009%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.99 | -1.451 | 0.972 | -2.41 | -5.263 | 5.263 | 7.303 | 3.537 | -0.214 | 2.847% | -2.847%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.991 | -1.423 | 0.973 | -2.366 | -5.263 | 5.263 | 7.196 | 3.485 | -0.211 | 2.849% | -2.849%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.991 | -1.421 | 0.973 | -2.363 | -5.263 | 5.263 | 7.188 | 3.481 | -0.21 | 2.839% | -2.839%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 5.263 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 5.263 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 5.263 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 5.263 | 5.258 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 5.258 | 8.967 | 4.343 | -0.092 | 1.016% | -1.016%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 5.263 | 5.205 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 5.205 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 5.263 | 5.095 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 5.095 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 5.263 | 4.979 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 4.979 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 5.263 | 4.916 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 4.916 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 5.263 | 4.984 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 4.984 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 5.263 | 5.016 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 5.016 | 9.243 | 4.477 | -0.095 | 1.017% | -1.017%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 5.263 | 5.147 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 5.147 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 5.263 | 5.237 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 5.237 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 5.263 | 9.782 | 4.738 | -0.101 | 1.022% | -1.022%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 5.263 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 5.263 | 7.885 | 3.819 | -0.162 | 2.013% | -2.013%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 5.263 | 7.561 | 3.662 | -0.155 | 2.009% | -2.009%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.99 | -1.451 | 0.972 | -2.41 | -5.263 | 5.263 | 7.303 | 3.537 | -0.214 | 2.847% | -2.847%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.991 | -1.423 | 0.973 | -2.366 | -5.263 | 5.263 | 7.196 | 3.485 | -0.211 | 2.849% | -2.849%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.991 | -1.421 | 0.973 | -2.363 | -5.263 | 5.263 | 7.188 | 3.481 | -0.21 | 2.839% | -2.839%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 5.263 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 5.263 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 5.263 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 5.263 | 8.967 | 4.343 | -0.092 | 1.016% | -1.016%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 5.263 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 5.263 | 5.258 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 5.258 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 5.263 | 5.242 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 5.242 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 5.263 | 5.226 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 5.226 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 5.263 | 5.226 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 5.226 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 5.263 | 5.237 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 5.237 | 9.243 | 4.477 | -0.095 | 1.017% | -1.017%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 5.263 | 5.252 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 5.252 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 5.263 | 5.258 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 5.258 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 5.263 | 9.782 | 4.738 | -0.101 | 1.022% | -1.022%
18 | 10 | 4.843 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 5.263 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 5.263 | 7.885 | 3.819 | -0.162 | 2.013% | -2.013%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 10.526 | 7.561 | 3.662 | -0.155 | 2.009% | -2.009%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.431 | 0.97 | -2.393 | -5.521 | 10.526 | 7.292 | 3.531 | -0.225 | 2.993% | -2.993%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.403 | 0.971 | -2.349 | -5.523 | 10.526 | 7.185 | 3.48 | -0.222 | 2.997% | -2.997%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.4 | 0.971 | -2.346 | -5.523 | 10.526 | 7.176 | 3.476 | -0.222 | 3.001% | -3.001%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 10.526 | 10.505 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 10.505 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 10.526 | 10.231 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 10.231 | 8.967 | 4.343 | -0.092 | 1.016% | -1.016%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 10.526 | 9.41 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 9.41 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 10.526 | 8.284 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 8.284 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 10.526 | 7.147 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 7.147 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 10.526 | 6.516 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 6.516 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 10.526 | 6.705 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 6.705 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 10.526 | 7.01 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 7.01 | 9.243 | 4.477 | -0.095 | 1.017% | -1.017%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 10.526 | 7.884 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 7.884 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 10.526 | 8.916 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 8.916 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 10.526 | 9.842 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 9.842 | 9.782 | 4.738 | -0.101 | 1.022% | -1.022%
18 | 10 | 4.843 | 0.9 | I | very sunny | 10.526 | 10.379 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 10.379 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 10.526 | 10.515 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 10.515 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 10.526 | 7.885 | 3.819 | -0.162 | 2.013% | -2.013%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 10.526 | 7.561 | 3.662 | -0.155 | 2.009% | -2.009%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.431 | 0.97 | -2.393 | -5.521 | 10.526 | 7.292 | 3.531 | -0.225 | 2.993% | -2.993%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.403 | 0.971 | -2.349 | -5.523 | 10.526 | 7.185 | 3.48 | -0.222 | 2.997% | -2.997%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.4 | 0.971 | -2.346 | -5.523 | 10.526 | 7.176 | 3.476 | -0.222 | 3.001% | -3.001%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 10.526 | 10.515 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 10.515 | 8.967 | 4.343 | -0.092 | 1.016% | -1.016%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 10.526 | 10.41 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 10.41 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 10.526 | 10.189 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 10.189 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 10.526 | 9.958 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 9.958 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 10.526 | 9.831 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 9.831 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 10.526 | 9.968 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 9.968 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 10.526 | 10.031 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 10.031 | 9.243 | 4.477 | -0.095 | 1.017% | -1.017%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 10.526 | 10.294 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 10.294 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 10.526 | 10.473 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 10.473 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 10.526 | 9.782 | 4.738 | -0.101 | 1.022% | -1.022%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 10.526 | 7.885 | 3.819 | -0.162 | 2.013% | -2.013%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 10.526 | 7.561 | 3.662 | -0.155 | 2.009% | -2.009%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.431 | 0.97 | -2.393 | -5.521 | 10.526 | 7.292 | 3.531 | -0.225 | 2.993% | -2.993%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.403 | 0.971 | -2.349 | -5.523 | 10.526 | 7.185 | 3.48 | -0.222 | 2.997% | -2.997%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.4 | 0.971 | -2.346 | -5.523 | 10.526 | 7.176 | 3.476 | -0.222 | 3.001% | -3.001%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997% | -1.997%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004% | -2.004%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017% | -2.017%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 10.526 | 8.967 | 4.343 | -0.092 | 1.016% | -1.016%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 10.526 | 9.088 | 4.402 | -0.093 | 1.013% | -1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 10.526 | 10.515 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 10.515 | 9.137 | 4.425 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 10.526 | 10.484 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 10.484 | 9.167 | 4.44 | -0.094 | 1.015% | -1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 10.526 | 10.452 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 10.452 | 9.198 | 4.455 | -0.094 | 1.012% | -1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 10.526 | 10.452 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 10.452 | 9.228 | 4.469 | -0.094 | 1.008% | -1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 10.526 | 10.473 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 10.473 | 9.243 | 4.477 | -0.095 | 1.017% | -1.017%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 10.526 | 10.505 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 10.505 | 9.309 | 4.508 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 10.526 | 10.515 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 10.515 | 9.497 | 4.599 | -0.097 | 1.011% | -1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 10.526 | 9.782 | 4.738 | -0.101 | 1.022% | -1.022%
18 | 10 | 4.843 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02% | -1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013% | -1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015% | -1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019% | -1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007% | -1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012% | -2.012%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 10.526 | 7.885 | 3.819 | -0.162 | 2.013% | -2.013%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 5.263 | 7.494 | 3.629 | -0.222 | 2.877% | -2.877%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 5.263 | 7.29 | 3.531 | -0.227 | 3.02% | -3.02%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 5.263 | 7.177 | 3.476 | -0.23 | 3.105% | -3.105%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 5.263 | 7.168 | 3.472 | -0.23 | 3.109% | -3.109%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 5.263 | 7.337 | 3.553 | -0.226 | 2.988% | -2.988%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 5.263 | 7.772 | 3.764 | -0.214 | 2.68% | -2.68%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 5.263 | 5.252 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 5.252 | 8.435 | 4.085 | -0.191 | 2.214% | -2.214%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 5.263 | 5.116 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 5.116 | 8.888 | 4.305 | -0.171 | 1.888% | -1.888%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 5.263 | 4.705 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 4.705 | 9.016 | 4.367 | -0.165 | 1.797% | -1.797%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 5.263 | 4.142 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 4.142 | 9.068 | 4.392 | -0.162 | 1.755% | -1.755%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 5.263 | 3.574 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 3.574 | 9.1 | 4.407 | -0.161 | 1.738% | -1.738%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 5.263 | 3.258 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 3.258 | 9.133 | 4.423 | -0.159 | 1.711% | -1.711%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 5.263 | 3.353 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 3.353 | 9.164 | 4.439 | -0.158 | 1.695% | -1.695%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 5.263 | 3.505 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 3.505 | 9.181 | 4.447 | -0.157 | 1.681% | -1.681%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 5.263 | 3.942 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 3.942 | 9.251 | 4.48 | -0.153 | 1.627% | -1.627%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 5.263 | 4.458 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 4.458 | 9.452 | 4.578 | -0.142 | 1.48% | -1.48%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 5.263 | 4.921 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 4.921 | 9.759 | 4.726 | -0.124 | 1.255% | -1.255%
18 | 10 | 4.843 | 0.9 | I | very sunny | 5.263 | 5.189 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 5.189 | 9.883 | 4.787 | -0.117 | 1.17% | -1.17%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 5.263 | 5.258 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 5.258 | 9.847 | 4.769 | -0.119 | 1.194% | -1.194%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 5.263 | 9.731 | 4.713 | -0.126 | 1.278% | -1.278%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 5.263 | 9.479 | 4.591 | -0.141 | 1.466% | -1.466%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 5.263 | 8.972 | 4.345 | -0.167 | 1.827% | -1.827%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 5.263 | 8.353 | 4.045 | -0.194 | 2.27% | -2.27%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 5.263 | 7.835 | 3.794 | -0.212 | 2.635% | -2.635%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 5.263 | 7.494 | 3.629 | -0.222 | 2.877% | -2.877%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 5.263 | 7.29 | 3.531 | -0.227 | 3.02% | -3.02%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 5.263 | 7.177 | 3.476 | -0.23 | 3.105% | -3.105%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 5.263 | 7.168 | 3.472 | -0.23 | 3.109% | -3.109%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 5.263 | 7.337 | 3.553 | -0.226 | 2.988% | -2.988%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 5.263 | 7.772 | 3.764 | -0.214 | 2.68% | -2.68%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 5.263 | 8.435 | 4.085 | -0.191 | 2.214% | -2.214%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 5.263 | 5.258 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 5.258 | 8.888 | 4.305 | -0.171 | 1.888% | -1.888%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 5.263 | 5.205 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 5.205 | 9.016 | 4.367 | -0.165 | 1.797% | -1.797%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 5.263 | 5.095 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 5.095 | 9.068 | 4.392 | -0.162 | 1.755% | -1.755%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 5.263 | 4.979 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 4.979 | 9.1 | 4.407 | -0.161 | 1.738% | -1.738%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 5.263 | 4.916 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 4.916 | 9.133 | 4.423 | -0.159 | 1.711% | -1.711%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 5.263 | 4.984 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 4.984 | 9.164 | 4.439 | -0.158 | 1.695% | -1.695%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 5.263 | 5.016 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 5.016 | 9.181 | 4.447 | -0.157 | 1.681% | -1.681%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 5.263 | 5.147 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 5.147 | 9.251 | 4.48 | -0.153 | 1.627% | -1.627%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 5.263 | 5.237 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 5.237 | 9.452 | 4.578 | -0.142 | 1.48% | -1.48%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 5.263 | 9.759 | 4.726 | -0.124 | 1.255% | -1.255%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 5.263 | 9.883 | 4.787 | -0.117 | 1.17% | -1.17%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 5.263 | 9.847 | 4.769 | -0.119 | 1.194% | -1.194%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 5.263 | 9.731 | 4.713 | -0.126 | 1.278% | -1.278%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 5.263 | 9.479 | 4.591 | -0.141 | 1.466% | -1.466%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 5.263 | 8.972 | 4.345 | -0.167 | 1.827% | -1.827%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 5.263 | 8.353 | 4.045 | -0.194 | 2.27% | -2.27%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 5.263 | 7.835 | 3.794 | -0.212 | 2.635% | -2.635%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 5.263 | 7.494 | 3.629 | -0.222 | 2.877% | -2.877%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 5.263 | 7.29 | 3.531 | -0.227 | 3.02% | -3.02%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 5.263 | 7.177 | 3.476 | -0.23 | 3.105% | -3.105%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 5.263 | 7.168 | 3.472 | -0.23 | 3.109% | -3.109%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 5.263 | 7.337 | 3.553 | -0.226 | 2.988% | -2.988%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 5.263 | 7.772 | 3.764 | -0.214 | 2.68% | -2.68%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 5.263 | 8.435 | 4.085 | -0.191 | 2.214% | -2.214%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 5.263 | 8.888 | 4.305 | -0.171 | 1.888% | -1.888%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 5.263 | 9.016 | 4.367 | -0.165 | 1.797% | -1.797%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 5.263 | 5.258 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 5.258 | 9.068 | 4.392 | -0.162 | 1.755% | -1.755%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 5.263 | 5.242 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 5.242 | 9.1 | 4.407 | -0.161 | 1.738% | -1.738%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 5.263 | 5.226 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 5.226 | 9.133 | 4.423 | -0.159 | 1.711% | -1.711%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 5.263 | 5.226 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 5.226 | 9.164 | 4.439 | -0.158 | 1.695% | -1.695%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 5.263 | 5.237 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 5.237 | 9.181 | 4.447 | -0.157 | 1.681% | -1.681%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 5.263 | 5.252 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 5.252 | 9.251 | 4.48 | -0.153 | 1.627% | -1.627%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 5.263 | 5.258 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 5.258 | 9.452 | 4.578 | -0.142 | 1.48% | -1.48%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 5.263 | 9.759 | 4.726 | -0.124 | 1.255% | -1.255%
18 | 10 | 4.843 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 5.263 | 9.883 | 4.787 | -0.117 | 1.17% | -1.17%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 5.263 | 9.847 | 4.769 | -0.119 | 1.194% | -1.194%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 5.263 | 9.731 | 4.713 | -0.126 | 1.278% | -1.278%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 5.263 | 9.479 | 4.591 | -0.141 | 1.466% | -1.466%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 5.263 | 8.972 | 4.345 | -0.167 | 1.827% | -1.827%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 5.263 | 8.353 | 4.045 | -0.194 | 2.27% | -2.27%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 5.263 | 7.835 | 3.794 | -0.212 | 2.635% | -2.635%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 10.526 | 7.494 | 3.629 | -0.222 | 2.877% | -2.877%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 10.526 | 7.29 | 3.531 | -0.227 | 3.02% | -3.02%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 10.526 | 7.177 | 3.476 | -0.23 | 3.105% | -3.105%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 10.526 | 7.168 | 3.472 | -0.23 | 3.109% | -3.109%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 10.526 | 7.337 | 3.553 | -0.226 | 2.988% | -2.988%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 10.526 | 7.772 | 3.764 | -0.214 | 2.68% | -2.68%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 10.526 | 10.505 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 10.505 | 8.435 | 4.085 | -0.191 | 2.214% | -2.214%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 10.526 | 10.231 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 10.231 | 8.888 | 4.305 | -0.171 | 1.888% | -1.888%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 10.526 | 9.41 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 9.41 | 9.016 | 4.367 | -0.165 | 1.797% | -1.797%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 10.526 | 8.284 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 8.284 | 9.068 | 4.392 | -0.162 | 1.755% | -1.755%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 10.526 | 7.147 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 7.147 | 9.1 | 4.407 | -0.161 | 1.738% | -1.738%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 10.526 | 6.516 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 6.516 | 9.133 | 4.423 | -0.159 | 1.711% | -1.711%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 10.526 | 6.705 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 6.705 | 9.164 | 4.439 | -0.158 | 1.695% | -1.695%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 10.526 | 7.01 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 7.01 | 9.181 | 4.447 | -0.157 | 1.681% | -1.681%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 10.526 | 7.884 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 7.884 | 9.251 | 4.48 | -0.153 | 1.627% | -1.627%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 10.526 | 8.916 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 8.916 | 9.452 | 4.578 | -0.142 | 1.48% | -1.48%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 10.526 | 9.842 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 9.842 | 9.759 | 4.726 | -0.124 | 1.255% | -1.255%
18 | 10 | 4.843 | 0.9 | I | very sunny | 10.526 | 10.379 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 10.379 | 9.883 | 4.787 | -0.117 | 1.17% | -1.17%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 10.526 | 10.515 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 10.515 | 9.847 | 4.769 | -0.119 | 1.194% | -1.194%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 10.526 | 9.731 | 4.713 | -0.126 | 1.278% | -1.278%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 10.526 | 9.479 | 4.591 | -0.141 | 1.466% | -1.466%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 10.526 | 8.972 | 4.345 | -0.167 | 1.827% | -1.827%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 10.526 | 8.353 | 4.045 | -0.194 | 2.27% | -2.27%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 10.526 | 7.835 | 3.794 | -0.212 | 2.635% | -2.635%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 10.526 | 7.494 | 3.629 | -0.222 | 2.877% | -2.877%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 10.526 | 7.29 | 3.531 | -0.227 | 3.02% | -3.02%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 10.526 | 7.177 | 3.476 | -0.23 | 3.105% | -3.105%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 10.526 | 7.168 | 3.472 | -0.23 | 3.109% | -3.109%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 10.526 | 7.337 | 3.553 | -0.226 | 2.988% | -2.988%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 10.526 | 7.772 | 3.764 | -0.214 | 2.68% | -2.68%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 10.526 | 8.435 | 4.085 | -0.191 | 2.214% | -2.214%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 10.526 | 10.515 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 10.515 | 8.888 | 4.305 | -0.171 | 1.888% | -1.888%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 10.526 | 10.41 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 10.41 | 9.016 | 4.367 | -0.165 | 1.797% | -1.797%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 10.526 | 10.189 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 10.189 | 9.068 | 4.392 | -0.162 | 1.755% | -1.755%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 10.526 | 9.958 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 9.958 | 9.1 | 4.407 | -0.161 | 1.738% | -1.738%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 10.526 | 9.831 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 9.831 | 9.133 | 4.423 | -0.159 | 1.711% | -1.711%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 10.526 | 9.968 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 9.968 | 9.164 | 4.439 | -0.158 | 1.695% | -1.695%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 10.526 | 10.031 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 10.031 | 9.181 | 4.447 | -0.157 | 1.681% | -1.681%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 10.526 | 10.294 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 10.294 | 9.251 | 4.48 | -0.153 | 1.627% | -1.627%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 10.526 | 10.473 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 10.473 | 9.452 | 4.578 | -0.142 | 1.48% | -1.48%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 10.526 | 9.759 | 4.726 | -0.124 | 1.255% | -1.255%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 10.526 | 9.883 | 4.787 | -0.117 | 1.17% | -1.17%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 10.526 | 9.847 | 4.769 | -0.119 | 1.194% | -1.194%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 10.526 | 9.731 | 4.713 | -0.126 | 1.278% | -1.278%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 10.526 | 9.479 | 4.591 | -0.141 | 1.466% | -1.466%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 10.526 | 8.972 | 4.345 | -0.167 | 1.827% | -1.827%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 10.526 | 8.353 | 4.045 | -0.194 | 2.27% | -2.27%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 10.526 | 7.835 | 3.794 | -0.212 | 2.635% | -2.635%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 10.526 | 7.494 | 3.629 | -0.222 | 2.877% | -2.877%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 10.526 | 7.29 | 3.531 | -0.227 | 3.02% | -3.02%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 10.526 | 7.177 | 3.476 | -0.23 | 3.105% | -3.105%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 10.526 | 7.168 | 3.472 | -0.23 | 3.109% | -3.109%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 10.526 | 7.337 | 3.553 | -0.226 | 2.988% | -2.988%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 10.526 | 7.772 | 3.764 | -0.214 | 2.68% | -2.68%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 10.526 | 8.435 | 4.085 | -0.191 | 2.214% | -2.214%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 10.526 | 8.888 | 4.305 | -0.171 | 1.888% | -1.888%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 10.526 | 9.016 | 4.367 | -0.165 | 1.797% | -1.797%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 10.526 | 10.515 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 10.515 | 9.068 | 4.392 | -0.162 | 1.755% | -1.755%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 10.526 | 10.484 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 10.484 | 9.1 | 4.407 | -0.161 | 1.738% | -1.738%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 10.526 | 10.452 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 10.452 | 9.133 | 4.423 | -0.159 | 1.711% | -1.711%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 10.526 | 10.452 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 10.452 | 9.164 | 4.439 | -0.158 | 1.695% | -1.695%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 10.526 | 10.473 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 10.473 | 9.181 | 4.447 | -0.157 | 1.681% | -1.681%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 10.526 | 10.505 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 10.505 | 9.251 | 4.48 | -0.153 | 1.627% | -1.627%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 10.526 | 10.515 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 10.515 | 9.452 | 4.578 | -0.142 | 1.48% | -1.48%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 10.526 | 9.759 | 4.726 | -0.124 | 1.255% | -1.255%
18 | 10 | 4.843 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 10.526 | 9.883 | 4.787 | -0.117 | 1.17% | -1.17%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 10.526 | 9.847 | 4.769 | -0.119 | 1.194% | -1.194%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 10.526 | 9.731 | 4.713 | -0.126 | 1.278% | -1.278%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 10.526 | 9.479 | 4.591 | -0.141 | 1.466% | -1.466%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 10.526 | 8.972 | 4.345 | -0.167 | 1.827% | -1.827%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 10.526 | 8.353 | 4.045 | -0.194 | 2.27% | -2.27%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 10.526 | 7.835 | 3.794 | -0.212 | 2.635% | -2.635%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.924 | 0.996 | -2.943 | -5.263 | 5.263 | 7.614 | 2.503 | -0.102 | 1.322% | -1.322%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.897 | 0.997 | -2.861 | -5.263 | 5.263 | 7.418 | 2.438 | -0.099 | 1.317% | -1.317%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.882 | 0.997 | -2.816 | -5.263 | 5.263 | 7.309 | 2.402 | -0.098 | 1.323% | -1.323%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.881 | 0.997 | -2.812 | -5.263 | 5.263 | 7.3 | 2.4 | -0.098 | 1.325% | -1.325%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.903 | 0.996 | -2.88 | -5.263 | 5.263 | 7.463 | 2.453 | -0.1 | 1.322% | -1.322%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.96 | 0.994 | -3.054 | -5.263 | 5.263 | 7.881 | 2.59 | -0.105 | 1.315% | -1.315%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 5.263 | 5.252 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.044 | 0.99 | -3.307 | -5.252 | 5.252 | 8.514 | 2.798 | -0.112 | 1.298% | -1.298%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 5.263 | 5.116 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.025 | -1.119 | 0.987 | -3.533 | -5.116 | 5.116 | 8.938 | 2.938 | -0.121 | 1.336% | -1.336%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 5.263 | 4.705 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.026 | -1.146 | 0.988 | -3.592 | -4.705 | 4.705 | 9.068 | 2.981 | -0.113 | 1.231% | -1.231%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 5.263 | 4.142 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.027 | -1.154 | 0.99 | -3.581 | -4.142 | 4.142 | 9.137 | 3.003 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 5.263 | 3.574 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.028 | -1.182 | 0.99 | -3.639 | -3.574 | 3.574 | 9.176 | 3.016 | -0.085 | 0.9178% | -0.9178%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 5.263 | 3.258 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.029 | -1.193 | 0.991 | -3.654 | -3.258 | 3.258 | 9.215 | 3.029 | -0.077 | 0.8287% | -0.8287%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 5.263 | 3.353 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.029 | -1.198 | 0.99 | -3.676 | -3.353 | 3.353 | 9.241 | 3.037 | -0.081 | 0.8689% | -0.8689%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 5.263 | 3.505 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.028 | -1.197 | 0.99 | -3.68 | -3.505 | 3.505 | 9.253 | 3.041 | -0.085 | 0.9103% | -0.9103%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 5.263 | 3.942 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.027 | -1.196 | 0.988 | -3.701 | -3.942 | 3.942 | 9.307 | 3.059 | -0.097 | 1.031% | -1.031%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 5.263 | 4.458 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.025 | -1.21 | 0.986 | -3.773 | -4.458 | 4.458 | 9.482 | 3.117 | -0.112 | 1.167% | -1.167%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 5.263 | 4.921 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.024 | -1.227 | 0.983 | -3.851 | -4.921 | 4.921 | 9.761 | 3.208 | -0.122 | 1.234% | -1.234%
18 | 10 | 3.287 | 0.95 | I | very sunny | 5.263 | 5.189 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.237 | 0.982 | -3.899 | -5.189 | 5.189 | 9.869 | 3.244 | -0.131 | 1.31% | -1.31%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 5.263 | 5.258 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.231 | 0.982 | -3.884 | -5.258 | 5.258 | 9.834 | 3.232 | -0.132 | 1.324% | -1.324%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.216 | 0.983 | -3.838 | -5.263 | 5.263 | 9.726 | 3.197 | -0.131 | 1.329% | -1.329%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.023 | -1.184 | 0.984 | -3.737 | -5.263 | 5.263 | 9.492 | 3.12 | -0.128 | 1.331% | -1.331%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.118 | 0.987 | -3.535 | -5.263 | 5.263 | 9.018 | 2.964 | -0.121 | 1.324% | -1.324%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.037 | 0.991 | -3.287 | -5.263 | 5.263 | 8.434 | 2.772 | -0.113 | 1.322% | -1.322%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.969 | 0.994 | -3.08 | -5.263 | 5.263 | 7.941 | 2.61 | -0.106 | 1.317% | -1.317%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.924 | 0.996 | -2.943 | -5.263 | 5.263 | 7.614 | 2.503 | -0.102 | 1.322% | -1.322%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.897 | 0.997 | -2.861 | -5.263 | 5.263 | 7.418 | 2.438 | -0.099 | 1.317% | -1.317%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.882 | 0.997 | -2.816 | -5.263 | 5.263 | 7.309 | 2.402 | -0.098 | 1.323% | -1.323%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.881 | 0.997 | -2.812 | -5.263 | 5.263 | 7.3 | 2.4 | -0.098 | 1.325% | -1.325%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.903 | 0.996 | -2.88 | -5.263 | 5.263 | 7.463 | 2.453 | -0.1 | 1.322% | -1.322%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.96 | 0.994 | -3.054 | -5.263 | 5.263 | 7.881 | 2.59 | -0.105 | 1.315% | -1.315%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.047 | 0.99 | -3.32 | -5.263 | 5.263 | 8.512 | 2.798 | -0.114 | 1.322% | -1.322%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 5.263 | 5.258 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.024 | -1.107 | 0.987 | -3.501 | -5.258 | 5.258 | 8.939 | 2.938 | -0.12 | 1.325% | -1.325%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 5.263 | 5.205 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.024 | -1.125 | 0.987 | -3.553 | -5.205 | 5.205 | 9.061 | 2.978 | -0.12 | 1.307% | -1.307%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 5.263 | 5.095 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.024 | -1.144 | 0.986 | -3.606 | -5.095 | 5.095 | 9.107 | 2.993 | -0.123 | 1.333% | -1.333%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 5.263 | 4.979 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.025 | -1.151 | 0.986 | -3.622 | -4.979 | 4.979 | 9.141 | 3.004 | -0.12 | 1.296% | -1.296%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 5.263 | 4.916 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.025 | -1.157 | 0.986 | -3.636 | -4.916 | 4.916 | 9.173 | 3.015 | -0.119 | 1.281% | -1.281%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 5.263 | 4.984 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.025 | -1.159 | 0.986 | -3.647 | -4.984 | 4.984 | 9.201 | 3.024 | -0.121 | 1.298% | -1.298%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 5.263 | 5.016 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.024 | -1.161 | 0.986 | -3.654 | -5.016 | 5.016 | 9.216 | 3.029 | -0.122 | 1.306% | -1.306%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 5.263 | 5.147 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.024 | -1.166 | 0.985 | -3.679 | -5.147 | 5.147 | 9.277 | 3.049 | -0.127 | 1.35% | -1.35%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 5.263 | 5.237 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.023 | -1.191 | 0.984 | -3.759 | -5.237 | 5.237 | 9.462 | 3.11 | -0.132 | 1.376% | -1.376%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.023 | -1.22 | 0.982 | -3.849 | -5.263 | 5.263 | 9.752 | 3.205 | -0.131 | 1.326% | -1.326%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.236 | 0.982 | -3.898 | -5.263 | 5.263 | 9.867 | 3.243 | -0.133 | 1.33% | -1.33%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.231 | 0.982 | -3.884 | -5.263 | 5.263 | 9.833 | 3.232 | -0.133 | 1.335% | -1.335%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.216 | 0.983 | -3.838 | -5.263 | 5.263 | 9.726 | 3.197 | -0.131 | 1.329% | -1.329%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.023 | -1.184 | 0.984 | -3.737 | -5.263 | 5.263 | 9.492 | 3.12 | -0.128 | 1.331% | -1.331%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.118 | 0.987 | -3.535 | -5.263 | 5.263 | 9.018 | 2.964 | -0.121 | 1.324% | -1.324%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.037 | 0.991 | -3.287 | -5.263 | 5.263 | 8.434 | 2.772 | -0.113 | 1.322% | -1.322%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.969 | 0.994 | -3.08 | -5.263 | 5.263 | 7.941 | 2.61 | -0.106 | 1.317% | -1.317%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.924 | 0.996 | -2.943 | -5.263 | 5.263 | 7.614 | 2.503 | -0.102 | 1.322% | -1.322%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.897 | 0.997 | -2.861 | -5.263 | 5.263 | 7.418 | 2.438 | -0.099 | 1.317% | -1.317%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.882 | 0.997 | -2.816 | -5.263 | 5.263 | 7.309 | 2.402 | -0.098 | 1.323% | -1.323%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.881 | 0.997 | -2.812 | -5.263 | 5.263 | 7.3 | 2.4 | -0.098 | 1.325% | -1.325%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.903 | 0.996 | -2.88 | -5.263 | 5.263 | 7.463 | 2.453 | -0.1 | 1.322% | -1.322%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.96 | 0.994 | -3.054 | -5.263 | 5.263 | 7.881 | 2.59 | -0.105 | 1.315% | -1.315%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.047 | 0.99 | -3.32 | -5.263 | 5.263 | 8.512 | 2.798 | -0.114 | 1.322% | -1.322%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.024 | -1.107 | 0.987 | -3.501 | -5.263 | 5.263 | 8.939 | 2.938 | -0.12 | 1.325% | -1.325%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.024 | -1.123 | 0.987 | -3.552 | -5.263 | 5.263 | 9.059 | 2.978 | -0.122 | 1.329% | -1.329%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 5.263 | 5.258 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.024 | -1.13 | 0.986 | -3.573 | -5.258 | 5.258 | 9.108 | 2.994 | -0.122 | 1.322% | -1.322%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 5.263 | 5.242 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.024 | -1.135 | 0.986 | -3.586 | -5.242 | 5.242 | 9.139 | 3.004 | -0.122 | 1.317% | -1.317%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 5.263 | 5.226 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.024 | -1.139 | 0.986 | -3.599 | -5.226 | 5.226 | 9.17 | 3.014 | -0.122 | 1.313% | -1.313%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 5.263 | 5.226 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.024 | -1.143 | 0.986 | -3.612 | -5.226 | 5.226 | 9.199 | 3.024 | -0.123 | 1.319% | -1.319%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 5.263 | 5.237 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.024 | -1.155 | 0.985 | -3.65 | -5.237 | 5.237 | 9.21 | 3.027 | -0.128 | 1.371% | -1.371%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 5.263 | 5.252 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.024 | -1.164 | 0.985 | -3.677 | -5.252 | 5.252 | 9.275 | 3.048 | -0.129 | 1.372% | -1.372%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 5.263 | 5.258 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.024 | -1.18 | 0.984 | -3.726 | -5.258 | 5.258 | 9.467 | 3.112 | -0.127 | 1.324% | -1.324%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.023 | -1.22 | 0.982 | -3.849 | -5.263 | 5.263 | 9.752 | 3.205 | -0.131 | 1.326% | -1.326%
18 | 10 | 3.287 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.236 | 0.982 | -3.898 | -5.263 | 5.263 | 9.867 | 3.243 | -0.133 | 1.33% | -1.33%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.231 | 0.982 | -3.884 | -5.263 | 5.263 | 9.833 | 3.232 | -0.133 | 1.335% | -1.335%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.216 | 0.983 | -3.838 | -5.263 | 5.263 | 9.726 | 3.197 | -0.131 | 1.329% | -1.329%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.023 | -1.184 | 0.984 | -3.737 | -5.263 | 5.263 | 9.492 | 3.12 | -0.128 | 1.331% | -1.331%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.118 | 0.987 | -3.535 | -5.263 | 5.263 | 9.018 | 2.964 | -0.121 | 1.324% | -1.324%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.037 | 0.991 | -3.287 | -5.263 | 5.263 | 8.434 | 2.772 | -0.113 | 1.322% | -1.322%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.969 | 0.994 | -3.08 | -5.263 | 5.263 | 7.941 | 2.61 | -0.106 | 1.317% | -1.317%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.799 | 0.981 | -2.855 | -10.526 | 10.526 | 7.505 | 2.467 | -0.211 | 2.735% | -2.735%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.772 | 0.982 | -2.772 | -10.526 | 10.526 | 7.312 | 2.403 | -0.205 | 2.727% | -2.727%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.757 | 0.983 | -2.727 | -10.526 | 10.526 | 7.205 | 2.368 | -0.202 | 2.727% | -2.727%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.756 | 0.983 | -2.723 | -10.526 | 10.526 | 7.196 | 2.365 | -0.202 | 2.73% | -2.73%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.778 | 0.982 | -2.791 | -10.526 | 10.526 | 7.356 | 2.418 | -0.207 | 2.737% | -2.737%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.835 | 0.98 | -2.968 | -10.526 | 10.526 | 7.767 | 2.553 | -0.219 | 2.742% | -2.742%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 10.526 | 10.505 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.923 | 0.976 | -3.238 | -10.505 | 10.505 | 8.389 | 2.757 | -0.237 | 2.748% | -2.748%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 10.526 | 10.231 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.011 | -0.989 | 0.974 | -3.424 | -10.231 | 10.231 | 8.817 | 2.898 | -0.242 | 2.671% | -2.671%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 10.526 | 9.41 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.018 | -1.073 | 0.98 | -3.535 | -7.644 | 9.41 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 10.526 | 8.284 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.018 | -1.08 | 0.98 | -3.556 | -7.644 | 8.284 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 10.526 | 7.147 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.019 | -1.095 | 0.981 | -3.573 | -7.147 | 7.147 | 9.089 | 2.987 | -0.172 | 1.857% | -1.857%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 10.526 | 6.516 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.021 | -1.112 | 0.982 | -3.59 | -6.516 | 6.516 | 9.136 | 3.003 | -0.156 | 1.679% | -1.679%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 10.526 | 6.705 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.02 | -1.117 | 0.982 | -3.617 | -6.705 | 6.705 | 9.158 | 3.01 | -0.164 | 1.759% | -1.759%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 10.526 | 7.01 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.019 | -1.112 | 0.981 | -3.618 | -7.01 | 7.01 | 9.166 | 3.013 | -0.172 | 1.842% | -1.842%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 10.526 | 7.884 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.104 | 0.979 | -3.63 | -7.642 | 7.884 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 10.526 | 8.916 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.13 | 0.977 | -3.711 | -7.64 | 8.916 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 10.526 | 9.842 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.17 | 0.976 | -3.835 | -7.637 | 9.842 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | very sunny | 10.526 | 10.379 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.187 | 0.975 | -3.885 | -7.636 | 10.379 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 10.526 | 10.515 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.182 | 0.975 | -3.871 | -7.636 | 10.515 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.167 | 0.976 | -3.824 | -7.637 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.134 | 0.977 | -3.722 | -7.64 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.993 | 0.973 | -3.455 | -10.526 | 10.526 | 8.887 | 2.921 | -0.252 | 2.757% | -2.757%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.912 | 0.976 | -3.204 | -10.526 | 10.526 | 8.312 | 2.732 | -0.235 | 2.75% | -2.75%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.2 | 1.012 | -0.844 | 0.979 | -2.994 | -10.526 | 10.526 | 7.826 | 2.572 | -0.221 | 2.746% | -2.746%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.799 | 0.981 | -2.855 | -10.526 | 10.526 | 7.505 | 2.467 | -0.211 | 2.735% | -2.735%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.772 | 0.982 | -2.772 | -10.526 | 10.526 | 7.312 | 2.403 | -0.205 | 2.727% | -2.727%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.757 | 0.983 | -2.727 | -10.526 | 10.526 | 7.205 | 2.368 | -0.202 | 2.727% | -2.727%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.756 | 0.983 | -2.723 | -10.526 | 10.526 | 7.196 | 2.365 | -0.202 | 2.73% | -2.73%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.778 | 0.982 | -2.791 | -10.526 | 10.526 | 7.356 | 2.418 | -0.207 | 2.737% | -2.737%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.835 | 0.98 | -2.968 | -10.526 | 10.526 | 7.767 | 2.553 | -0.219 | 2.742% | -2.742%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.923 | 0.976 | -3.238 | -10.526 | 10.526 | 8.389 | 2.757 | -0.237 | 2.748% | -2.748%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 10.526 | 10.515 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.01 | -0.982 | 0.973 | -3.421 | -10.515 | 10.515 | 8.809 | 2.895 | -0.25 | 2.76% | -2.76%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 10.526 | 10.41 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.018 | -1.073 | 0.98 | -3.535 | -7.644 | 10.41 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 10.526 | 10.189 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.018 | -1.08 | 0.98 | -3.556 | -7.644 | 10.189 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 10.526 | 9.958 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.018 | -1.084 | 0.979 | -3.569 | -7.643 | 9.958 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 10.526 | 9.831 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.018 | -1.089 | 0.979 | -3.582 | -7.643 | 9.831 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 10.526 | 9.968 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.018 | -1.093 | 0.979 | -3.595 | -7.643 | 9.968 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 10.526 | 10.031 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.018 | -1.095 | 0.979 | -3.602 | -7.643 | 10.031 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 10.526 | 10.294 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.104 | 0.979 | -3.63 | -7.642 | 10.294 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 10.526 | 10.473 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.13 | 0.977 | -3.711 | -7.64 | 10.473 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.17 | 0.976 | -3.835 | -7.637 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.187 | 0.975 | -3.885 | -7.636 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.182 | 0.975 | -3.871 | -7.636 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.167 | 0.976 | -3.824 | -7.637 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.134 | 0.977 | -3.722 | -7.64 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.993 | 0.973 | -3.455 | -10.526 | 10.526 | 8.887 | 2.921 | -0.252 | 2.757% | -2.757%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.912 | 0.976 | -3.204 | -10.526 | 10.526 | 8.312 | 2.732 | -0.235 | 2.75% | -2.75%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.2 | 1.012 | -0.844 | 0.979 | -2.994 | -10.526 | 10.526 | 7.826 | 2.572 | -0.221 | 2.746% | -2.746%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.799 | 0.981 | -2.855 | -10.526 | 10.526 | 7.505 | 2.467 | -0.211 | 2.735% | -2.735%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.772 | 0.982 | -2.772 | -10.526 | 10.526 | 7.312 | 2.403 | -0.205 | 2.727% | -2.727%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.757 | 0.983 | -2.727 | -10.526 | 10.526 | 7.205 | 2.368 | -0.202 | 2.727% | -2.727%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.756 | 0.983 | -2.723 | -10.526 | 10.526 | 7.196 | 2.365 | -0.202 | 2.73% | -2.73%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.778 | 0.982 | -2.791 | -10.526 | 10.526 | 7.356 | 2.418 | -0.207 | 2.737% | -2.737%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.835 | 0.98 | -2.968 | -10.526 | 10.526 | 7.767 | 2.553 | -0.219 | 2.742% | -2.742%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.923 | 0.976 | -3.238 | -10.526 | 10.526 | 8.389 | 2.757 | -0.237 | 2.748% | -2.748%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.01 | -0.982 | 0.973 | -3.421 | -10.526 | 10.526 | 8.809 | 2.895 | -0.25 | 2.76% | -2.76%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.018 | -1.073 | 0.98 | -3.535 | -7.644 | 10.526 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 10.526 | 10.515 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.018 | -1.08 | 0.98 | -3.556 | -7.644 | 10.515 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 10.526 | 10.484 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.018 | -1.084 | 0.979 | -3.569 | -7.643 | 10.484 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 10.526 | 10.452 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.018 | -1.089 | 0.979 | -3.582 | -7.643 | 10.452 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 10.526 | 10.452 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.018 | -1.093 | 0.979 | -3.595 | -7.643 | 10.452 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 10.526 | 10.473 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.018 | -1.095 | 0.979 | -3.602 | -7.643 | 10.473 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 10.526 | 10.505 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.104 | 0.979 | -3.63 | -7.642 | 10.505 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 10.526 | 10.515 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.13 | 0.977 | -3.711 | -7.64 | 10.515 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.17 | 0.976 | -3.835 | -7.637 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.187 | 0.975 | -3.885 | -7.636 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.182 | 0.975 | -3.871 | -7.636 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.167 | 0.976 | -3.824 | -7.637 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.134 | 0.977 | -3.722 | -7.64 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.993 | 0.973 | -3.455 | -10.526 | 10.526 | 8.887 | 2.921 | -0.252 | 2.757% | -2.757%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.912 | 0.976 | -3.204 | -10.526 | 10.526 | 8.312 | 2.732 | -0.235 | 2.75% | -2.75%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.2 | 1.012 | -0.844 | 0.979 | -2.994 | -10.526 | 10.526 | 7.826 | 2.572 | -0.221 | 2.746% | -2.746%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.996 | -1.592 | 0.981 | -2.637 | -5.263 | 5.263 | 7.5 | 2.465 | -0.216 | 2.799% | -2.799%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.997 | -1.538 | 0.982 | -2.555 | -5.263 | 5.263 | 7.307 | 2.402 | -0.21 | 2.794% | -2.794%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.997 | -1.509 | 0.982 | -2.51 | -5.263 | 5.263 | 7.2 | 2.366 | -0.207 | 2.795% | -2.795%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.997 | -1.507 | 0.982 | -2.506 | -5.263 | 5.263 | 7.191 | 2.364 | -0.207 | 2.798% | -2.798%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.551 | 0.981 | -2.574 | -5.263 | 5.263 | 7.351 | 2.416 | -0.212 | 2.803% | -2.803%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.995 | -1.664 | 0.979 | -2.749 | -5.263 | 5.263 | 7.762 | 2.551 | -0.224 | 2.805% | -2.805%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 5.263 | 5.252 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.993 | -1.837 | 0.975 | -3.016 | -5.252 | 5.252 | 8.383 | 2.755 | -0.243 | 2.817% | -2.817%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 5.263 | 5.116 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.992 | -1.964 | 0.973 | -3.206 | -5.116 | 5.116 | 8.81 | 2.896 | -0.249 | 2.749% | -2.749%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 5.263 | 4.705 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 4.705 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 5.263 | 4.142 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 4.142 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 5.263 | 3.574 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.999 | -2.158 | 0.98 | -3.422 | -3.574 | 3.574 | 9.084 | 2.986 | -0.177 | 1.911% | -1.911%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 5.263 | 3.258 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 1.001 | -2.19 | 0.982 | -3.453 | -3.258 | 3.258 | 9.131 | 3.001 | -0.161 | 1.733% | -1.733%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 5.263 | 3.353 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 1 | -2.199 | 0.981 | -3.472 | -3.353 | 3.353 | 9.154 | 3.009 | -0.168 | 1.802% | -1.802%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 5.263 | 3.505 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.999 | -2.19 | 0.98 | -3.467 | -3.505 | 3.505 | 9.162 | 3.011 | -0.176 | 1.885% | -1.885%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 5.263 | 3.942 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 3.942 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 5.263 | 4.458 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 4.458 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 5.263 | 4.921 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 4.921 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | very sunny | 5.263 | 5.189 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 5.189 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 5.263 | 5.258 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 5.258 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 5.263 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 5.263 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.99 | -1.975 | 0.972 | -3.231 | -5.263 | 5.263 | 8.88 | 2.919 | -0.259 | 2.834% | -2.834%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.993 | -1.815 | 0.975 | -2.983 | -5.263 | 5.263 | 8.306 | 2.73 | -0.241 | 2.82% | -2.82%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.995 | -1.68 | 0.979 | -2.774 | -5.263 | 5.263 | 7.821 | 2.571 | -0.226 | 2.808% | -2.808%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.996 | -1.592 | 0.981 | -2.637 | -5.263 | 5.263 | 7.5 | 2.465 | -0.216 | 2.799% | -2.799%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.997 | -1.538 | 0.982 | -2.555 | -5.263 | 5.263 | 7.307 | 2.402 | -0.21 | 2.794% | -2.794%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.997 | -1.509 | 0.982 | -2.51 | -5.263 | 5.263 | 7.2 | 2.366 | -0.207 | 2.795% | -2.795%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.997 | -1.507 | 0.982 | -2.506 | -5.263 | 5.263 | 7.191 | 2.364 | -0.207 | 2.798% | -2.798%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.551 | 0.981 | -2.574 | -5.263 | 5.263 | 7.351 | 2.416 | -0.212 | 2.803% | -2.803%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.995 | -1.664 | 0.979 | -2.749 | -5.263 | 5.263 | 7.762 | 2.551 | -0.224 | 2.805% | -2.805%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.992 | -1.836 | 0.975 | -3.016 | -5.263 | 5.263 | 8.382 | 2.755 | -0.244 | 2.829% | -2.829%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 5.263 | 5.258 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.991 | -1.954 | 0.972 | -3.198 | -5.258 | 5.258 | 8.802 | 2.893 | -0.257 | 2.837% | -2.837%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 5.263 | 5.205 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 5.205 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 5.263 | 5.095 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 5.095 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 5.263 | 4.979 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 4.979 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 5.263 | 4.916 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 4.916 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 5.263 | 4.984 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 4.984 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 5.263 | 5.016 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 5.016 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 5.263 | 5.147 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 5.147 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 5.263 | 5.237 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 5.237 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 5.263 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 5.263 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 5.263 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 5.263 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 5.263 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.99 | -1.975 | 0.972 | -3.231 | -5.263 | 5.263 | 8.88 | 2.919 | -0.259 | 2.834% | -2.834%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.993 | -1.815 | 0.975 | -2.983 | -5.263 | 5.263 | 8.306 | 2.73 | -0.241 | 2.82% | -2.82%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.995 | -1.68 | 0.979 | -2.774 | -5.263 | 5.263 | 7.821 | 2.571 | -0.226 | 2.808% | -2.808%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.996 | -1.592 | 0.981 | -2.637 | -5.263 | 5.263 | 7.5 | 2.465 | -0.216 | 2.799% | -2.799%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.997 | -1.538 | 0.982 | -2.555 | -5.263 | 5.263 | 7.307 | 2.402 | -0.21 | 2.794% | -2.794%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.997 | -1.509 | 0.982 | -2.51 | -5.263 | 5.263 | 7.2 | 2.366 | -0.207 | 2.795% | -2.795%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.997 | -1.507 | 0.982 | -2.506 | -5.263 | 5.263 | 7.191 | 2.364 | -0.207 | 2.798% | -2.798%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.551 | 0.981 | -2.574 | -5.263 | 5.263 | 7.351 | 2.416 | -0.212 | 2.803% | -2.803%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.995 | -1.664 | 0.979 | -2.749 | -5.263 | 5.263 | 7.762 | 2.551 | -0.224 | 2.805% | -2.805%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.992 | -1.836 | 0.975 | -3.016 | -5.263 | 5.263 | 8.382 | 2.755 | -0.244 | 2.829% | -2.829%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.991 | -1.953 | 0.972 | -3.198 | -5.263 | 5.263 | 8.802 | 2.893 | -0.257 | 2.837% | -2.837%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 5.263 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 5.263 | 5.258 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 5.258 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 5.263 | 5.242 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 5.242 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 5.263 | 5.226 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 5.226 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 5.263 | 5.226 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 5.226 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 5.263 | 5.237 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 5.237 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 5.263 | 5.252 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 5.252 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 5.263 | 5.258 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 5.258 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 5.263 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 5.263 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 5.263 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 5.263 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 5.263 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.99 | -1.975 | 0.972 | -3.231 | -5.263 | 5.263 | 8.88 | 2.919 | -0.259 | 2.834% | -2.834%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.993 | -1.815 | 0.975 | -2.983 | -5.263 | 5.263 | 8.306 | 2.73 | -0.241 | 2.82% | -2.82%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.995 | -1.68 | 0.979 | -2.774 | -5.263 | 5.263 | 7.821 | 2.571 | -0.226 | 2.808% | -2.808%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.569 | 0.979 | -2.619 | -5.555 | 10.526 | 7.487 | 2.461 | -0.229 | 2.968% | -2.968%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.358 | 0.97 | -2.388 | -7.333 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.328 | 0.971 | -2.343 | -7.335 | 10.526 | 7.114 | 2.338 | -0.293 | 3.956% | -3.956%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.326 | 0.971 | -2.339 | -7.335 | 10.526 | 7.105 | 2.335 | -0.293 | 3.961% | -3.961%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.995 | -1.528 | 0.98 | -2.555 | -5.557 | 10.526 | 7.338 | 2.412 | -0.225 | 2.975% | -2.975%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.642 | 0.977 | -2.731 | -5.551 | 10.526 | 7.748 | 2.547 | -0.238 | 2.98% | -2.98%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 10.526 | 10.505 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.815 | 0.973 | -2.999 | -5.542 | 10.505 | 8.368 | 2.75 | -0.258 | 2.991% | -2.991%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 10.526 | 10.231 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.933 | 0.971 | -3.181 | -5.535 | 10.231 | 8.787 | 2.888 | -0.272 | 3.003% | -3.003%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 10.526 | 9.41 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 9.41 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 10.526 | 8.284 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 8.284 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 10.526 | 7.147 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 7.147 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 10.526 | 6.516 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 6.516 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 10.526 | 6.705 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 6.705 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 10.526 | 7.01 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 7.01 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 10.526 | 7.884 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 7.884 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 10.526 | 8.916 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 8.916 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 10.526 | 9.842 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 9.842 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | very sunny | 10.526 | 10.379 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 10.379 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 10.526 | 10.515 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 10.515 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.955 | 0.97 | -3.215 | -5.534 | 10.526 | 8.865 | 2.914 | -0.274 | 2.998% | -2.998%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.794 | 0.974 | -2.966 | -5.543 | 10.526 | 8.292 | 2.725 | -0.255 | 2.984% | -2.984%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.658 | 0.977 | -2.756 | -5.55 | 10.526 | 7.807 | 2.566 | -0.24 | 2.982% | -2.982%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.569 | 0.979 | -2.619 | -5.555 | 10.526 | 7.487 | 2.461 | -0.229 | 2.968% | -2.968%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.358 | 0.97 | -2.388 | -7.333 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.328 | 0.971 | -2.343 | -7.335 | 10.526 | 7.114 | 2.338 | -0.293 | 3.956% | -3.956%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.326 | 0.971 | -2.339 | -7.335 | 10.526 | 7.105 | 2.335 | -0.293 | 3.961% | -3.961%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.995 | -1.528 | 0.98 | -2.555 | -5.557 | 10.526 | 7.338 | 2.412 | -0.225 | 2.975% | -2.975%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.642 | 0.977 | -2.731 | -5.551 | 10.526 | 7.748 | 2.547 | -0.238 | 2.98% | -2.98%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.815 | 0.973 | -2.999 | -5.542 | 10.526 | 8.368 | 2.75 | -0.258 | 2.991% | -2.991%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 10.526 | 10.515 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.933 | 0.971 | -3.181 | -5.535 | 10.515 | 8.787 | 2.888 | -0.272 | 3.003% | -3.003%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 10.526 | 10.41 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 10.41 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 10.526 | 10.189 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 10.189 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 10.526 | 9.958 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 9.958 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 10.526 | 9.831 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 9.831 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 10.526 | 9.968 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 9.968 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 10.526 | 10.031 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 10.031 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 10.526 | 10.294 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 10.294 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 10.526 | 10.473 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 10.473 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.955 | 0.97 | -3.215 | -5.534 | 10.526 | 8.865 | 2.914 | -0.274 | 2.998% | -2.998%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.794 | 0.974 | -2.966 | -5.543 | 10.526 | 8.292 | 2.725 | -0.255 | 2.984% | -2.984%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.658 | 0.977 | -2.756 | -5.55 | 10.526 | 7.807 | 2.566 | -0.24 | 2.982% | -2.982%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.569 | 0.979 | -2.619 | -5.555 | 10.526 | 7.487 | 2.461 | -0.229 | 2.968% | -2.968%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.358 | 0.97 | -2.388 | -7.333 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.328 | 0.971 | -2.343 | -7.335 | 10.526 | 7.114 | 2.338 | -0.293 | 3.956% | -3.956%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.326 | 0.971 | -2.339 | -7.335 | 10.526 | 7.105 | 2.335 | -0.293 | 3.961% | -3.961%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.995 | -1.528 | 0.98 | -2.555 | -5.557 | 10.526 | 7.338 | 2.412 | -0.225 | 2.975% | -2.975%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.642 | 0.977 | -2.731 | -5.551 | 10.526 | 7.748 | 2.547 | -0.238 | 2.98% | -2.98%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.815 | 0.973 | -2.999 | -5.542 | 10.526 | 8.368 | 2.75 | -0.258 | 2.991% | -2.991%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.933 | 0.971 | -3.181 | -5.535 | 10.526 | 8.787 | 2.888 | -0.272 | 3.003% | -3.003%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 10.526 | 8.997 | 2.957 | -0.184 | 2.004% | -2.004%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 10.526 | 10.515 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 10.515 | 9.045 | 2.973 | -0.185 | 2.004% | -2.004%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 10.526 | 10.484 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 10.484 | 9.076 | 2.983 | -0.185 | 1.998% | -1.998%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 10.526 | 10.452 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 10.452 | 9.106 | 2.993 | -0.186 | 2.002% | -2.002%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 10.526 | 10.452 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 10.452 | 9.135 | 3.003 | -0.187 | 2.006% | -2.006%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 10.526 | 10.473 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 10.473 | 9.151 | 3.008 | -0.187 | 2.003% | -2.003%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 10.526 | 10.505 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 10.505 | 9.216 | 3.029 | -0.188 | 1.999% | -1.999%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 10.526 | 10.515 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 10.515 | 9.402 | 3.09 | -0.192 | 2.001% | -2.001%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014% | -2.014%
18 | 10 | 3.287 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01% | -2.01%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007% | -2.007%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009% | -2.009%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006% | -2.006%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.955 | 0.97 | -3.215 | -5.534 | 10.526 | 8.865 | 2.914 | -0.274 | 2.998% | -2.998%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.794 | 0.974 | -2.966 | -5.543 | 10.526 | 8.292 | 2.725 | -0.255 | 2.984% | -2.984%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.658 | 0.977 | -2.756 | -5.55 | 10.526 | 7.807 | 2.566 | -0.24 | 2.982% | -2.982%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 5.263 | 7.419 | 2.438 | -0.297 | 3.849% | -3.849%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 5.263 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 5.263 | 7.109 | 2.337 | -0.298 | 4.023% | -4.023%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 5.263 | 7.1 | 2.334 | -0.298 | 4.028% | -4.028%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 5.263 | 7.265 | 2.388 | -0.298 | 3.94% | -3.94%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 5.263 | 7.691 | 2.528 | -0.295 | 3.694% | -3.694%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 5.263 | 5.252 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 5.252 | 8.339 | 2.741 | -0.287 | 3.327% | -3.327%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 5.263 | 5.116 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 5.116 | 8.781 | 2.886 | -0.278 | 3.069% | -3.069%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 5.263 | 4.705 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 4.705 | 8.906 | 2.927 | -0.275 | 2.995% | -2.995%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 5.263 | 4.142 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 4.142 | 8.956 | 2.944 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 5.263 | 3.574 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.574 | 3.574 | 8.988 | 2.954 | -0.273 | 2.948% | -2.948%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 5.263 | 3.258 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.973 | -3.222 | 0.973 | -3.222 | -3.258 | 3.258 | 9.044 | 2.973 | -0.248 | 2.669% | -2.669%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 5.263 | 3.353 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.972 | -3.224 | 0.972 | -3.224 | -3.353 | 3.353 | 9.065 | 2.98 | -0.257 | 2.757% | -2.757%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 5.263 | 3.505 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.505 | 3.505 | 9.067 | 2.98 | -0.271 | 2.902% | -2.902%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 5.263 | 3.942 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 3.942 | 9.135 | 3.002 | -0.269 | 2.86% | -2.86%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 5.263 | 4.458 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 4.458 | 9.33 | 3.067 | -0.264 | 2.752% | -2.752%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 5.263 | 4.921 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 4.921 | 9.629 | 3.165 | -0.254 | 2.57% | -2.57%
18 | 10 | 3.287 | 0.95 | I | very sunny | 5.263 | 5.189 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 5.189 | 9.75 | 3.205 | -0.25 | 2.5% | -2.5%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 5.263 | 5.258 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 5.258 | 9.714 | 3.193 | -0.252 | 2.529% | -2.529%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 5.263 | 9.602 | 3.156 | -0.255 | 2.587% | -2.587%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 5.263 | 9.357 | 3.075 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 5.263 | 8.863 | 2.913 | -0.276 | 3.02% | -3.02%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 5.263 | 8.259 | 2.715 | -0.288 | 3.37% | -3.37%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 5.263 | 7.752 | 2.548 | -0.295 | 3.666% | -3.666%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 5.263 | 7.419 | 2.438 | -0.297 | 3.849% | -3.849%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 5.263 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 5.263 | 7.109 | 2.337 | -0.298 | 4.023% | -4.023%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 5.263 | 7.1 | 2.334 | -0.298 | 4.028% | -4.028%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 5.263 | 7.265 | 2.388 | -0.298 | 3.94% | -3.94%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 5.263 | 7.691 | 2.528 | -0.295 | 3.694% | -3.694%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 5.263 | 8.339 | 2.741 | -0.287 | 3.327% | -3.327%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 5.263 | 5.258 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 5.258 | 8.781 | 2.886 | -0.278 | 3.069% | -3.069%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 5.263 | 5.205 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 5.205 | 8.906 | 2.927 | -0.275 | 2.995% | -2.995%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 5.263 | 5.095 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 5.095 | 8.956 | 2.944 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 5.263 | 4.979 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 4.979 | 8.988 | 2.954 | -0.273 | 2.948% | -2.948%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 5.263 | 4.916 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 4.916 | 9.02 | 2.965 | -0.272 | 2.927% | -2.927%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 5.263 | 4.984 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 4.984 | 9.05 | 2.975 | -0.272 | 2.918% | -2.918%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 5.263 | 5.016 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 5.016 | 9.067 | 2.98 | -0.271 | 2.902% | -2.902%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 5.263 | 5.147 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 5.147 | 9.135 | 3.002 | -0.269 | 2.86% | -2.86%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 5.263 | 5.237 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 5.237 | 9.33 | 3.067 | -0.264 | 2.752% | -2.752%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 5.263 | 9.629 | 3.165 | -0.254 | 2.57% | -2.57%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 5.263 | 9.75 | 3.205 | -0.25 | 2.5% | -2.5%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 5.263 | 9.714 | 3.193 | -0.252 | 2.529% | -2.529%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 5.263 | 9.602 | 3.156 | -0.255 | 2.587% | -2.587%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 5.263 | 9.357 | 3.075 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 5.263 | 8.863 | 2.913 | -0.276 | 3.02% | -3.02%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 5.263 | 8.259 | 2.715 | -0.288 | 3.37% | -3.37%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 5.263 | 7.752 | 2.548 | -0.295 | 3.666% | -3.666%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 5.263 | 7.419 | 2.438 | -0.297 | 3.849% | -3.849%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 5.263 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 5.263 | 7.109 | 2.337 | -0.298 | 4.023% | -4.023%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 5.263 | 7.1 | 2.334 | -0.298 | 4.028% | -4.028%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 5.263 | 7.265 | 2.388 | -0.298 | 3.94% | -3.94%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 5.263 | 7.691 | 2.528 | -0.295 | 3.694% | -3.694%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 5.263 | 8.339 | 2.741 | -0.287 | 3.327% | -3.327%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 5.263 | 8.781 | 2.886 | -0.278 | 3.069% | -3.069%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 5.263 | 8.906 | 2.927 | -0.275 | 2.995% | -2.995%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 5.263 | 5.258 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 5.258 | 8.956 | 2.944 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 5.263 | 5.242 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 5.242 | 8.988 | 2.954 | -0.273 | 2.948% | -2.948%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 5.263 | 5.226 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 5.226 | 9.02 | 2.965 | -0.272 | 2.927% | -2.927%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 5.263 | 5.226 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 5.226 | 9.05 | 2.975 | -0.272 | 2.918% | -2.918%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 5.263 | 5.237 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 5.237 | 9.067 | 2.98 | -0.271 | 2.902% | -2.902%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 5.263 | 5.252 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 5.252 | 9.135 | 3.002 | -0.269 | 2.86% | -2.86%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 5.263 | 5.258 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 5.258 | 9.33 | 3.067 | -0.264 | 2.752% | -2.752%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 5.263 | 9.629 | 3.165 | -0.254 | 2.57% | -2.57%
18 | 10 | 3.287 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 5.263 | 9.75 | 3.205 | -0.25 | 2.5% | -2.5%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 5.263 | 9.714 | 3.193 | -0.252 | 2.529% | -2.529%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 5.263 | 9.602 | 3.156 | -0.255 | 2.587% | -2.587%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 5.263 | 9.357 | 3.075 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 5.263 | 8.863 | 2.913 | -0.276 | 3.02% | -3.02%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 5.263 | 8.259 | 2.715 | -0.288 | 3.37% | -3.37%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 5.263 | 7.752 | 2.548 | -0.295 | 3.666% | -3.666%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 10.526 | 7.419 | 2.438 | -0.297 | 3.849% | -3.849%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 10.526 | 7.109 | 2.337 | -0.298 | 4.023% | -4.023%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 10.526 | 7.1 | 2.334 | -0.298 | 4.028% | -4.028%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 10.526 | 7.265 | 2.388 | -0.298 | 3.94% | -3.94%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 10.526 | 7.691 | 2.528 | -0.295 | 3.694% | -3.694%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 10.526 | 10.505 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 10.505 | 8.339 | 2.741 | -0.287 | 3.327% | -3.327%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 10.526 | 10.231 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 10.231 | 8.781 | 2.886 | -0.278 | 3.069% | -3.069%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 10.526 | 9.41 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 9.41 | 8.906 | 2.927 | -0.275 | 2.995% | -2.995%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 10.526 | 8.284 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 8.284 | 8.956 | 2.944 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 10.526 | 7.147 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 7.147 | 8.988 | 2.954 | -0.273 | 2.948% | -2.948%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 10.526 | 6.516 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 6.516 | 9.02 | 2.965 | -0.272 | 2.927% | -2.927%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 10.526 | 6.705 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 6.705 | 9.05 | 2.975 | -0.272 | 2.918% | -2.918%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 10.526 | 7.01 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 7.01 | 9.067 | 2.98 | -0.271 | 2.902% | -2.902%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 10.526 | 7.884 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 7.884 | 9.135 | 3.002 | -0.269 | 2.86% | -2.86%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 10.526 | 8.916 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 8.916 | 9.33 | 3.067 | -0.264 | 2.752% | -2.752%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 10.526 | 9.842 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 9.842 | 9.629 | 3.165 | -0.254 | 2.57% | -2.57%
18 | 10 | 3.287 | 0.95 | I | very sunny | 10.526 | 10.379 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 10.379 | 9.75 | 3.205 | -0.25 | 2.5% | -2.5%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 10.526 | 10.515 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 10.515 | 9.714 | 3.193 | -0.252 | 2.529% | -2.529%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 10.526 | 9.602 | 3.156 | -0.255 | 2.587% | -2.587%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 10.526 | 9.357 | 3.075 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 10.526 | 8.863 | 2.913 | -0.276 | 3.02% | -3.02%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 10.526 | 8.259 | 2.715 | -0.288 | 3.37% | -3.37%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 10.526 | 7.752 | 2.548 | -0.295 | 3.666% | -3.666%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 10.526 | 7.419 | 2.438 | -0.297 | 3.849% | -3.849%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 10.526 | 7.109 | 2.337 | -0.298 | 4.023% | -4.023%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 10.526 | 7.1 | 2.334 | -0.298 | 4.028% | -4.028%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 10.526 | 7.265 | 2.388 | -0.298 | 3.94% | -3.94%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 10.526 | 7.691 | 2.528 | -0.295 | 3.694% | -3.694%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 10.526 | 8.339 | 2.741 | -0.287 | 3.327% | -3.327%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 10.526 | 10.515 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 10.515 | 8.781 | 2.886 | -0.278 | 3.069% | -3.069%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 10.526 | 10.41 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 10.41 | 8.906 | 2.927 | -0.275 | 2.995% | -2.995%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 10.526 | 10.189 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 10.189 | 8.956 | 2.944 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 10.526 | 9.958 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 9.958 | 8.988 | 2.954 | -0.273 | 2.948% | -2.948%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 10.526 | 9.831 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 9.831 | 9.02 | 2.965 | -0.272 | 2.927% | -2.927%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 10.526 | 9.968 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 9.968 | 9.05 | 2.975 | -0.272 | 2.918% | -2.918%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 10.526 | 10.031 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 10.031 | 9.067 | 2.98 | -0.271 | 2.902% | -2.902%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 10.526 | 10.294 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 10.294 | 9.135 | 3.002 | -0.269 | 2.86% | -2.86%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 10.526 | 10.473 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 10.473 | 9.33 | 3.067 | -0.264 | 2.752% | -2.752%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 10.526 | 9.629 | 3.165 | -0.254 | 2.57% | -2.57%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 10.526 | 9.75 | 3.205 | -0.25 | 2.5% | -2.5%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 10.526 | 9.714 | 3.193 | -0.252 | 2.529% | -2.529%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 10.526 | 9.602 | 3.156 | -0.255 | 2.587% | -2.587%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 10.526 | 9.357 | 3.075 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 10.526 | 8.863 | 2.913 | -0.276 | 3.02% | -3.02%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 10.526 | 8.259 | 2.715 | -0.288 | 3.37% | -3.37%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 10.526 | 7.752 | 2.548 | -0.295 | 3.666% | -3.666%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 10.526 | 7.419 | 2.438 | -0.297 | 3.849% | -3.849%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964% | -3.964%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 10.526 | 7.109 | 2.337 | -0.298 | 4.023% | -4.023%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 10.526 | 7.1 | 2.334 | -0.298 | 4.028% | -4.028%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 10.526 | 7.265 | 2.388 | -0.298 | 3.94% | -3.94%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 10.526 | 7.691 | 2.528 | -0.295 | 3.694% | -3.694%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 10.526 | 8.339 | 2.741 | -0.287 | 3.327% | -3.327%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 10.526 | 8.781 | 2.886 | -0.278 | 3.069% | -3.069%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 10.526 | 8.906 | 2.927 | -0.275 | 2.995% | -2.995%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 10.526 | 10.515 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 10.515 | 8.956 | 2.944 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 10.526 | 10.484 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 10.484 | 8.988 | 2.954 | -0.273 | 2.948% | -2.948%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 10.526 | 10.452 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 10.452 | 9.02 | 2.965 | -0.272 | 2.927% | -2.927%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 10.526 | 10.452 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 10.452 | 9.05 | 2.975 | -0.272 | 2.918% | -2.918%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 10.526 | 10.473 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 10.473 | 9.067 | 2.98 | -0.271 | 2.902% | -2.902%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 10.526 | 10.505 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 10.505 | 9.135 | 3.002 | -0.269 | 2.86% | -2.86%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 10.526 | 10.515 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 10.515 | 9.33 | 3.067 | -0.264 | 2.752% | -2.752%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 10.526 | 9.629 | 3.165 | -0.254 | 2.57% | -2.57%
18 | 10 | 3.287 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 10.526 | 9.75 | 3.205 | -0.25 | 2.5% | -2.5%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 10.526 | 9.714 | 3.193 | -0.252 | 2.529% | -2.529%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 10.526 | 9.602 | 3.156 | -0.255 | 2.587% | -2.587%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 10.526 | 9.357 | 3.075 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 10.526 | 8.863 | 2.913 | -0.276 | 3.02% | -3.02%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 10.526 | 8.259 | 2.715 | -0.288 | 3.37% | -3.37%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 10.526 | 7.752 | 2.548 | -0.295 | 3.666% | -3.666%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.943 | 1.003 | -3.059 | -5.263 | 5.263 | 7.615 | 1.546 | -0.101 | 1.309% | -1.309%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.029 | -0.916 | 1.004 | -2.975 | -5.263 | 5.263 | 7.418 | 1.506 | -0.099 | 1.317% | -1.317%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.901 | 1.005 | -2.928 | -5.263 | 5.263 | 7.31 | 1.484 | -0.097 | 1.31% | -1.31%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.9 | 1.005 | -2.924 | -5.263 | 5.263 | 7.301 | 1.483 | -0.097 | 1.311% | -1.311%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.922 | 1.004 | -2.994 | -5.263 | 5.263 | 7.464 | 1.516 | -0.099 | 1.309% | -1.309%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.981 | 1.002 | -3.174 | -5.263 | 5.263 | 7.881 | 1.6 | -0.105 | 1.315% | -1.315%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 5.263 | 5.252 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.065 | 0.999 | -3.434 | -5.252 | 5.252 | 8.515 | 1.729 | -0.111 | 1.287% | -1.287%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 5.263 | 5.116 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.142 | 0.997 | -3.665 | -5.116 | 5.116 | 8.94 | 1.815 | -0.119 | 1.314% | -1.314%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 5.263 | 4.705 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.029 | -1.169 | 0.997 | -3.725 | -4.705 | 4.705 | 9.07 | 1.842 | -0.111 | 1.209% | -1.209%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 5.263 | 4.142 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.03 | -1.176 | 0.999 | -3.714 | -4.142 | 4.142 | 9.137 | 1.855 | -0.093 | 1.008% | -1.008%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 5.263 | 3.574 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.032 | -1.205 | 1 | -3.773 | -3.574 | 3.574 | 9.177 | 1.863 | -0.084 | 0.907% | -0.907%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 5.263 | 3.258 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.032 | -1.216 | 1.001 | -3.788 | -3.258 | 3.258 | 9.215 | 1.871 | -0.077 | 0.8287% | -0.8287%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 5.263 | 3.353 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.032 | -1.221 | 1 | -3.81 | -3.353 | 3.353 | 9.242 | 1.877 | -0.08 | 0.8582% | -0.8582%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 5.263 | 3.505 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.032 | -1.22 | 1 | -3.814 | -3.505 | 3.505 | 9.254 | 1.879 | -0.084 | 0.8996% | -0.8996%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 5.263 | 3.942 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.03 | -1.218 | 0.998 | -3.836 | -3.942 | 3.942 | 9.309 | 1.89 | -0.095 | 1.01% | -1.01%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 5.263 | 4.458 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.029 | -1.233 | 0.996 | -3.909 | -4.458 | 4.458 | 9.484 | 1.926 | -0.11 | 1.147% | -1.147%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 5.263 | 4.921 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.027 | -1.251 | 0.994 | -3.991 | -4.921 | 4.921 | 9.762 | 1.982 | -0.121 | 1.224% | -1.224%
18 | 10 | 2.031 | 0.98 | I | very sunny | 5.263 | 5.189 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.262 | 0.992 | -4.04 | -5.189 | 5.189 | 9.87 | 2.004 | -0.13 | 1.3% | -1.3%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 5.263 | 5.258 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.255 | 0.992 | -4.025 | -5.258 | 5.258 | 9.835 | 1.997 | -0.131 | 1.314% | -1.314%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.026 | -1.24 | 0.993 | -3.978 | -5.263 | 5.263 | 9.727 | 1.975 | -0.13 | 1.319% | -1.319%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.207 | 0.994 | -3.875 | -5.263 | 5.263 | 9.493 | 1.928 | -0.127 | 1.32% | -1.32%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.14 | 0.997 | -3.667 | -5.263 | 5.263 | 9.019 | 1.831 | -0.12 | 1.313% | -1.313%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.058 | 0.999 | -3.413 | -5.263 | 5.263 | 8.435 | 1.713 | -0.112 | 1.31% | -1.31%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.989 | 1.002 | -3.2 | -5.263 | 5.263 | 7.941 | 1.613 | -0.106 | 1.317% | -1.317%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.943 | 1.003 | -3.059 | -5.263 | 5.263 | 7.615 | 1.546 | -0.101 | 1.309% | -1.309%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.029 | -0.916 | 1.004 | -2.975 | -5.263 | 5.263 | 7.418 | 1.506 | -0.099 | 1.317% | -1.317%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.901 | 1.005 | -2.928 | -5.263 | 5.263 | 7.31 | 1.484 | -0.097 | 1.31% | -1.31%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.9 | 1.005 | -2.924 | -5.263 | 5.263 | 7.301 | 1.483 | -0.097 | 1.311% | -1.311%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.922 | 1.004 | -2.994 | -5.263 | 5.263 | 7.464 | 1.516 | -0.099 | 1.309% | -1.309%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.981 | 1.002 | -3.174 | -5.263 | 5.263 | 7.881 | 1.6 | -0.105 | 1.315% | -1.315%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.069 | 0.999 | -3.447 | -5.263 | 5.263 | 8.513 | 1.729 | -0.113 | 1.31% | -1.31%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 5.263 | 5.258 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.129 | 0.997 | -3.633 | -5.258 | 5.258 | 8.94 | 1.815 | -0.119 | 1.314% | -1.314%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 5.263 | 5.205 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.027 | -1.147 | 0.996 | -3.686 | -5.205 | 5.205 | 9.062 | 1.84 | -0.119 | 1.296% | -1.296%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 5.263 | 5.095 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.028 | -1.166 | 0.996 | -3.74 | -5.095 | 5.095 | 9.109 | 1.85 | -0.121 | 1.311% | -1.311%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 5.263 | 4.979 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.028 | -1.173 | 0.996 | -3.755 | -4.979 | 4.979 | 9.142 | 1.856 | -0.119 | 1.285% | -1.285%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 5.263 | 4.916 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.028 | -1.179 | 0.996 | -3.77 | -4.916 | 4.916 | 9.174 | 1.863 | -0.118 | 1.27% | -1.27%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 5.263 | 4.984 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.028 | -1.182 | 0.996 | -3.782 | -4.984 | 4.984 | 9.202 | 1.869 | -0.12 | 1.287% | -1.287%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 5.263 | 5.016 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.028 | -1.183 | 0.996 | -3.788 | -5.016 | 5.016 | 9.217 | 1.872 | -0.121 | 1.296% | -1.296%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 5.263 | 5.147 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.027 | -1.189 | 0.995 | -3.815 | -5.147 | 5.147 | 9.279 | 1.884 | -0.125 | 1.329% | -1.329%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 5.263 | 5.237 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.027 | -1.214 | 0.994 | -3.896 | -5.237 | 5.237 | 9.464 | 1.922 | -0.13 | 1.355% | -1.355%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.026 | -1.244 | 0.993 | -3.989 | -5.263 | 5.263 | 9.753 | 1.98 | -0.13 | 1.315% | -1.315%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.26 | 0.992 | -4.04 | -5.263 | 5.263 | 9.868 | 2.004 | -0.132 | 1.32% | -1.32%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.255 | 0.992 | -4.025 | -5.263 | 5.263 | 9.834 | 1.997 | -0.132 | 1.324% | -1.324%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.026 | -1.24 | 0.993 | -3.978 | -5.263 | 5.263 | 9.727 | 1.975 | -0.13 | 1.319% | -1.319%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.207 | 0.994 | -3.875 | -5.263 | 5.263 | 9.493 | 1.928 | -0.127 | 1.32% | -1.32%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.14 | 0.997 | -3.667 | -5.263 | 5.263 | 9.019 | 1.831 | -0.12 | 1.313% | -1.313%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.058 | 0.999 | -3.413 | -5.263 | 5.263 | 8.435 | 1.713 | -0.112 | 1.31% | -1.31%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.989 | 1.002 | -3.2 | -5.263 | 5.263 | 7.941 | 1.613 | -0.106 | 1.317% | -1.317%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.943 | 1.003 | -3.059 | -5.263 | 5.263 | 7.615 | 1.546 | -0.101 | 1.309% | -1.309%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.029 | -0.916 | 1.004 | -2.975 | -5.263 | 5.263 | 7.418 | 1.506 | -0.099 | 1.317% | -1.317%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.901 | 1.005 | -2.928 | -5.263 | 5.263 | 7.31 | 1.484 | -0.097 | 1.31% | -1.31%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.9 | 1.005 | -2.924 | -5.263 | 5.263 | 7.301 | 1.483 | -0.097 | 1.311% | -1.311%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.922 | 1.004 | -2.994 | -5.263 | 5.263 | 7.464 | 1.516 | -0.099 | 1.309% | -1.309%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.981 | 1.002 | -3.174 | -5.263 | 5.263 | 7.881 | 1.6 | -0.105 | 1.315% | -1.315%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.069 | 0.999 | -3.447 | -5.263 | 5.263 | 8.513 | 1.729 | -0.113 | 1.31% | -1.31%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.129 | 0.997 | -3.633 | -5.263 | 5.263 | 8.94 | 1.815 | -0.119 | 1.314% | -1.314%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.027 | -1.146 | 0.996 | -3.685 | -5.263 | 5.263 | 9.06 | 1.84 | -0.121 | 1.318% | -1.318%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 5.263 | 5.258 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.027 | -1.153 | 0.996 | -3.707 | -5.258 | 5.258 | 9.109 | 1.85 | -0.121 | 1.311% | -1.311%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 5.263 | 5.242 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.027 | -1.158 | 0.996 | -3.72 | -5.242 | 5.242 | 9.139 | 1.856 | -0.122 | 1.317% | -1.317%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 5.263 | 5.226 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.027 | -1.162 | 0.996 | -3.734 | -5.226 | 5.226 | 9.17 | 1.862 | -0.122 | 1.313% | -1.313%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 5.263 | 5.226 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.027 | -1.166 | 0.996 | -3.746 | -5.226 | 5.226 | 9.2 | 1.868 | -0.122 | 1.309% | -1.309%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 5.263 | 5.237 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.027 | -1.178 | 0.995 | -3.784 | -5.237 | 5.237 | 9.212 | 1.871 | -0.126 | 1.349% | -1.349%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 5.263 | 5.252 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.027 | -1.187 | 0.995 | -3.813 | -5.252 | 5.252 | 9.277 | 1.884 | -0.127 | 1.35% | -1.35%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 5.263 | 5.258 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.027 | -1.203 | 0.994 | -3.864 | -5.258 | 5.258 | 9.468 | 1.922 | -0.126 | 1.313% | -1.313%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.026 | -1.244 | 0.993 | -3.989 | -5.263 | 5.263 | 9.753 | 1.98 | -0.13 | 1.315% | -1.315%
18 | 10 | 2.031 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.26 | 0.992 | -4.04 | -5.263 | 5.263 | 9.868 | 2.004 | -0.132 | 1.32% | -1.32%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.255 | 0.992 | -4.025 | -5.263 | 5.263 | 9.834 | 1.997 | -0.132 | 1.324% | -1.324%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.026 | -1.24 | 0.993 | -3.978 | -5.263 | 5.263 | 9.727 | 1.975 | -0.13 | 1.319% | -1.319%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.207 | 0.994 | -3.875 | -5.263 | 5.263 | 9.493 | 1.928 | -0.127 | 1.32% | -1.32%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.14 | 0.997 | -3.667 | -5.263 | 5.263 | 9.019 | 1.831 | -0.12 | 1.313% | -1.313%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.058 | 0.999 | -3.413 | -5.263 | 5.263 | 8.435 | 1.713 | -0.112 | 1.31% | -1.31%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.989 | 1.002 | -3.2 | -5.263 | 5.263 | 7.941 | 1.613 | -0.106 | 1.317% | -1.317%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.819 | 0.989 | -2.973 | -10.526 | 10.526 | 7.507 | 1.524 | -0.209 | 2.709% | -2.709%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.015 | -0.791 | 0.99 | -2.888 | -10.526 | 10.526 | 7.314 | 1.485 | -0.203 | 2.701% | -2.701%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.776 | 0.991 | -2.84 | -10.526 | 10.526 | 7.207 | 1.463 | -0.2 | 2.7% | -2.7%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.775 | 0.991 | -2.837 | -10.526 | 10.526 | 7.198 | 1.462 | -0.2 | 2.703% | -2.703%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.015 | -0.798 | 0.99 | -2.907 | -10.526 | 10.526 | 7.358 | 1.494 | -0.205 | 2.711% | -2.711%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.856 | 0.988 | -3.089 | -10.526 | 10.526 | 7.769 | 1.578 | -0.217 | 2.717% | -2.717%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 10.526 | 10.505 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.937 | 0.985 | -3.337 | -10.505 | 10.505 | 8.395 | 1.705 | -0.231 | 2.678% | -2.678%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 10.526 | 10.231 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.014 | -1.016 | 0.983 | -3.574 | -10.231 | 10.231 | 8.817 | 1.79 | -0.242 | 2.671% | -2.671%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 10.526 | 9.41 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.016 | -1.054 | 0.985 | -3.642 | -9.41 | 9.41 | 8.956 | 1.819 | -0.225 | 2.451% | -2.451%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 10.526 | 8.284 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.019 | -1.077 | 0.988 | -3.644 | -8.284 | 8.284 | 9.036 | 1.835 | -0.194 | 2.102% | -2.102%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 10.526 | 7.147 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.022 | -1.118 | 0.991 | -3.707 | -7.147 | 7.147 | 9.091 | 1.846 | -0.17 | 1.836% | -1.836%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 10.526 | 6.516 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.024 | -1.135 | 0.992 | -3.725 | -6.516 | 6.516 | 9.137 | 1.855 | -0.155 | 1.668% | -1.668%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 10.526 | 6.705 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.023 | -1.14 | 0.991 | -3.752 | -6.705 | 6.705 | 9.16 | 1.86 | -0.162 | 1.738% | -1.738%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 10.526 | 7.01 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.022 | -1.135 | 0.991 | -3.753 | -7.01 | 7.01 | 9.169 | 1.862 | -0.169 | 1.81% | -1.81%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 10.526 | 7.884 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.02 | -1.123 | 0.988 | -3.766 | -7.884 | 7.884 | 9.212 | 1.87 | -0.192 | 2.042% | -2.042%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 10.526 | 8.916 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.017 | -1.124 | 0.984 | -3.832 | -8.916 | 8.916 | 9.371 | 1.903 | -0.223 | 2.324% | -2.324%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 10.526 | 9.842 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.014 | -1.134 | 0.98 | -3.92 | -9.842 | 9.842 | 9.631 | 1.956 | -0.252 | 2.55% | -2.55%
18 | 10 | 2.031 | 0.98 | I | very sunny | 10.526 | 10.379 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.013 | -1.139 | 0.978 | -3.969 | -10.379 | 10.379 | 9.73 | 1.976 | -0.27 | 2.7% | -2.7%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 10.526 | 10.515 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.132 | 0.978 | -3.953 | -10.515 | 10.515 | 9.693 | 1.968 | -0.273 | 2.739% | -2.739%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.012 | -1.116 | 0.979 | -3.905 | -10.526 | 10.526 | 9.587 | 1.947 | -0.27 | 2.739% | -2.739%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.083 | 0.98 | -3.801 | -10.526 | 10.526 | 9.357 | 1.9 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.013 | -1.016 | 0.982 | -3.59 | -10.526 | 10.526 | 8.889 | 1.805 | -0.25 | 2.736% | -2.736%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.934 | 0.985 | -3.332 | -10.526 | 10.526 | 8.314 | 1.688 | -0.233 | 2.726% | -2.726%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.865 | 0.988 | -3.116 | -10.526 | 10.526 | 7.829 | 1.59 | -0.218 | 2.709% | -2.709%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.819 | 0.989 | -2.973 | -10.526 | 10.526 | 7.507 | 1.524 | -0.209 | 2.709% | -2.709%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.015 | -0.791 | 0.99 | -2.888 | -10.526 | 10.526 | 7.314 | 1.485 | -0.203 | 2.701% | -2.701%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.776 | 0.991 | -2.84 | -10.526 | 10.526 | 7.207 | 1.463 | -0.2 | 2.7% | -2.7%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.775 | 0.991 | -2.837 | -10.526 | 10.526 | 7.198 | 1.462 | -0.2 | 2.703% | -2.703%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.015 | -0.798 | 0.99 | -2.907 | -10.526 | 10.526 | 7.358 | 1.494 | -0.205 | 2.711% | -2.711%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.856 | 0.988 | -3.089 | -10.526 | 10.526 | 7.769 | 1.578 | -0.217 | 2.717% | -2.717%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.945 | 0.985 | -3.366 | -10.526 | 10.526 | 8.391 | 1.704 | -0.235 | 2.724% | -2.724%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 10.526 | 10.515 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.013 | -1.005 | 0.983 | -3.555 | -10.515 | 10.515 | 8.812 | 1.789 | -0.247 | 2.727% | -2.727%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 10.526 | 10.41 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.014 | -1.024 | 0.982 | -3.609 | -10.41 | 10.41 | 8.933 | 1.814 | -0.248 | 2.701% | -2.701%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 10.526 | 10.189 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.014 | -1.041 | 0.983 | -3.649 | -10.189 | 10.189 | 8.985 | 1.824 | -0.245 | 2.654% | -2.654%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 10.526 | 9.958 | 3 | 1.041 | -1.291 | 1.009 | -3.839 | 1.015 | -1.052 | 0.983 | -3.667 | -9.958 | 9.958 | 9.021 | 1.832 | -0.24 | 2.592% | -2.592%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 10.526 | 9.831 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.015 | -1.059 | 0.983 | -3.683 | -9.831 | 9.831 | 9.054 | 1.838 | -0.238 | 2.561% | -2.561%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 10.526 | 9.968 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.014 | -1.06 | 0.983 | -3.694 | -9.968 | 9.968 | 9.08 | 1.844 | -0.242 | 2.596% | -2.596%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 10.526 | 10.031 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.014 | -1.06 | 0.982 | -3.7 | -10.031 | 10.031 | 9.094 | 1.847 | -0.244 | 2.613% | -2.613%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 10.526 | 10.294 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.014 | -1.063 | 0.981 | -3.724 | -10.294 | 10.294 | 9.151 | 1.858 | -0.253 | 2.69% | -2.69%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 10.526 | 10.473 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.013 | -1.085 | 0.98 | -3.805 | -10.473 | 10.473 | 9.331 | 1.895 | -0.263 | 2.741% | -2.741%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.012 | -1.12 | 0.978 | -3.916 | -10.526 | 10.526 | 9.612 | 1.952 | -0.271 | 2.742% | -2.742%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.012 | -1.136 | 0.978 | -3.968 | -10.526 | 10.526 | 9.726 | 1.975 | -0.274 | 2.74% | -2.74%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.132 | 0.978 | -3.953 | -10.526 | 10.526 | 9.693 | 1.968 | -0.273 | 2.739% | -2.739%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.012 | -1.116 | 0.979 | -3.905 | -10.526 | 10.526 | 9.587 | 1.947 | -0.27 | 2.739% | -2.739%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.083 | 0.98 | -3.801 | -10.526 | 10.526 | 9.357 | 1.9 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.013 | -1.016 | 0.982 | -3.59 | -10.526 | 10.526 | 8.889 | 1.805 | -0.25 | 2.736% | -2.736%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.934 | 0.985 | -3.332 | -10.526 | 10.526 | 8.314 | 1.688 | -0.233 | 2.726% | -2.726%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.865 | 0.988 | -3.116 | -10.526 | 10.526 | 7.829 | 1.59 | -0.218 | 2.709% | -2.709%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.819 | 0.989 | -2.973 | -10.526 | 10.526 | 7.507 | 1.524 | -0.209 | 2.709% | -2.709%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.015 | -0.791 | 0.99 | -2.888 | -10.526 | 10.526 | 7.314 | 1.485 | -0.203 | 2.701% | -2.701%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.776 | 0.991 | -2.84 | -10.526 | 10.526 | 7.207 | 1.463 | -0.2 | 2.7% | -2.7%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.775 | 0.991 | -2.837 | -10.526 | 10.526 | 7.198 | 1.462 | -0.2 | 2.703% | -2.703%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.015 | -0.798 | 0.99 | -2.907 | -10.526 | 10.526 | 7.358 | 1.494 | -0.205 | 2.711% | -2.711%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.856 | 0.988 | -3.089 | -10.526 | 10.526 | 7.769 | 1.578 | -0.217 | 2.717% | -2.717%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.945 | 0.985 | -3.366 | -10.526 | 10.526 | 8.391 | 1.704 | -0.235 | 2.724% | -2.724%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.013 | -1.005 | 0.983 | -3.555 | -10.526 | 10.526 | 8.812 | 1.789 | -0.247 | 2.727% | -2.727%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.013 | -1.022 | 0.982 | -3.608 | -10.526 | 10.526 | 8.93 | 1.813 | -0.251 | 2.734% | -2.734%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 10.526 | 10.515 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.013 | -1.029 | 0.982 | -3.63 | -10.515 | 10.515 | 8.978 | 1.823 | -0.252 | 2.73% | -2.73%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 10.526 | 10.484 | 3 | 1.041 | -1.291 | 1.009 | -3.839 | 1.013 | -1.034 | 0.982 | -3.644 | -10.484 | 10.484 | 9.009 | 1.829 | -0.252 | 2.721% | -2.721%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 10.526 | 10.452 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.013 | -1.039 | 0.982 | -3.657 | -10.452 | 10.452 | 9.04 | 1.836 | -0.252 | 2.712% | -2.712%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 10.526 | 10.452 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.013 | -1.043 | 0.982 | -3.67 | -10.452 | 10.452 | 9.069 | 1.842 | -0.253 | 2.714% | -2.714%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 10.526 | 10.473 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.013 | -1.05 | 0.981 | -3.692 | -10.473 | 10.473 | 9.083 | 1.844 | -0.255 | 2.731% | -2.731%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 10.526 | 10.505 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.013 | -1.058 | 0.981 | -3.72 | -10.505 | 10.505 | 9.146 | 1.857 | -0.258 | 2.744% | -2.744%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 10.526 | 10.515 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.013 | -1.08 | 0.98 | -3.789 | -10.515 | 10.515 | 9.332 | 1.895 | -0.262 | 2.731% | -2.731%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.012 | -1.12 | 0.978 | -3.916 | -10.526 | 10.526 | 9.612 | 1.952 | -0.271 | 2.742% | -2.742%
18 | 10 | 2.031 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.012 | -1.136 | 0.978 | -3.968 | -10.526 | 10.526 | 9.726 | 1.975 | -0.274 | 2.74% | -2.74%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.132 | 0.978 | -3.953 | -10.526 | 10.526 | 9.693 | 1.968 | -0.273 | 2.739% | -2.739%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.012 | -1.116 | 0.979 | -3.905 | -10.526 | 10.526 | 9.587 | 1.947 | -0.27 | 2.739% | -2.739%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.083 | 0.98 | -3.801 | -10.526 | 10.526 | 9.357 | 1.9 | -0.263 | 2.734% | -2.734%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.013 | -1.016 | 0.982 | -3.59 | -10.526 | 10.526 | 8.889 | 1.805 | -0.25 | 2.736% | -2.736%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.934 | 0.985 | -3.332 | -10.526 | 10.526 | 8.314 | 1.688 | -0.233 | 2.726% | -2.726%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.865 | 0.988 | -3.116 | -10.526 | 10.526 | 7.829 | 1.59 | -0.218 | 2.709% | -2.709%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.001 | -1.663 | 0.989 | -2.755 | -5.263 | 5.263 | 7.502 | 1.523 | -0.214 | 2.773% | -2.773%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.002 | -1.608 | 0.99 | -2.67 | -5.263 | 5.263 | 7.309 | 1.484 | -0.208 | 2.767% | -2.767%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.002 | -1.578 | 0.99 | -2.624 | -5.263 | 5.263 | 7.202 | 1.463 | -0.205 | 2.768% | -2.768%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.002 | -1.575 | 0.99 | -2.62 | -5.263 | 5.263 | 7.194 | 1.461 | -0.204 | 2.757% | -2.757%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.002 | -1.621 | 0.989 | -2.69 | -5.263 | 5.263 | 7.354 | 1.493 | -0.209 | 2.763% | -2.763%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.737 | 0.987 | -2.87 | -5.263 | 5.263 | 7.765 | 1.577 | -0.221 | 2.767% | -2.767%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 5.263 | 5.252 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.897 | 0.985 | -3.116 | -5.252 | 5.252 | 8.39 | 1.704 | -0.236 | 2.736% | -2.736%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 5.263 | 5.116 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.998 | -2.054 | 0.983 | -3.353 | -5.116 | 5.116 | 8.812 | 1.789 | -0.247 | 2.727% | -2.727%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 5.263 | 4.705 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 1 | -2.124 | 0.984 | -3.439 | -4.705 | 4.705 | 8.951 | 1.818 | -0.23 | 2.505% | -2.505%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 5.263 | 4.142 | 4 | 1.025 | -2.537 | 1.009 | -3.826 | 1.003 | -2.165 | 0.988 | -3.47 | -4.142 | 4.142 | 9.032 | 1.834 | -0.198 | 2.145% | -2.145%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 5.263 | 3.574 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 1.006 | -2.241 | 0.99 | -3.557 | -3.574 | 3.574 | 9.087 | 1.845 | -0.174 | 1.879% | -1.879%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 5.263 | 3.258 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 1.007 | -2.272 | 0.992 | -3.588 | -3.258 | 3.258 | 9.134 | 1.855 | -0.158 | 1.7% | -1.7%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 5.263 | 3.353 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 1.007 | -2.281 | 0.991 | -3.608 | -3.353 | 3.353 | 9.157 | 1.859 | -0.165 | 1.77% | -1.77%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 5.263 | 3.505 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 1.006 | -2.273 | 0.99 | -3.603 | -3.505 | 3.505 | 9.165 | 1.861 | -0.173 | 1.853% | -1.853%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 5.263 | 3.942 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 1.004 | -2.228 | 0.988 | -3.556 | -3.942 | 3.942 | 9.213 | 1.871 | -0.191 | 2.031% | -2.031%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 5.263 | 4.458 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 1 | -2.262 | 0.984 | -3.638 | -4.458 | 4.458 | 9.366 | 1.902 | -0.228 | 2.376% | -2.376%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 5.263 | 4.921 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.996 | -2.29 | 0.98 | -3.708 | -4.921 | 4.921 | 9.625 | 1.954 | -0.258 | 2.611% | -2.611%
18 | 10 | 2.031 | 0.98 | I | very sunny | 5.263 | 5.189 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.994 | -2.303 | 0.978 | -3.744 | -5.189 | 5.189 | 9.723 | 1.974 | -0.277 | 2.77% | -2.77%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 5.263 | 5.258 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.994 | -2.289 | 0.977 | -3.726 | -5.258 | 5.258 | 9.686 | 1.967 | -0.28 | 2.81% | -2.81%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.258 | 0.978 | -3.678 | -5.263 | 5.263 | 9.58 | 1.945 | -0.277 | 2.81% | -2.81%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.995 | -2.192 | 0.979 | -3.574 | -5.263 | 5.263 | 9.35 | 1.899 | -0.27 | 2.807% | -2.807%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.997 | -2.057 | 0.982 | -3.366 | -5.263 | 5.263 | 8.884 | 1.804 | -0.255 | 2.79% | -2.79%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.893 | 0.985 | -3.111 | -5.263 | 5.263 | 8.309 | 1.687 | -0.238 | 2.785% | -2.785%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1 | -1.754 | 0.987 | -2.896 | -5.263 | 5.263 | 7.824 | 1.589 | -0.223 | 2.771% | -2.771%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.001 | -1.663 | 0.989 | -2.755 | -5.263 | 5.263 | 7.502 | 1.523 | -0.214 | 2.773% | -2.773%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.002 | -1.608 | 0.99 | -2.67 | -5.263 | 5.263 | 7.309 | 1.484 | -0.208 | 2.767% | -2.767%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.002 | -1.578 | 0.99 | -2.624 | -5.263 | 5.263 | 7.202 | 1.463 | -0.205 | 2.768% | -2.768%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.002 | -1.575 | 0.99 | -2.62 | -5.263 | 5.263 | 7.194 | 1.461 | -0.204 | 2.757% | -2.757%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.002 | -1.621 | 0.989 | -2.69 | -5.263 | 5.263 | 7.354 | 1.493 | -0.209 | 2.763% | -2.763%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.737 | 0.987 | -2.87 | -5.263 | 5.263 | 7.765 | 1.577 | -0.221 | 2.767% | -2.767%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.915 | 0.984 | -3.145 | -5.263 | 5.263 | 8.386 | 1.703 | -0.24 | 2.782% | -2.782%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 5.263 | 5.258 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.997 | -2.035 | 0.982 | -3.332 | -5.258 | 5.258 | 8.806 | 1.788 | -0.253 | 2.793% | -2.793%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 5.263 | 5.205 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.997 | -2.073 | 0.982 | -3.387 | -5.205 | 5.205 | 8.928 | 1.813 | -0.253 | 2.756% | -2.756%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 5.263 | 5.095 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.997 | -2.104 | 0.982 | -3.429 | -5.095 | 5.095 | 8.979 | 1.823 | -0.251 | 2.719% | -2.719%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 5.263 | 4.979 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.998 | -2.123 | 0.982 | -3.452 | -4.979 | 4.979 | 9.015 | 1.831 | -0.246 | 2.656% | -2.656%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 5.263 | 4.916 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.998 | -2.137 | 0.983 | -3.47 | -4.916 | 4.916 | 9.049 | 1.837 | -0.243 | 2.615% | -2.615%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 5.263 | 4.984 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.998 | -2.139 | 0.982 | -3.478 | -4.984 | 4.984 | 9.074 | 1.843 | -0.248 | 2.66% | -2.66%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 5.263 | 5.016 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.998 | -2.141 | 0.982 | -3.482 | -5.016 | 5.016 | 9.088 | 1.845 | -0.25 | 2.677% | -2.677%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 5.263 | 5.147 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.997 | -2.148 | 0.981 | -3.5 | -5.147 | 5.147 | 9.146 | 1.857 | -0.258 | 2.744% | -2.744%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 5.263 | 5.237 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.996 | -2.186 | 0.979 | -3.565 | -5.237 | 5.237 | 9.327 | 1.894 | -0.267 | 2.783% | -2.783%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.994 | -2.265 | 0.978 | -3.689 | -5.263 | 5.263 | 9.605 | 1.95 | -0.278 | 2.813% | -2.813%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.994 | -2.298 | 0.977 | -3.74 | -5.263 | 5.263 | 9.719 | 1.974 | -0.281 | 2.81% | -2.81%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.994 | -2.289 | 0.977 | -3.725 | -5.263 | 5.263 | 9.686 | 1.967 | -0.28 | 2.81% | -2.81%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.258 | 0.978 | -3.678 | -5.263 | 5.263 | 9.58 | 1.945 | -0.277 | 2.81% | -2.81%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.995 | -2.192 | 0.979 | -3.574 | -5.263 | 5.263 | 9.35 | 1.899 | -0.27 | 2.807% | -2.807%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.997 | -2.057 | 0.982 | -3.366 | -5.263 | 5.263 | 8.884 | 1.804 | -0.255 | 2.79% | -2.79%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.893 | 0.985 | -3.111 | -5.263 | 5.263 | 8.309 | 1.687 | -0.238 | 2.785% | -2.785%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1 | -1.754 | 0.987 | -2.896 | -5.263 | 5.263 | 7.824 | 1.589 | -0.223 | 2.771% | -2.771%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.001 | -1.663 | 0.989 | -2.755 | -5.263 | 5.263 | 7.502 | 1.523 | -0.214 | 2.773% | -2.773%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.002 | -1.608 | 0.99 | -2.67 | -5.263 | 5.263 | 7.309 | 1.484 | -0.208 | 2.767% | -2.767%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.002 | -1.578 | 0.99 | -2.624 | -5.263 | 5.263 | 7.202 | 1.463 | -0.205 | 2.768% | -2.768%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.002 | -1.575 | 0.99 | -2.62 | -5.263 | 5.263 | 7.194 | 1.461 | -0.204 | 2.757% | -2.757%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.002 | -1.621 | 0.989 | -2.69 | -5.263 | 5.263 | 7.354 | 1.493 | -0.209 | 2.763% | -2.763%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.737 | 0.987 | -2.87 | -5.263 | 5.263 | 7.765 | 1.577 | -0.221 | 2.767% | -2.767%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.915 | 0.984 | -3.145 | -5.263 | 5.263 | 8.386 | 1.703 | -0.24 | 2.782% | -2.782%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.997 | -2.035 | 0.982 | -3.331 | -5.263 | 5.263 | 8.806 | 1.788 | -0.253 | 2.793% | -2.793%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.997 | -2.069 | 0.981 | -3.384 | -5.263 | 5.263 | 8.924 | 1.812 | -0.257 | 2.799% | -2.799%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 5.263 | 5.258 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.997 | -2.083 | 0.981 | -3.405 | -5.258 | 5.258 | 8.972 | 1.822 | -0.258 | 2.795% | -2.795%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 5.263 | 5.242 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.997 | -2.093 | 0.981 | -3.42 | -5.242 | 5.242 | 9.003 | 1.828 | -0.258 | 2.786% | -2.786%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 5.263 | 5.226 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.997 | -2.103 | 0.981 | -3.434 | -5.226 | 5.226 | 9.034 | 1.834 | -0.258 | 2.777% | -2.777%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 5.263 | 5.226 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.997 | -2.111 | 0.981 | -3.447 | -5.226 | 5.226 | 9.063 | 1.84 | -0.259 | 2.778% | -2.778%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 5.263 | 5.237 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.996 | -2.122 | 0.981 | -3.464 | -5.237 | 5.237 | 9.077 | 1.843 | -0.261 | 2.795% | -2.795%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 5.263 | 5.252 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.996 | -2.139 | 0.98 | -3.492 | -5.252 | 5.252 | 9.14 | 1.856 | -0.264 | 2.807% | -2.807%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 5.263 | 5.258 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.995 | -2.185 | 0.979 | -3.563 | -5.258 | 5.258 | 9.325 | 1.894 | -0.269 | 2.804% | -2.804%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.994 | -2.265 | 0.978 | -3.689 | -5.263 | 5.263 | 9.605 | 1.95 | -0.278 | 2.813% | -2.813%
18 | 10 | 2.031 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.994 | -2.298 | 0.977 | -3.74 | -5.263 | 5.263 | 9.719 | 1.974 | -0.281 | 2.81% | -2.81%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.994 | -2.289 | 0.977 | -3.725 | -5.263 | 5.263 | 9.686 | 1.967 | -0.28 | 2.81% | -2.81%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.258 | 0.978 | -3.678 | -5.263 | 5.263 | 9.58 | 1.945 | -0.277 | 2.81% | -2.81%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.995 | -2.192 | 0.979 | -3.574 | -5.263 | 5.263 | 9.35 | 1.899 | -0.27 | 2.807% | -2.807%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.997 | -2.057 | 0.982 | -3.366 | -5.263 | 5.263 | 8.884 | 1.804 | -0.255 | 2.79% | -2.79%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.893 | 0.985 | -3.111 | -5.263 | 5.263 | 8.309 | 1.687 | -0.238 | 2.785% | -2.785%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1 | -1.754 | 0.987 | -2.896 | -5.263 | 5.263 | 7.824 | 1.589 | -0.223 | 2.771% | -2.771%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.48 | 0.977 | -2.588 | -7.371 | 10.526 | 7.412 | 1.505 | -0.304 | 3.94% | -3.94%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.425 | 0.978 | -2.502 | -7.373 | 10.526 | 7.222 | 1.466 | -0.295 | 3.924% | -3.924%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.395 | 0.978 | -2.455 | -7.374 | 10.526 | 7.116 | 1.445 | -0.291 | 3.929% | -3.929%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.392 | 0.978 | -2.452 | -7.374 | 10.526 | 7.107 | 1.443 | -0.291 | 3.933% | -3.933%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.438 | 0.978 | -2.522 | -7.372 | 10.526 | 7.266 | 1.475 | -0.297 | 3.927% | -3.927%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.555 | 0.976 | -2.704 | -7.366 | 10.526 | 7.671 | 1.558 | -0.315 | 3.944% | -3.944%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 10.526 | 10.505 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.733 | 0.972 | -2.98 | -7.357 | 10.505 | 8.285 | 1.682 | -0.341 | 3.953% | -3.953%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 10.526 | 10.231 | 4 | 1.025 | -2.489 | 1.01 | -3.753 | 0.985 | -1.854 | 0.97 | -3.168 | -7.351 | 10.231 | 8.7 | 1.767 | -0.359 | 3.963% | -3.963%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 10.526 | 9.41 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.995 | -2.046 | 0.98 | -3.366 | -5.57 | 9.41 | 8.908 | 1.809 | -0.273 | 2.974% | -2.974%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 10.526 | 8.284 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -2.06 | 0.979 | -3.387 | -5.57 | 8.284 | 8.956 | 1.819 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 10.526 | 7.147 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -2.069 | 0.979 | -3.401 | -5.57 | 7.147 | 8.986 | 1.825 | -0.275 | 2.969% | -2.969%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 10.526 | 6.516 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -2.078 | 0.979 | -3.414 | -5.569 | 6.516 | 9.016 | 1.831 | -0.276 | 2.97% | -2.97%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 10.526 | 6.705 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2.086 | 0.979 | -3.427 | -5.569 | 6.705 | 9.045 | 1.837 | -0.277 | 2.971% | -2.971%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 10.526 | 7.01 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.09 | 0.979 | -3.434 | -5.569 | 7.01 | 9.06 | 1.84 | -0.278 | 2.977% | -2.977%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 10.526 | 7.884 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.109 | 0.978 | -3.463 | -5.568 | 7.884 | 9.124 | 1.853 | -0.28 | 2.977% | -2.977%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 10.526 | 8.916 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.162 | 0.978 | -3.546 | -5.566 | 8.916 | 9.308 | 1.89 | -0.286 | 2.981% | -2.981%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 10.526 | 9.842 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.244 | 0.976 | -3.672 | -5.563 | 9.842 | 9.588 | 1.947 | -0.295 | 2.985% | -2.985%
18 | 10 | 2.031 | 0.98 | I | very sunny | 10.526 | 10.379 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.277 | 0.975 | -3.724 | -5.561 | 10.379 | 9.702 | 1.97 | -0.298 | 2.98% | -2.98%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 10.526 | 10.515 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.267 | 0.976 | -3.709 | -5.562 | 10.515 | 9.669 | 1.963 | -0.297 | 2.98% | -2.98%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.236 | 0.976 | -3.661 | -5.563 | 10.526 | 9.563 | 1.942 | -0.294 | 2.983% | -2.983%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.17 | 0.977 | -3.557 | -5.565 | 10.526 | 9.333 | 1.895 | -0.287 | 2.983% | -2.983%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.995 | -2.035 | 0.98 | -3.348 | -5.571 | 10.526 | 8.867 | 1.801 | -0.272 | 2.976% | -2.976%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.711 | 0.973 | -2.946 | -7.359 | 10.526 | 8.209 | 1.667 | -0.338 | 3.955% | -3.955%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.572 | 0.975 | -2.73 | -7.365 | 10.526 | 7.73 | 1.57 | -0.317 | 3.939% | -3.939%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.48 | 0.977 | -2.588 | -7.37 | 10.526 | 7.412 | 1.505 | -0.304 | 3.94% | -3.94%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.425 | 0.978 | -2.502 | -7.373 | 10.526 | 7.222 | 1.466 | -0.295 | 3.924% | -3.924%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.395 | 0.978 | -2.455 | -7.374 | 10.526 | 7.116 | 1.445 | -0.291 | 3.929% | -3.929%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.392 | 0.978 | -2.452 | -7.374 | 10.526 | 7.107 | 1.443 | -0.291 | 3.933% | -3.933%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.438 | 0.978 | -2.522 | -7.372 | 10.526 | 7.266 | 1.475 | -0.297 | 3.927% | -3.927%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.555 | 0.976 | -2.704 | -7.366 | 10.526 | 7.671 | 1.558 | -0.315 | 3.944% | -3.944%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.733 | 0.972 | -2.98 | -7.357 | 10.526 | 8.285 | 1.682 | -0.341 | 3.953% | -3.953%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 10.526 | 10.515 | 4 | 1.025 | -2.489 | 1.01 | -3.753 | 0.985 | -1.854 | 0.97 | -3.168 | -7.351 | 10.515 | 8.7 | 1.767 | -0.359 | 3.963% | -3.963%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 10.526 | 10.41 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.995 | -2.046 | 0.98 | -3.366 | -5.57 | 10.41 | 8.908 | 1.809 | -0.273 | 2.974% | -2.974%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 10.526 | 10.189 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -2.06 | 0.979 | -3.387 | -5.57 | 10.189 | 8.956 | 1.819 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 10.526 | 9.958 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -2.069 | 0.979 | -3.401 | -5.57 | 9.958 | 8.986 | 1.825 | -0.275 | 2.969% | -2.969%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 10.526 | 9.831 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -2.078 | 0.979 | -3.414 | -5.569 | 9.831 | 9.016 | 1.831 | -0.276 | 2.97% | -2.97%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 10.526 | 9.968 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2.086 | 0.979 | -3.427 | -5.569 | 9.968 | 9.045 | 1.837 | -0.277 | 2.971% | -2.971%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 10.526 | 10.031 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.09 | 0.979 | -3.434 | -5.569 | 10.031 | 9.06 | 1.84 | -0.278 | 2.977% | -2.977%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 10.526 | 10.294 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.109 | 0.978 | -3.463 | -5.568 | 10.294 | 9.124 | 1.853 | -0.28 | 2.977% | -2.977%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 10.526 | 10.473 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.162 | 0.978 | -3.546 | -5.566 | 10.473 | 9.308 | 1.89 | -0.286 | 2.981% | -2.981%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.244 | 0.976 | -3.672 | -5.563 | 10.526 | 9.588 | 1.947 | -0.295 | 2.985% | -2.985%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.277 | 0.975 | -3.724 | -5.561 | 10.526 | 9.702 | 1.97 | -0.298 | 2.98% | -2.98%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.267 | 0.976 | -3.709 | -5.562 | 10.526 | 9.669 | 1.963 | -0.297 | 2.98% | -2.98%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.236 | 0.976 | -3.661 | -5.563 | 10.526 | 9.563 | 1.942 | -0.294 | 2.983% | -2.983%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.17 | 0.977 | -3.557 | -5.565 | 10.526 | 9.333 | 1.895 | -0.287 | 2.983% | -2.983%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.995 | -2.035 | 0.98 | -3.348 | -5.571 | 10.526 | 8.867 | 1.801 | -0.272 | 2.976% | -2.976%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.711 | 0.973 | -2.946 | -7.359 | 10.526 | 8.209 | 1.667 | -0.338 | 3.955% | -3.955%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.572 | 0.975 | -2.73 | -7.365 | 10.526 | 7.73 | 1.57 | -0.317 | 3.939% | -3.939%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.48 | 0.977 | -2.588 | -7.37 | 10.526 | 7.412 | 1.505 | -0.304 | 3.94% | -3.94%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.425 | 0.978 | -2.502 | -7.373 | 10.526 | 7.222 | 1.466 | -0.295 | 3.924% | -3.924%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.395 | 0.978 | -2.455 | -7.374 | 10.526 | 7.116 | 1.445 | -0.291 | 3.929% | -3.929%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.392 | 0.978 | -2.452 | -7.374 | 10.526 | 7.107 | 1.443 | -0.291 | 3.933% | -3.933%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.438 | 0.978 | -2.522 | -7.372 | 10.526 | 7.266 | 1.475 | -0.297 | 3.927% | -3.927%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.555 | 0.976 | -2.704 | -7.366 | 10.526 | 7.671 | 1.558 | -0.315 | 3.944% | -3.944%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.733 | 0.972 | -2.98 | -7.357 | 10.526 | 8.285 | 1.682 | -0.341 | 3.953% | -3.953%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.489 | 1.01 | -3.753 | 0.985 | -1.854 | 0.97 | -3.168 | -7.351 | 10.526 | 8.7 | 1.767 | -0.359 | 3.963% | -3.963%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.995 | -2.046 | 0.98 | -3.366 | -5.57 | 10.526 | 8.908 | 1.809 | -0.273 | 2.974% | -2.974%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 10.526 | 10.515 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -2.06 | 0.979 | -3.387 | -5.57 | 10.515 | 8.956 | 1.819 | -0.274 | 2.969% | -2.969%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 10.526 | 10.484 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -2.069 | 0.979 | -3.401 | -5.57 | 10.484 | 8.986 | 1.825 | -0.275 | 2.969% | -2.969%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 10.526 | 10.452 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -2.078 | 0.979 | -3.414 | -5.569 | 10.452 | 9.016 | 1.831 | -0.276 | 2.97% | -2.97%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 10.526 | 10.452 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2.086 | 0.979 | -3.427 | -5.569 | 10.452 | 9.045 | 1.837 | -0.277 | 2.971% | -2.971%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 10.526 | 10.473 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.09 | 0.979 | -3.434 | -5.569 | 10.473 | 9.06 | 1.84 | -0.278 | 2.977% | -2.977%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 10.526 | 10.505 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.109 | 0.978 | -3.463 | -5.568 | 10.505 | 9.124 | 1.853 | -0.28 | 2.977% | -2.977%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 10.526 | 10.515 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.162 | 0.978 | -3.546 | -5.566 | 10.515 | 9.308 | 1.89 | -0.286 | 2.981% | -2.981%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.244 | 0.976 | -3.672 | -5.563 | 10.526 | 9.588 | 1.947 | -0.295 | 2.985% | -2.985%
18 | 10 | 2.031 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.277 | 0.975 | -3.724 | -5.561 | 10.526 | 9.702 | 1.97 | -0.298 | 2.98% | -2.98%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.267 | 0.976 | -3.709 | -5.562 | 10.526 | 9.669 | 1.963 | -0.297 | 2.98% | -2.98%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.236 | 0.976 | -3.661 | -5.563 | 10.526 | 9.563 | 1.942 | -0.294 | 2.983% | -2.983%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.17 | 0.977 | -3.557 | -5.565 | 10.526 | 9.333 | 1.895 | -0.287 | 2.983% | -2.983%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.995 | -2.035 | 0.98 | -3.348 | -5.571 | 10.526 | 8.867 | 1.801 | -0.272 | 2.976% | -2.976%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.711 | 0.973 | -2.946 | -7.359 | 10.526 | 8.209 | 1.667 | -0.338 | 3.955% | -3.955%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.572 | 0.975 | -2.73 | -7.365 | 10.526 | 7.73 | 1.57 | -0.317 | 3.939% | -3.939%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.974 | -2.38 | 0.974 | -2.38 | -5.263 | 5.263 | 7.388 | 1.5 | -0.328 | 4.251% | -4.251%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.975 | -2.293 | 0.975 | -2.293 | -5.263 | 5.263 | 7.198 | 1.462 | -0.319 | 4.244% | -4.244%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.975 | -2.246 | 0.975 | -2.246 | -5.263 | 5.263 | 7.093 | 1.44 | -0.314 | 4.239% | -4.239%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.975 | -2.242 | 0.975 | -2.242 | -5.263 | 5.263 | 7.084 | 1.439 | -0.314 | 4.244% | -4.244%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.974 | -2.313 | 0.974 | -2.313 | -5.263 | 5.263 | 7.242 | 1.47 | -0.321 | 4.244% | -4.244%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.972 | -2.497 | 0.972 | -2.497 | -5.263 | 5.263 | 7.645 | 1.552 | -0.341 | 4.27% | -4.27%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 5.263 | 5.252 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 5.252 | 8.265 | 1.678 | -0.361 | 4.185% | -4.185%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 5.263 | 5.116 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 5.116 | 8.698 | 1.766 | -0.361 | 3.985% | -3.985%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 5.263 | 4.705 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.705 | 4.705 | 8.821 | 1.791 | -0.36 | 3.921% | -3.921%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 5.263 | 4.142 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.976 | -3.185 | 0.976 | -3.185 | -4.142 | 4.142 | 8.922 | 1.812 | -0.308 | 3.337% | -3.337%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 5.263 | 3.574 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.98 | -3.311 | 0.98 | -3.311 | -3.574 | 3.574 | 8.993 | 1.826 | -0.268 | 2.894% | -2.894%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 5.263 | 3.258 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.983 | -3.373 | 0.983 | -3.373 | -3.258 | 3.258 | 9.048 | 1.837 | -0.244 | 2.626% | -2.626%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 5.263 | 3.353 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.982 | -3.371 | 0.982 | -3.371 | -3.353 | 3.353 | 9.069 | 1.842 | -0.253 | 2.714% | -2.714%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 5.263 | 3.505 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.98 | -3.354 | 0.98 | -3.354 | -3.505 | 3.505 | 9.073 | 1.842 | -0.265 | 2.838% | -2.838%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 5.263 | 3.942 | 5 | 1.008 | -3.901 | 1.008 | -3.901 | 0.977 | -3.286 | 0.977 | -3.286 | -3.942 | 3.942 | 9.106 | 1.849 | -0.298 | 3.169% | -3.169%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 5.263 | 4.458 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.458 | 4.458 | 9.237 | 1.876 | -0.357 | 3.721% | -3.721%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 5.263 | 4.921 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 4.921 | 9.529 | 1.935 | -0.354 | 3.582% | -3.582%
18 | 10 | 2.031 | 0.98 | I | very sunny | 5.263 | 5.189 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 5.189 | 9.647 | 1.959 | -0.353 | 3.53% | -3.53%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 5.263 | 5.258 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 5.258 | 9.613 | 1.952 | -0.353 | 3.542% | -3.542%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 5.263 | 9.502 | 1.93 | -0.355 | 3.602% | -3.602%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 5.263 | 9.263 | 1.881 | -0.357 | 3.711% | -3.711%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 5.263 | 8.779 | 1.783 | -0.36 | 3.939% | -3.939%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 5.263 | 8.186 | 1.662 | -0.361 | 4.224% | -4.224%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.972 | -2.524 | 0.972 | -2.524 | -5.263 | 5.263 | 7.703 | 1.564 | -0.344 | 4.275% | -4.275%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.974 | -2.38 | 0.974 | -2.38 | -5.263 | 5.263 | 7.388 | 1.5 | -0.328 | 4.251% | -4.251%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.975 | -2.293 | 0.975 | -2.293 | -5.263 | 5.263 | 7.198 | 1.462 | -0.319 | 4.244% | -4.244%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.975 | -2.246 | 0.975 | -2.246 | -5.263 | 5.263 | 7.093 | 1.44 | -0.314 | 4.239% | -4.239%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.975 | -2.242 | 0.975 | -2.242 | -5.263 | 5.263 | 7.084 | 1.439 | -0.314 | 4.244% | -4.244%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.974 | -2.313 | 0.974 | -2.313 | -5.263 | 5.263 | 7.242 | 1.47 | -0.321 | 4.244% | -4.244%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.972 | -2.497 | 0.972 | -2.497 | -5.263 | 5.263 | 7.645 | 1.552 | -0.341 | 4.27% | -4.27%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 5.263 | 8.265 | 1.678 | -0.361 | 4.185% | -4.185%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 5.263 | 5.258 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 5.258 | 8.698 | 1.766 | -0.361 | 3.985% | -3.985%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 5.263 | 5.205 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 5.205 | 8.821 | 1.791 | -0.36 | 3.921% | -3.921%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 5.263 | 5.095 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 5.095 | 8.87 | 1.801 | -0.36 | 3.9% | -3.9%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 5.263 | 4.979 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 4.979 | 8.901 | 1.807 | -0.36 | 3.887% | -3.887%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 5.263 | 4.916 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 4.916 | 8.932 | 1.814 | -0.36 | 3.874% | -3.874%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 5.263 | 4.984 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 4.984 | 8.962 | 1.82 | -0.36 | 3.862% | -3.862%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 5.263 | 5.016 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 5.016 | 8.979 | 1.823 | -0.359 | 3.845% | -3.845%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 5.263 | 5.147 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 5.147 | 9.045 | 1.837 | -0.359 | 3.818% | -3.818%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 5.263 | 5.237 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 5.237 | 9.237 | 1.876 | -0.357 | 3.721% | -3.721%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 5.263 | 9.529 | 1.935 | -0.354 | 3.582% | -3.582%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 5.263 | 9.647 | 1.959 | -0.353 | 3.53% | -3.53%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 5.263 | 9.613 | 1.952 | -0.353 | 3.542% | -3.542%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 5.263 | 9.502 | 1.93 | -0.355 | 3.602% | -3.602%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 5.263 | 9.263 | 1.881 | -0.357 | 3.711% | -3.711%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 5.263 | 8.779 | 1.783 | -0.36 | 3.939% | -3.939%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 5.263 | 8.186 | 1.662 | -0.361 | 4.224% | -4.224%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.972 | -2.524 | 0.972 | -2.524 | -5.263 | 5.263 | 7.703 | 1.564 | -0.344 | 4.275% | -4.275%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.974 | -2.38 | 0.974 | -2.38 | -5.263 | 5.263 | 7.388 | 1.5 | -0.328 | 4.251% | -4.251%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.975 | -2.293 | 0.975 | -2.293 | -5.263 | 5.263 | 7.198 | 1.462 | -0.319 | 4.244% | -4.244%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.975 | -2.246 | 0.975 | -2.246 | -5.263 | 5.263 | 7.093 | 1.44 | -0.314 | 4.239% | -4.239%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.975 | -2.242 | 0.975 | -2.242 | -5.263 | 5.263 | 7.084 | 1.439 | -0.314 | 4.244% | -4.244%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.974 | -2.313 | 0.974 | -2.313 | -5.263 | 5.263 | 7.242 | 1.47 | -0.321 | 4.244% | -4.244%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.972 | -2.497 | 0.972 | -2.497 | -5.263 | 5.263 | 7.645 | 1.552 | -0.341 | 4.27% | -4.27%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 5.263 | 8.265 | 1.678 | -0.361 | 4.185% | -4.185%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 5.263 | 8.698 | 1.766 | -0.361 | 3.985% | -3.985%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 5.263 | 8.821 | 1.791 | -0.36 | 3.921% | -3.921%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 5.263 | 5.258 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 5.258 | 8.87 | 1.801 | -0.36 | 3.9% | -3.9%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 5.263 | 5.242 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 5.242 | 8.901 | 1.807 | -0.36 | 3.887% | -3.887%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 5.263 | 5.226 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 5.226 | 8.932 | 1.814 | -0.36 | 3.874% | -3.874%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 5.263 | 5.226 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 5.226 | 8.962 | 1.82 | -0.36 | 3.862% | -3.862%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 5.263 | 5.237 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 5.237 | 8.979 | 1.823 | -0.359 | 3.845% | -3.845%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 5.263 | 5.252 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 5.252 | 9.045 | 1.837 | -0.359 | 3.818% | -3.818%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 5.263 | 5.258 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 5.258 | 9.237 | 1.876 | -0.357 | 3.721% | -3.721%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 5.263 | 9.529 | 1.935 | -0.354 | 3.582% | -3.582%
18 | 10 | 2.031 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 5.263 | 9.647 | 1.959 | -0.353 | 3.53% | -3.53%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 5.263 | 9.613 | 1.952 | -0.353 | 3.542% | -3.542%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 5.263 | 9.502 | 1.93 | -0.355 | 3.602% | -3.602%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 5.263 | 9.263 | 1.881 | -0.357 | 3.711% | -3.711%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 5.263 | 8.779 | 1.783 | -0.36 | 3.939% | -3.939%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 5.263 | 8.186 | 1.662 | -0.361 | 4.224% | -4.224%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.972 | -2.524 | 0.972 | -2.524 | -5.263 | 5.263 | 7.703 | 1.564 | -0.344 | 4.275% | -4.275%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.33 | 0.97 | -2.33 | -5.654 | 10.526 | 7.361 | 1.495 | -0.355 | 4.601% | -4.601%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.229 | 0.97 | -2.229 | -5.767 | 10.526 | 7.164 | 1.455 | -0.353 | 4.696% | -4.696%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.173 | 0.97 | -2.173 | -5.829 | 10.526 | 7.056 | 1.433 | -0.351 | 4.739% | -4.739%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -2.169 | 0.97 | -2.169 | -5.834 | 10.526 | 7.047 | 1.431 | -0.351 | 4.745% | -4.745%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.252 | 0.97 | -2.252 | -5.741 | 10.526 | 7.209 | 1.464 | -0.354 | 4.681% | -4.681%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.468 | 0.97 | -2.468 | -5.5 | 10.526 | 7.628 | 1.549 | -0.358 | 4.483% | -4.483%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 10.526 | 10.505 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 10.505 | 8.265 | 1.678 | -0.361 | 4.185% | -4.185%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 10.526 | 10.231 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 10.231 | 8.698 | 1.766 | -0.361 | 3.985% | -3.985%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 10.526 | 9.41 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 9.41 | 8.821 | 1.791 | -0.36 | 3.921% | -3.921%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 10.526 | 8.284 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 8.284 | 8.87 | 1.801 | -0.36 | 3.9% | -3.9%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 10.526 | 7.147 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 7.147 | 8.901 | 1.807 | -0.36 | 3.887% | -3.887%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 10.526 | 6.516 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 6.516 | 8.932 | 1.814 | -0.36 | 3.874% | -3.874%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 10.526 | 6.705 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 6.705 | 8.962 | 1.82 | -0.36 | 3.862% | -3.862%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 10.526 | 7.01 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 7.01 | 8.979 | 1.823 | -0.359 | 3.845% | -3.845%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 10.526 | 7.884 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 7.884 | 9.045 | 1.837 | -0.359 | 3.818% | -3.818%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 10.526 | 8.916 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 8.916 | 9.237 | 1.876 | -0.357 | 3.721% | -3.721%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 10.526 | 9.842 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 9.842 | 9.529 | 1.935 | -0.354 | 3.582% | -3.582%
18 | 10 | 2.031 | 0.98 | I | very sunny | 10.526 | 10.379 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 10.379 | 9.647 | 1.959 | -0.353 | 3.53% | -3.53%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 10.526 | 10.515 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 10.515 | 9.613 | 1.952 | -0.353 | 3.542% | -3.542%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 10.526 | 9.502 | 1.93 | -0.355 | 3.602% | -3.602%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 10.526 | 9.263 | 1.881 | -0.357 | 3.711% | -3.711%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 10.526 | 8.779 | 1.783 | -0.36 | 3.939% | -3.939%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 10.526 | 8.186 | 1.662 | -0.361 | 4.224% | -4.224%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.97 | -2.499 | 0.97 | -2.499 | -5.465 | 10.526 | 7.689 | 1.561 | -0.358 | 4.449% | -4.449%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.33 | 0.97 | -2.33 | -5.654 | 10.526 | 7.361 | 1.495 | -0.355 | 4.601% | -4.601%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.229 | 0.97 | -2.229 | -5.767 | 10.526 | 7.164 | 1.455 | -0.353 | 4.696% | -4.696%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.173 | 0.97 | -2.173 | -5.829 | 10.526 | 7.056 | 1.433 | -0.351 | 4.739% | -4.739%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -2.169 | 0.97 | -2.169 | -5.834 | 10.526 | 7.047 | 1.431 | -0.351 | 4.745% | -4.745%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.252 | 0.97 | -2.252 | -5.741 | 10.526 | 7.209 | 1.464 | -0.354 | 4.681% | -4.681%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.468 | 0.97 | -2.468 | -5.5 | 10.526 | 7.628 | 1.549 | -0.358 | 4.483% | -4.483%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 10.526 | 8.265 | 1.678 | -0.361 | 4.185% | -4.185%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 10.526 | 10.515 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 10.515 | 8.698 | 1.766 | -0.361 | 3.985% | -3.985%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 10.526 | 10.41 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 10.41 | 8.821 | 1.791 | -0.36 | 3.921% | -3.921%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 10.526 | 10.189 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 10.189 | 8.87 | 1.801 | -0.36 | 3.9% | -3.9%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 10.526 | 9.958 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 9.958 | 8.901 | 1.807 | -0.36 | 3.887% | -3.887%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 10.526 | 9.831 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 9.831 | 8.932 | 1.814 | -0.36 | 3.874% | -3.874%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 10.526 | 9.968 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 9.968 | 8.962 | 1.82 | -0.36 | 3.862% | -3.862%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 10.526 | 10.031 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 10.031 | 8.979 | 1.823 | -0.359 | 3.845% | -3.845%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 10.526 | 10.294 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 10.294 | 9.045 | 1.837 | -0.359 | 3.818% | -3.818%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 10.526 | 10.473 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 10.473 | 9.237 | 1.876 | -0.357 | 3.721% | -3.721%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 10.526 | 9.529 | 1.935 | -0.354 | 3.582% | -3.582%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 10.526 | 9.647 | 1.959 | -0.353 | 3.53% | -3.53%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 10.526 | 9.613 | 1.952 | -0.353 | 3.542% | -3.542%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 10.526 | 9.502 | 1.93 | -0.355 | 3.602% | -3.602%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 10.526 | 9.263 | 1.881 | -0.357 | 3.711% | -3.711%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 10.526 | 8.779 | 1.783 | -0.36 | 3.939% | -3.939%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 10.526 | 8.186 | 1.662 | -0.361 | 4.224% | -4.224%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.97 | -2.499 | 0.97 | -2.499 | -5.465 | 10.526 | 7.689 | 1.561 | -0.358 | 4.449% | -4.449%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.33 | 0.97 | -2.33 | -5.654 | 10.526 | 7.361 | 1.495 | -0.355 | 4.601% | -4.601%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.229 | 0.97 | -2.229 | -5.767 | 10.526 | 7.164 | 1.455 | -0.353 | 4.696% | -4.696%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.173 | 0.97 | -2.173 | -5.829 | 10.526 | 7.056 | 1.433 | -0.351 | 4.739% | -4.739%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -2.169 | 0.97 | -2.169 | -5.834 | 10.526 | 7.047 | 1.431 | -0.351 | 4.745% | -4.745%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.252 | 0.97 | -2.252 | -5.741 | 10.526 | 7.209 | 1.464 | -0.354 | 4.681% | -4.681%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.468 | 0.97 | -2.468 | -5.5 | 10.526 | 7.628 | 1.549 | -0.358 | 4.483% | -4.483%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 10.526 | 8.265 | 1.678 | -0.361 | 4.185% | -4.185%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 10.526 | 8.698 | 1.766 | -0.361 | 3.985% | -3.985%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 10.526 | 8.821 | 1.791 | -0.36 | 3.921% | -3.921%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 10.526 | 10.515 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 10.515 | 8.87 | 1.801 | -0.36 | 3.9% | -3.9%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 10.526 | 10.484 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 10.484 | 8.901 | 1.807 | -0.36 | 3.887% | -3.887%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 10.526 | 10.452 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 10.452 | 8.932 | 1.814 | -0.36 | 3.874% | -3.874%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 10.526 | 10.452 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 10.452 | 8.962 | 1.82 | -0.36 | 3.862% | -3.862%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 10.526 | 10.473 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 10.473 | 8.979 | 1.823 | -0.359 | 3.845% | -3.845%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 10.526 | 10.505 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 10.505 | 9.045 | 1.837 | -0.359 | 3.818% | -3.818%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 10.526 | 10.515 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 10.515 | 9.237 | 1.876 | -0.357 | 3.721% | -3.721%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 10.526 | 9.529 | 1.935 | -0.354 | 3.582% | -3.582%
18 | 10 | 2.031 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 10.526 | 9.647 | 1.959 | -0.353 | 3.53% | -3.53%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 10.526 | 9.613 | 1.952 | -0.353 | 3.542% | -3.542%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 10.526 | 9.502 | 1.93 | -0.355 | 3.602% | -3.602%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 10.526 | 9.263 | 1.881 | -0.357 | 3.711% | -3.711%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 10.526 | 8.779 | 1.783 | -0.36 | 3.939% | -3.939%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 10.526 | 8.186 | 1.662 | -0.361 | 4.224% | -4.224%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.97 | -2.499 | 0.97 | -2.499 | -5.465 | 10.526 | 7.689 | 1.561 | -0.358 | 4.449% | -4.449%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0369 | -1.0325 | 0.99876 | -2.9186 | 1.0237 | -0.90306 | 0.98634 | -2.8137 | -5.263 | 5.263 | 7.6148 | 3.5573 | -0.10121 | 1.312% | -1.312%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0241 | -0.87646 | 0.98777 | -2.7344 | -5.263 | 5.263 | 7.4184 | 3.4661 | -0.098585 | 1.311% | -1.311%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0243 | -0.86177 | 0.98855 | -2.6906 | -5.263 | 5.263 | 7.3098 | 3.4155 | -0.097206 | 1.312% | -1.312%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0243 | -0.86057 | 0.98862 | -2.6871 | -5.263 | 5.263 | 7.3009 | 3.4114 | -0.097093 | 1.312% | -1.312%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.024 | -0.88261 | 0.98744 | -2.7527 | -5.263 | 5.263 | 7.4638 | 3.4872 | -0.09916 | 1.311% | -1.311%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0231 | -0.93925 | 0.98438 | -2.9217 | -5.263 | 5.263 | 7.8816 | 3.6816 | -0.10444 | 1.308% | -1.308%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2525 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0218 | -1.0256 | 0.97973 | -3.1798 | -5.2525 | 5.2525 | 8.5139 | 3.976 | -0.11211 | 1.3% | -1.3%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1156 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 5.1156 | 8.969 | 4.2242 | -0.090001 | 0.9935% | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.7051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 4.7051 | 9.0898 | 4.2808 | -0.091187 | 0.9932% | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.142 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 4.142 | 9.1383 | 4.3036 | -0.091662 | 0.9931% | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5736 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0247 | -1.1577 | 0.97881 | -3.4856 | -3.5736 | 3.5736 | 9.1786 | 4.3353 | -0.082375 | 0.8895% | -0.8895%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.2578 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0254 | -1.1683 | 0.97934 | -3.4995 | -3.2578 | 3.2578 | 9.217 | 4.3636 | -0.075031 | 0.8075% | -0.8075%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.3525 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0251 | -1.1705 | 0.97889 | -3.5115 | -3.3525 | 3.3525 | 9.2445 | 4.3735 | -0.077549 | 0.8319% | -0.8319%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5052 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0247 | -1.1696 | 0.9784 | -3.5175 | -3.5052 | 3.5052 | 9.2566 | 4.3743 | -0.081369 | 0.8714% | -0.8714%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.942 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1698 | 0.97684 | -3.5431 | -3.942 | 3.942 | 9.3114 | 4.3858 | -0.09256 | 0.9843% | -0.9843%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.4578 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 4.4578 | 9.4988 | 4.4725 | -0.095187 | 0.9922% | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.9209 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 4.9209 | 9.785 | 4.6065 | -0.09798 | 0.9914% | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1893 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 5.1893 | 9.9009 | 4.6607 | -0.09911 | 0.9911% | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2577 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 5.2577 | 9.8672 | 4.645 | -0.098782 | 0.9912% | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 5.263 | 9.7593 | 4.5944 | -0.097732 | 0.9915% | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 5.263 | 9.5246 | 4.4845 | -0.09544 | 0.9921% | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 5.263 | 9.0482 | 4.2613 | -0.09078 | 0.9933% | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0219 | -1.0147 | 0.98028 | -3.1478 | -5.263 | 5.263 | 8.4356 | 3.9393 | -0.11137 | 1.303% | -1.303%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.023 | -0.94743 | 0.98394 | -2.9462 | -5.263 | 5.263 | 7.9418 | 3.7097 | -0.10519 | 1.307% | -1.307%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0236 | -0.90307 | 0.98633 | -2.8137 | -5.263 | 5.263 | 7.6149 | 3.5576 | -0.10107 | 1.31% | -1.31%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0241 | -0.87646 | 0.98777 | -2.7344 | -5.263 | 5.263 | 7.4184 | 3.4661 | -0.098585 | 1.311% | -1.311%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0243 | -0.86177 | 0.98855 | -2.6906 | -5.263 | 5.263 | 7.3098 | 3.4155 | -0.097206 | 1.312% | -1.312%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0243 | -0.86057 | 0.98862 | -2.6871 | -5.263 | 5.263 | 7.3009 | 3.4114 | -0.097093 | 1.312% | -1.312%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.024 | -0.88261 | 0.98744 | -2.7527 | -5.263 | 5.263 | 7.4638 | 3.4872 | -0.09916 | 1.311% | -1.311%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0231 | -0.93925 | 0.98438 | -2.9217 | -5.263 | 5.263 | 7.8816 | 3.6816 | -0.10444 | 1.308% | -1.308%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0218 | -1.0253 | 0.9797 | -3.1798 | -5.263 | 5.263 | 8.5137 | 3.9756 | -0.11235 | 1.302% | -1.302%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 5.2577 | 8.969 | 4.2242 | -0.090001 | 0.9935% | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 5.2051 | 9.0898 | 4.2808 | -0.091187 | 0.9932% | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 5.0946 | 9.1383 | 4.3036 | -0.091662 | 0.9931% | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 4.9788 | 9.169 | 4.318 | -0.091965 | 0.993% | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 4.9156 | 9.1997 | 4.3324 | -0.092264 | 0.9929% | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 4.9841 | 9.2294 | 4.3463 | -0.092556 | 0.9929% | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 5.0156 | 9.2453 | 4.3537 | -0.09271 | 0.9928% | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 5.1472 | 9.3106 | 4.3843 | -0.093351 | 0.9927% | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 5.2367 | 9.4988 | 4.4725 | -0.095187 | 0.9922% | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 5.263 | 9.785 | 4.6065 | -0.09798 | 0.9914% | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 5.263 | 9.9009 | 4.6607 | -0.09911 | 0.9911% | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 5.263 | 9.8672 | 4.645 | -0.098782 | 0.9912% | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 5.263 | 9.7593 | 4.5944 | -0.097732 | 0.9915% | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 5.263 | 9.5246 | 4.4845 | -0.09544 | 0.9921% | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 5.263 | 9.0482 | 4.2613 | -0.09078 | 0.9933% | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0219 | -1.0147 | 0.98028 | -3.1478 | -5.263 | 5.263 | 8.4356 | 3.9393 | -0.11137 | 1.303% | -1.303%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.023 | -0.94743 | 0.98394 | -2.9462 | -5.263 | 5.263 | 7.9418 | 3.7097 | -0.10519 | 1.307% | -1.307%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0236 | -0.90307 | 0.98633 | -2.8137 | -5.263 | 5.263 | 7.6149 | 3.5576 | -0.10107 | 1.31% | -1.31%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0241 | -0.87646 | 0.98777 | -2.7344 | -5.263 | 5.263 | 7.4184 | 3.4661 | -0.098585 | 1.311% | -1.311%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0243 | -0.86177 | 0.98855 | -2.6906 | -5.263 | 5.263 | 7.3098 | 3.4155 | -0.097206 | 1.312% | -1.312%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0243 | -0.86057 | 0.98862 | -2.6871 | -5.263 | 5.263 | 7.3009 | 3.4114 | -0.097093 | 1.312% | -1.312%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.024 | -0.88261 | 0.98744 | -2.7527 | -5.263 | 5.263 | 7.4638 | 3.4872 | -0.09916 | 1.311% | -1.311%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0231 | -0.93925 | 0.98438 | -2.9217 | -5.263 | 5.263 | 7.8816 | 3.6816 | -0.10444 | 1.308% | -1.308%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0218 | -1.0253 | 0.9797 | -3.1798 | -5.263 | 5.263 | 8.5137 | 3.9756 | -0.11235 | 1.302% | -1.302%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 5.263 | 8.969 | 4.2242 | -0.090001 | 0.9935% | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 5.263 | 9.0898 | 4.2808 | -0.091187 | 0.9932% | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 5.2577 | 9.1383 | 4.3036 | -0.091662 | 0.9931% | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2419 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 5.2419 | 9.169 | 4.318 | -0.091965 | 0.993% | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 5.2262 | 9.1997 | 4.3324 | -0.092264 | 0.9929% | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 5.2262 | 9.2294 | 4.3463 | -0.092556 | 0.9929% | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2367 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 5.2367 | 9.2453 | 4.3537 | -0.09271 | 0.9928% | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2525 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 5.2525 | 9.3106 | 4.3843 | -0.093351 | 0.9927% | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 5.2577 | 9.4988 | 4.4725 | -0.095187 | 0.9922% | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 5.263 | 9.785 | 4.6065 | -0.09798 | 0.9914% | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 5.263 | 9.9009 | 4.6607 | -0.09911 | 0.9911% | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 5.263 | 9.8672 | 4.645 | -0.098782 | 0.9912% | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 5.263 | 9.7593 | 4.5944 | -0.097732 | 0.9915% | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 5.263 | 9.5246 | 4.4845 | -0.09544 | 0.9921% | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 5.263 | 9.0482 | 4.2613 | -0.09078 | 0.9933% | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0219 | -1.0147 | 0.98028 | -3.1478 | -5.263 | 5.263 | 8.4356 | 3.9393 | -0.11137 | 1.303% | -1.303%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.023 | -0.94743 | 0.98394 | -2.9462 | -5.263 | 5.263 | 7.9418 | 3.7097 | -0.10519 | 1.307% | -1.307%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84817 | 0.97987 | -2.7949 | -7.8399 | 10.526 | 7.5623 | 3.4649 | -0.1537 | 1.992% | -1.992%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0103 | -0.75359 | 0.9747 | -2.661 | -10.526 | 10.526 | 7.315 | 3.2851 | -0.20199 | 2.687% | -2.687%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0105 | -0.73882 | 0.97547 | -2.6164 | -10.526 | 10.526 | 7.2079 | 3.2374 | -0.19914 | 2.689% | -2.689%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0105 | -0.73761 | 0.97554 | -2.6128 | -10.526 | 10.526 | 7.1991 | 3.2335 | -0.1989 | 2.689% | -2.689%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0102 | -0.75977 | 0.97437 | -2.6797 | -10.526 | 10.526 | 7.3598 | 3.3051 | -0.20319 | 2.687% | -2.687%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88453 | 0.97792 | -2.9046 | -7.8445 | 10.526 | 7.827 | 3.5852 | -0.15899 | 1.991% | -1.991%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5049 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97104 | 0.97324 | -3.1666 | -7.8559 | 10.5049 | 8.4545 | 3.8701 | -0.17149 | 1.988% | -1.988%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.2313 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 10.2313 | 8.969 | 4.2242 | -0.090001 | 0.9935% | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 9.4102 | 9.0898 | 4.2808 | -0.091187 | 0.9932% | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.284 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 8.284 | 9.1383 | 4.3036 | -0.091662 | 0.9931% | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.1472 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 7.1472 | 9.169 | 4.318 | -0.091965 | 0.993% | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.5156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 6.5156 | 9.1997 | 4.3324 | -0.092264 | 0.9929% | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.7051 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 6.7051 | 9.2294 | 4.3463 | -0.092556 | 0.9929% | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.0103 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 7.0103 | 9.2453 | 4.3537 | -0.09271 | 0.9928% | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.884 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 7.884 | 9.3106 | 4.3843 | -0.093351 | 0.9927% | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.9155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 8.9155 | 9.4988 | 4.4725 | -0.095187 | 0.9922% | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.8418 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 9.8418 | 9.785 | 4.6065 | -0.09798 | 0.9914% | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.3786 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 10.3786 | 9.9009 | 4.6607 | -0.09911 | 0.9911% | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5155 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 10.5155 | 9.8672 | 4.645 | -0.098782 | 0.9912% | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 10.526 | 9.7593 | 4.5944 | -0.097732 | 0.9915% | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 10.526 | 9.5246 | 4.4845 | -0.09544 | 0.9921% | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 10.526 | 9.0482 | 4.2613 | -0.09078 | 0.9933% | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96033 | 0.97382 | -3.1341 | -7.8546 | 10.526 | 8.377 | 3.8349 | -0.16995 | 1.988% | -1.988%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.89275 | 0.97747 | -2.9295 | -7.8456 | 10.526 | 7.8868 | 3.6124 | -0.16018 | 1.991% | -1.991%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84817 | 0.97987 | -2.7949 | -7.8399 | 10.526 | 7.5623 | 3.4649 | -0.1537 | 1.992% | -1.992%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0103 | -0.75359 | 0.9747 | -2.661 | -10.526 | 10.526 | 7.315 | 3.2851 | -0.20199 | 2.687% | -2.687%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0105 | -0.73882 | 0.97547 | -2.6164 | -10.526 | 10.526 | 7.2079 | 3.2374 | -0.19914 | 2.689% | -2.689%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0105 | -0.73761 | 0.97554 | -2.6128 | -10.526 | 10.526 | 7.1991 | 3.2335 | -0.1989 | 2.689% | -2.689%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0102 | -0.75977 | 0.97437 | -2.6797 | -10.526 | 10.526 | 7.3598 | 3.3051 | -0.20319 | 2.687% | -2.687%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88453 | 0.97792 | -2.9046 | -7.8445 | 10.526 | 7.827 | 3.5852 | -0.15899 | 1.991% | -1.991%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97104 | 0.97324 | -3.1666 | -7.8559 | 10.526 | 8.4545 | 3.8701 | -0.17149 | 1.988% | -1.988%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 10.5155 | 8.969 | 4.2242 | -0.090001 | 0.9935% | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 10.4102 | 9.0898 | 4.2808 | -0.091187 | 0.9932% | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 10.1892 | 9.1383 | 4.3036 | -0.091662 | 0.9931% | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 9.9576 | 9.169 | 4.318 | -0.091965 | 0.993% | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 9.8313 | 9.1997 | 4.3324 | -0.092264 | 0.9929% | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 9.9681 | 9.2294 | 4.3463 | -0.092556 | 0.9929% | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 10.0313 | 9.2453 | 4.3537 | -0.09271 | 0.9928% | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 10.2944 | 9.3106 | 4.3843 | -0.093351 | 0.9927% | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 10.4734 | 9.4988 | 4.4725 | -0.095187 | 0.9922% | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 10.526 | 9.785 | 4.6065 | -0.09798 | 0.9914% | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 10.526 | 9.9009 | 4.6607 | -0.09911 | 0.9911% | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 10.526 | 9.8672 | 4.645 | -0.098782 | 0.9912% | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 10.526 | 9.7593 | 4.5944 | -0.097732 | 0.9915% | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 10.526 | 9.5246 | 4.4845 | -0.09544 | 0.9921% | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 10.526 | 9.0482 | 4.2613 | -0.09078 | 0.9933% | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96033 | 0.97382 | -3.1341 | -7.8546 | 10.526 | 8.377 | 3.8349 | -0.16995 | 1.988% | -1.988%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.89275 | 0.97747 | -2.9295 | -7.8456 | 10.526 | 7.8868 | 3.6124 | -0.16018 | 1.991% | -1.991%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84817 | 0.97987 | -2.7949 | -7.8399 | 10.526 | 7.5623 | 3.4649 | -0.1537 | 1.992% | -1.992%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0103 | -0.75359 | 0.9747 | -2.661 | -10.526 | 10.526 | 7.315 | 3.2851 | -0.20199 | 2.687% | -2.687%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0105 | -0.73882 | 0.97547 | -2.6164 | -10.526 | 10.526 | 7.2079 | 3.2374 | -0.19914 | 2.689% | -2.689%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0105 | -0.73761 | 0.97554 | -2.6128 | -10.526 | 10.526 | 7.1991 | 3.2335 | -0.1989 | 2.689% | -2.689%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0102 | -0.75977 | 0.97437 | -2.6797 | -10.526 | 10.526 | 7.3598 | 3.3051 | -0.20319 | 2.687% | -2.687%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88453 | 0.97792 | -2.9046 | -7.8445 | 10.526 | 7.827 | 3.5852 | -0.15899 | 1.991% | -1.991%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97104 | 0.97324 | -3.1666 | -7.8559 | 10.526 | 8.4545 | 3.8701 | -0.17149 | 1.988% | -1.988%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 10.526 | 8.969 | 4.2242 | -0.090001 | 0.9935% | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 10.526 | 9.0898 | 4.2808 | -0.091187 | 0.9932% | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 10.5155 | 9.1383 | 4.3036 | -0.091662 | 0.9931% | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4839 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 10.4839 | 9.169 | 4.318 | -0.091965 | 0.993% | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 10.4523 | 9.1997 | 4.3324 | -0.092264 | 0.9929% | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 10.4523 | 9.2294 | 4.3463 | -0.092556 | 0.9929% | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4734 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 10.4734 | 9.2453 | 4.3537 | -0.09271 | 0.9928% | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5049 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 10.5049 | 9.3106 | 4.3843 | -0.093351 | 0.9927% | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 10.5155 | 9.4988 | 4.4725 | -0.095187 | 0.9922% | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 10.526 | 9.785 | 4.6065 | -0.09798 | 0.9914% | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 10.526 | 9.9009 | 4.6607 | -0.09911 | 0.9911% | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 10.526 | 9.8672 | 4.645 | -0.098782 | 0.9912% | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 10.526 | 9.7593 | 4.5944 | -0.097732 | 0.9915% | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 10.526 | 9.5246 | 4.4845 | -0.09544 | 0.9921% | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 10.526 | 9.0482 | 4.2613 | -0.09078 | 0.9933% | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96033 | 0.97382 | -3.1341 | -7.8546 | 10.526 | 8.377 | 3.8349 | -0.16995 | 1.988% | -1.988%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.89275 | 0.97747 | -2.9295 | -7.8456 | 10.526 | 7.8868 | 3.6124 | -0.16018 | 1.991% | -1.991%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 5.263 | 7.5579 | 3.4572 | -0.15809 | 2.049% | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99168 | -1.4701 | 0.97402 | -2.4415 | -5.263 | 5.263 | 7.3096 | 3.2758 | -0.20735 | 2.758% | -2.758%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99218 | -1.4415 | 0.9748 | -2.3975 | -5.263 | 5.263 | 7.2026 | 3.2283 | -0.20439 | 2.759% | -2.759%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99222 | -1.4392 | 0.97486 | -2.3939 | -5.263 | 5.263 | 7.1939 | 3.2244 | -0.20415 | 2.759% | -2.759%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99147 | -1.4821 | 0.97369 | -2.46 | -5.263 | 5.263 | 7.3544 | 3.2957 | -0.20859 | 2.758% | -2.758%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 5.263 | 7.8223 | 3.5769 | -0.16372 | 2.05% | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2525 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 5.2525 | 8.4489 | 3.8601 | -0.1771 | 2.053% | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1156 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 5.1156 | 8.9659 | 4.2186 | -0.093133 | 1.028% | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.7051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 4.7051 | 9.0866 | 4.275 | -0.094413 | 1.028% | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.142 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 4.142 | 9.1351 | 4.2977 | -0.094928 | 1.028% | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5736 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 3.5736 | 9.1657 | 4.312 | -0.095252 | 1.029% | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.2578 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 3.2578 | 9.1964 | 4.3263 | -0.095577 | 1.029% | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.3525 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 3.3525 | 9.2261 | 4.3402 | -0.095893 | 1.029% | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5052 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 3.5052 | 9.2419 | 4.3476 | -0.096062 | 1.029% | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.942 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 3.942 | 9.3072 | 4.3781 | -0.096754 | 1.029% | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.4578 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 4.4578 | 9.4953 | 4.466 | -0.098747 | 1.029% | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.9209 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 4.9209 | 9.7812 | 4.5995 | -0.10178 | 1.03% | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1893 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 5.1893 | 9.897 | 4.6536 | -0.10301 | 1.03% | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2577 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 5.2577 | 9.8633 | 4.6379 | -0.10266 | 1.03% | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 5.263 | 9.7555 | 4.5875 | -0.10151 | 1.03% | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 5.263 | 9.521 | 4.478 | -0.099021 | 1.029% | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 5.263 | 9.045 | 4.2556 | -0.093972 | 1.028% | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 5.263 | 8.3716 | 3.8252 | -0.17544 | 2.053% | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 5.263 | 7.882 | 3.6039 | -0.16499 | 2.05% | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 5.263 | 7.5579 | 3.4572 | -0.15809 | 2.049% | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99168 | -1.4701 | 0.97402 | -2.4415 | -5.263 | 5.263 | 7.3096 | 3.2758 | -0.20735 | 2.758% | -2.758%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99218 | -1.4415 | 0.9748 | -2.3975 | -5.263 | 5.263 | 7.2026 | 3.2283 | -0.20439 | 2.759% | -2.759%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99222 | -1.4392 | 0.97486 | -2.3939 | -5.263 | 5.263 | 7.1939 | 3.2244 | -0.20415 | 2.759% | -2.759%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99147 | -1.4821 | 0.97369 | -2.46 | -5.263 | 5.263 | 7.3544 | 3.2957 | -0.20859 | 2.758% | -2.758%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 5.263 | 7.8223 | 3.5769 | -0.16372 | 2.05% | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 5.263 | 8.4489 | 3.8601 | -0.1771 | 2.053% | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 5.2577 | 8.9659 | 4.2186 | -0.093133 | 1.028% | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 5.2051 | 9.0866 | 4.275 | -0.094413 | 1.028% | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 5.0946 | 9.1351 | 4.2977 | -0.094928 | 1.028% | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 4.9788 | 9.1657 | 4.312 | -0.095252 | 1.029% | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 4.9156 | 9.1964 | 4.3263 | -0.095577 | 1.029% | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 4.9841 | 9.2261 | 4.3402 | -0.095893 | 1.029% | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 5.0156 | 9.2419 | 4.3476 | -0.096062 | 1.029% | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 5.1472 | 9.3072 | 4.3781 | -0.096754 | 1.029% | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 5.2367 | 9.4953 | 4.466 | -0.098747 | 1.029% | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 5.263 | 9.7812 | 4.5995 | -0.10178 | 1.03% | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 5.263 | 9.897 | 4.6536 | -0.10301 | 1.03% | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 5.263 | 9.8633 | 4.6379 | -0.10266 | 1.03% | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 5.263 | 9.7555 | 4.5875 | -0.10151 | 1.03% | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 5.263 | 9.521 | 4.478 | -0.099021 | 1.029% | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 5.263 | 9.045 | 4.2556 | -0.093972 | 1.028% | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 5.263 | 8.3716 | 3.8252 | -0.17544 | 2.053% | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 5.263 | 7.882 | 3.6039 | -0.16499 | 2.05% | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 5.263 | 7.5579 | 3.4572 | -0.15809 | 2.049% | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99168 | -1.4701 | 0.97402 | -2.4415 | -5.263 | 5.263 | 7.3096 | 3.2758 | -0.20735 | 2.758% | -2.758%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99218 | -1.4415 | 0.9748 | -2.3975 | -5.263 | 5.263 | 7.2026 | 3.2283 | -0.20439 | 2.759% | -2.759%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99222 | -1.4392 | 0.97486 | -2.3939 | -5.263 | 5.263 | 7.1939 | 3.2244 | -0.20415 | 2.759% | -2.759%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99147 | -1.4821 | 0.97369 | -2.46 | -5.263 | 5.263 | 7.3544 | 3.2957 | -0.20859 | 2.758% | -2.758%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 5.263 | 7.8223 | 3.5769 | -0.16372 | 2.05% | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 5.263 | 8.4489 | 3.8601 | -0.1771 | 2.053% | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 5.263 | 8.9659 | 4.2186 | -0.093133 | 1.028% | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 5.263 | 9.0866 | 4.275 | -0.094413 | 1.028% | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 5.2577 | 9.1351 | 4.2977 | -0.094928 | 1.028% | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2419 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 5.2419 | 9.1657 | 4.312 | -0.095252 | 1.029% | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 5.2262 | 9.1964 | 4.3263 | -0.095577 | 1.029% | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 5.2262 | 9.2261 | 4.3402 | -0.095893 | 1.029% | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2367 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 5.2367 | 9.2419 | 4.3476 | -0.096062 | 1.029% | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2525 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 5.2525 | 9.3072 | 4.3781 | -0.096754 | 1.029% | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 5.2577 | 9.4953 | 4.466 | -0.098747 | 1.029% | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 5.263 | 9.7812 | 4.5995 | -0.10178 | 1.03% | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 5.263 | 9.897 | 4.6536 | -0.10301 | 1.03% | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 5.263 | 9.8633 | 4.6379 | -0.10266 | 1.03% | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 5.263 | 9.7555 | 4.5875 | -0.10151 | 1.03% | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 5.263 | 9.521 | 4.478 | -0.099021 | 1.029% | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 5.263 | 9.045 | 4.2556 | -0.093972 | 1.028% | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 5.263 | 8.3716 | 3.8252 | -0.17544 | 2.053% | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 5.263 | 7.882 | 3.6039 | -0.16499 | 2.05% | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 10.526 | 7.5579 | 3.4572 | -0.15809 | 2.049% | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.429 | 0.97106 | -2.4088 | -5.8247 | 10.526 | 7.2862 | 3.2351 | -0.23077 | 3.07% | -3.07%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4005 | 0.97185 | -2.3646 | -5.8215 | 10.526 | 7.1797 | 3.1885 | -0.22734 | 3.069% | -3.069%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.3982 | 0.97192 | -2.361 | -5.8213 | 10.526 | 7.1709 | 3.1847 | -0.22705 | 3.069% | -3.069%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4409 | 0.97073 | -2.4272 | -5.8258 | 10.526 | 7.3308 | 3.2546 | -0.23221 | 3.07% | -3.07%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 10.526 | 7.8223 | 3.5769 | -0.16372 | 2.05% | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5049 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 10.5049 | 8.4489 | 3.8601 | -0.1771 | 2.053% | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.2313 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 10.2313 | 8.9659 | 4.2186 | -0.093133 | 1.028% | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 9.4102 | 9.0866 | 4.275 | -0.094413 | 1.028% | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.284 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 8.284 | 9.1351 | 4.2977 | -0.094928 | 1.028% | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.1472 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 7.1472 | 9.1657 | 4.312 | -0.095252 | 1.029% | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.5156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 6.5156 | 9.1964 | 4.3263 | -0.095577 | 1.029% | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.7051 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 6.7051 | 9.2261 | 4.3402 | -0.095893 | 1.029% | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.0103 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 7.0103 | 9.2419 | 4.3476 | -0.096062 | 1.029% | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.884 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 7.884 | 9.3072 | 4.3781 | -0.096754 | 1.029% | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.9155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 8.9155 | 9.4953 | 4.466 | -0.098747 | 1.029% | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.8418 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 9.8418 | 9.7812 | 4.5995 | -0.10178 | 1.03% | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.3786 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 10.3786 | 9.897 | 4.6536 | -0.10301 | 1.03% | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5155 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 10.5155 | 9.8633 | 4.6379 | -0.10266 | 1.03% | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 10.526 | 9.7555 | 4.5875 | -0.10151 | 1.03% | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 10.526 | 9.521 | 4.478 | -0.099021 | 1.029% | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 10.526 | 9.045 | 4.2556 | -0.093972 | 1.028% | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 10.526 | 8.3716 | 3.8252 | -0.17544 | 2.053% | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 10.526 | 7.882 | 3.6039 | -0.16499 | 2.05% | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 10.526 | 7.5579 | 3.4572 | -0.15809 | 2.049% | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.429 | 0.97106 | -2.4088 | -5.8247 | 10.526 | 7.2862 | 3.2351 | -0.23077 | 3.07% | -3.07%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4005 | 0.97185 | -2.3646 | -5.8215 | 10.526 | 7.1797 | 3.1885 | -0.22734 | 3.069% | -3.069%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.3982 | 0.97192 | -2.361 | -5.8213 | 10.526 | 7.1709 | 3.1847 | -0.22705 | 3.069% | -3.069%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4409 | 0.97073 | -2.4272 | -5.8258 | 10.526 | 7.3308 | 3.2546 | -0.23221 | 3.07% | -3.07%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 10.526 | 7.8223 | 3.5769 | -0.16372 | 2.05% | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 10.526 | 8.4489 | 3.8601 | -0.1771 | 2.053% | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 10.5155 | 8.9659 | 4.2186 | -0.093133 | 1.028% | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 10.4102 | 9.0866 | 4.275 | -0.094413 | 1.028% | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 10.1892 | 9.1351 | 4.2977 | -0.094928 | 1.028% | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 9.9576 | 9.1657 | 4.312 | -0.095252 | 1.029% | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 9.8313 | 9.1964 | 4.3263 | -0.095577 | 1.029% | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 9.9681 | 9.2261 | 4.3402 | -0.095893 | 1.029% | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 10.0313 | 9.2419 | 4.3476 | -0.096062 | 1.029% | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 10.2944 | 9.3072 | 4.3781 | -0.096754 | 1.029% | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 10.4734 | 9.4953 | 4.466 | -0.098747 | 1.029% | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 10.526 | 9.7812 | 4.5995 | -0.10178 | 1.03% | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 10.526 | 9.897 | 4.6536 | -0.10301 | 1.03% | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 10.526 | 9.8633 | 4.6379 | -0.10266 | 1.03% | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 10.526 | 9.7555 | 4.5875 | -0.10151 | 1.03% | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 10.526 | 9.521 | 4.478 | -0.099021 | 1.029% | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 10.526 | 9.045 | 4.2556 | -0.093972 | 1.028% | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 10.526 | 8.3716 | 3.8252 | -0.17544 | 2.053% | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 10.526 | 7.882 | 3.6039 | -0.16499 | 2.05% | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 10.526 | 7.5579 | 3.4572 | -0.15809 | 2.049% | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.429 | 0.97106 | -2.4088 | -5.8247 | 10.526 | 7.2862 | 3.2351 | -0.23077 | 3.07% | -3.07%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4005 | 0.97185 | -2.3646 | -5.8215 | 10.526 | 7.1797 | 3.1885 | -0.22734 | 3.069% | -3.069%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.3982 | 0.97192 | -2.361 | -5.8213 | 10.526 | 7.1709 | 3.1847 | -0.22705 | 3.069% | -3.069%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4409 | 0.97073 | -2.4272 | -5.8258 | 10.526 | 7.3308 | 3.2546 | -0.23221 | 3.07% | -3.07%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 10.526 | 7.8223 | 3.5769 | -0.16372 | 2.05% | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 10.526 | 8.4489 | 3.8601 | -0.1771 | 2.053% | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 10.526 | 8.9659 | 4.2186 | -0.093133 | 1.028% | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 10.526 | 9.0866 | 4.275 | -0.094413 | 1.028% | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 10.5155 | 9.1351 | 4.2977 | -0.094928 | 1.028% | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4839 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 10.4839 | 9.1657 | 4.312 | -0.095252 | 1.029% | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 10.4523 | 9.1964 | 4.3263 | -0.095577 | 1.029% | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 10.4523 | 9.2261 | 4.3402 | -0.095893 | 1.029% | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4734 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 10.4734 | 9.2419 | 4.3476 | -0.096062 | 1.029% | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5049 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 10.5049 | 9.3072 | 4.3781 | -0.096754 | 1.029% | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 10.5155 | 9.4953 | 4.466 | -0.098747 | 1.029% | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 10.526 | 9.7812 | 4.5995 | -0.10178 | 1.03% | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 10.526 | 9.897 | 4.6536 | -0.10301 | 1.03% | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 10.526 | 9.8633 | 4.6379 | -0.10266 | 1.03% | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 10.526 | 9.7555 | 4.5875 | -0.10151 | 1.03% | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 10.526 | 9.521 | 4.478 | -0.099021 | 1.029% | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 10.526 | 9.045 | 4.2556 | -0.093972 | 1.028% | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 10.526 | 8.3716 | 3.8252 | -0.17544 | 2.053% | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 10.526 | 7.882 | 3.6039 | -0.16499 | 2.05% | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 5.263 | 7.4821 | 3.3248 | -0.23391 | 3.032% | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 5.263 | 7.2779 | 3.2206 | -0.23914 | 3.181% | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 5.263 | 7.1653 | 3.1636 | -0.24174 | 3.264% | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 5.263 | 7.1561 | 3.1589 | -0.24194 | 3.27% | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 5.263 | 7.325 | 3.2446 | -0.238 | 3.147% | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 5.263 | 7.7603 | 3.468 | -0.22573 | 2.827% | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2525 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 5.2525 | 8.4248 | 3.8173 | -0.20117 | 2.332% | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1156 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 5.1156 | 8.8787 | 4.0618 | -0.18034 | 1.991% | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.7051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 4.7051 | 9.0072 | 4.1319 | -0.17383 | 1.893% | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.142 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 4.142 | 9.0589 | 4.1602 | -0.17114 | 1.854% | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5736 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 3.5736 | 9.0916 | 4.1781 | -0.16942 | 1.829% | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.2578 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 3.2578 | 9.1243 | 4.1961 | -0.16767 | 1.804% | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.3525 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 3.3525 | 9.156 | 4.2136 | -0.16597 | 1.78% | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5052 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 3.5052 | 9.1729 | 4.2229 | -0.16505 | 1.768% | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.942 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 3.942 | 9.2428 | 4.2614 | -0.16122 | 1.714% | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.4578 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 4.4578 | 9.4443 | 4.3734 | -0.14972 | 1.561% | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.9209 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 4.9209 | 9.7521 | 4.5463 | -0.13089 | 1.324% | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1893 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 5.1893 | 9.8772 | 4.6173 | -0.1228 | 1.228% | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2577 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 5.2577 | 9.8408 | 4.5966 | -0.12518 | 1.256% | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 5.263 | 9.7243 | 4.5306 | -0.13265 | 1.346% | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 5.263 | 9.4719 | 4.3888 | -0.1481 | 1.539% | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 5.263 | 8.9629 | 4.1077 | -0.1761 | 1.927% | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 5.263 | 8.3424 | 3.7735 | -0.2046 | 2.394% | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 5.263 | 7.8233 | 3.5007 | -0.2237 | 2.78% | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 5.263 | 7.4821 | 3.3248 | -0.23392 | 3.032% | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 5.263 | 7.2779 | 3.2206 | -0.23914 | 3.181% | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 5.263 | 7.1653 | 3.1636 | -0.24174 | 3.264% | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 5.263 | 7.1561 | 3.1589 | -0.24194 | 3.27% | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 5.263 | 7.325 | 3.2446 | -0.238 | 3.147% | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 5.263 | 7.7603 | 3.468 | -0.22573 | 2.827% | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 5.263 | 8.4248 | 3.8173 | -0.20117 | 2.332% | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 5.2577 | 8.8787 | 4.0618 | -0.18034 | 1.991% | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 5.2051 | 9.0072 | 4.1319 | -0.17383 | 1.893% | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 5.0946 | 9.0589 | 4.1602 | -0.17114 | 1.854% | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 4.9788 | 9.0916 | 4.1781 | -0.16942 | 1.829% | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 4.9156 | 9.1243 | 4.1961 | -0.16767 | 1.804% | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 4.9841 | 9.156 | 4.2136 | -0.16597 | 1.78% | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 5.0156 | 9.1729 | 4.2229 | -0.16505 | 1.768% | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 5.1472 | 9.2428 | 4.2614 | -0.16122 | 1.714% | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 5.2367 | 9.4443 | 4.3734 | -0.14972 | 1.561% | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 5.263 | 9.7521 | 4.5463 | -0.13089 | 1.324% | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 5.263 | 9.8772 | 4.6173 | -0.1228 | 1.228% | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 5.263 | 9.8408 | 4.5966 | -0.12518 | 1.256% | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 5.263 | 9.7243 | 4.5306 | -0.13265 | 1.346% | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 5.263 | 9.4719 | 4.3888 | -0.1481 | 1.539% | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 5.263 | 8.9629 | 4.1077 | -0.1761 | 1.927% | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 5.263 | 8.3424 | 3.7735 | -0.2046 | 2.394% | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 5.263 | 7.8233 | 3.5007 | -0.2237 | 2.78% | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 5.263 | 7.4821 | 3.3248 | -0.23392 | 3.032% | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 5.263 | 7.2779 | 3.2206 | -0.23914 | 3.181% | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 5.263 | 7.1653 | 3.1636 | -0.24174 | 3.264% | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 5.263 | 7.1561 | 3.1589 | -0.24194 | 3.27% | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 5.263 | 7.325 | 3.2446 | -0.238 | 3.147% | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 5.263 | 7.7603 | 3.468 | -0.22573 | 2.827% | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 5.263 | 8.4248 | 3.8173 | -0.20117 | 2.332% | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 5.263 | 8.8787 | 4.0618 | -0.18034 | 1.991% | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 5.263 | 9.0072 | 4.1319 | -0.17383 | 1.893% | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 5.2577 | 9.0589 | 4.1602 | -0.17114 | 1.854% | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2419 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 5.2419 | 9.0916 | 4.1781 | -0.16942 | 1.829% | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 5.2262 | 9.1243 | 4.1961 | -0.16767 | 1.804% | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 5.2262 | 9.156 | 4.2136 | -0.16597 | 1.78% | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2367 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 5.2367 | 9.1729 | 4.2229 | -0.16505 | 1.768% | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2525 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 5.2525 | 9.2428 | 4.2614 | -0.16122 | 1.714% | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 5.2577 | 9.4443 | 4.3734 | -0.14972 | 1.561% | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 5.263 | 9.7521 | 4.5463 | -0.13089 | 1.324% | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 5.263 | 9.8772 | 4.6173 | -0.1228 | 1.228% | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 5.263 | 9.8408 | 4.5966 | -0.12518 | 1.256% | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 5.263 | 9.7243 | 4.5306 | -0.13265 | 1.346% | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 5.263 | 9.4719 | 4.3888 | -0.1481 | 1.539% | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 5.263 | 8.9629 | 4.1077 | -0.1761 | 1.927% | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 5.263 | 8.3424 | 3.7735 | -0.2046 | 2.394% | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 5.263 | 7.8233 | 3.5007 | -0.2237 | 2.78% | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 10.526 | 7.4821 | 3.3248 | -0.23392 | 3.032% | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 10.526 | 7.2779 | 3.2206 | -0.23914 | 3.181% | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 10.526 | 7.1653 | 3.1636 | -0.24174 | 3.264% | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 10.526 | 7.1561 | 3.1589 | -0.24194 | 3.27% | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 10.526 | 7.325 | 3.2446 | -0.238 | 3.147% | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 10.526 | 7.7603 | 3.468 | -0.22573 | 2.827% | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5049 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 10.5049 | 8.4248 | 3.8173 | -0.20117 | 2.332% | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.2313 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 10.2313 | 8.8787 | 4.0618 | -0.18034 | 1.991% | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 9.4102 | 9.0072 | 4.1319 | -0.17383 | 1.893% | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.284 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 8.284 | 9.0589 | 4.1602 | -0.17114 | 1.854% | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.1472 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 7.1472 | 9.0916 | 4.1781 | -0.16942 | 1.829% | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.5156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 6.5156 | 9.1243 | 4.1961 | -0.16767 | 1.804% | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.7051 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 6.7051 | 9.156 | 4.2136 | -0.16597 | 1.78% | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.0103 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 7.0103 | 9.1729 | 4.2229 | -0.16505 | 1.768% | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.884 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 7.884 | 9.2428 | 4.2614 | -0.16122 | 1.714% | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.9155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 8.9155 | 9.4443 | 4.3734 | -0.14972 | 1.561% | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.8418 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 9.8418 | 9.7521 | 4.5463 | -0.13089 | 1.324% | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.3786 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 10.3786 | 9.8772 | 4.6173 | -0.1228 | 1.228% | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5155 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 10.5155 | 9.8408 | 4.5966 | -0.12518 | 1.256% | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 10.526 | 9.7243 | 4.5306 | -0.13265 | 1.346% | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 10.526 | 9.4719 | 4.3888 | -0.1481 | 1.539% | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 10.526 | 8.9629 | 4.1077 | -0.1761 | 1.927% | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 10.526 | 8.3424 | 3.7735 | -0.2046 | 2.394% | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 10.526 | 7.8233 | 3.5007 | -0.2237 | 2.78% | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 10.526 | 7.4821 | 3.3248 | -0.23392 | 3.032% | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 10.526 | 7.2779 | 3.2206 | -0.23914 | 3.181% | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 10.526 | 7.1653 | 3.1636 | -0.24174 | 3.264% | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 10.526 | 7.1561 | 3.1589 | -0.24194 | 3.27% | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 10.526 | 7.325 | 3.2446 | -0.238 | 3.147% | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 10.526 | 7.7603 | 3.468 | -0.22573 | 2.827% | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 10.526 | 8.4248 | 3.8173 | -0.20117 | 2.332% | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 10.5155 | 8.8787 | 4.0618 | -0.18034 | 1.991% | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 10.4102 | 9.0072 | 4.1319 | -0.17383 | 1.893% | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 10.1892 | 9.0589 | 4.1602 | -0.17114 | 1.854% | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 9.9576 | 9.0916 | 4.1781 | -0.16942 | 1.829% | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 9.8313 | 9.1243 | 4.1961 | -0.16767 | 1.804% | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 9.9681 | 9.156 | 4.2136 | -0.16597 | 1.78% | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 10.0313 | 9.1729 | 4.2229 | -0.16505 | 1.768% | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 10.2944 | 9.2428 | 4.2614 | -0.16122 | 1.714% | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 10.4734 | 9.4443 | 4.3734 | -0.14972 | 1.561% | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 10.526 | 9.7521 | 4.5463 | -0.13089 | 1.324% | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 10.526 | 9.8772 | 4.6173 | -0.1228 | 1.228% | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 10.526 | 9.8408 | 4.5966 | -0.12518 | 1.256% | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 10.526 | 9.7243 | 4.5306 | -0.13265 | 1.346% | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 10.526 | 9.4719 | 4.3888 | -0.1481 | 1.539% | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 10.526 | 8.9629 | 4.1077 | -0.1761 | 1.927% | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 10.526 | 8.3424 | 3.7735 | -0.2046 | 2.394% | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 10.526 | 7.8233 | 3.5007 | -0.2237 | 2.78% | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 10.526 | 7.4821 | 3.3248 | -0.23392 | 3.032% | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 10.526 | 7.2779 | 3.2206 | -0.23914 | 3.181% | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 10.526 | 7.1653 | 3.1636 | -0.24174 | 3.264% | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 10.526 | 7.1561 | 3.1589 | -0.24194 | 3.27% | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 10.526 | 7.325 | 3.2446 | -0.238 | 3.147% | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 10.526 | 7.7603 | 3.468 | -0.22573 | 2.827% | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 10.526 | 8.4248 | 3.8173 | -0.20117 | 2.332% | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 10.526 | 8.8787 | 4.0618 | -0.18034 | 1.991% | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 10.526 | 9.0072 | 4.1319 | -0.17383 | 1.893% | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 10.5155 | 9.0589 | 4.1602 | -0.17114 | 1.854% | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4839 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 10.4839 | 9.0916 | 4.1781 | -0.16942 | 1.829% | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 10.4523 | 9.1243 | 4.1961 | -0.16767 | 1.804% | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 10.4523 | 9.156 | 4.2136 | -0.16597 | 1.78% | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4734 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 10.4734 | 9.1729 | 4.2229 | -0.16505 | 1.768% | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5049 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 10.5049 | 9.2428 | 4.2614 | -0.16122 | 1.714% | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 10.5155 | 9.4443 | 4.3734 | -0.14972 | 1.561% | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 10.526 | 9.7521 | 4.5463 | -0.13089 | 1.324% | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 10.526 | 9.8772 | 4.6173 | -0.1228 | 1.228% | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 10.526 | 9.8408 | 4.5966 | -0.12518 | 1.256% | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 10.526 | 9.7243 | 4.5306 | -0.13265 | 1.346% | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 10.526 | 9.4719 | 4.3888 | -0.1481 | 1.539% | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 10.526 | 8.9629 | 4.1077 | -0.1761 | 1.927% | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 10.526 | 8.3424 | 3.7735 | -0.2046 | 2.394% | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 10.526 | 7.8233 | 3.5007 | -0.2237 | 2.78% | -2.78%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0268 | -0.9258 | 0.9961 | -2.9536 | -5.263 | 5.263 | 7.6133 | 2.4147 | -0.10274 | 1.331% | -1.331%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0271 | -0.89874 | 0.99726 | -2.8714 | -5.263 | 5.263 | 7.4169 | 2.3526 | -0.10013 | 1.332% | -1.332%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0273 | -0.8838 | 0.9979 | -2.826 | -5.263 | 5.263 | 7.3083 | 2.3183 | -0.098697 | 1.332% | -1.332%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0273 | -0.88258 | 0.99795 | -2.8223 | -5.263 | 5.263 | 7.2994 | 2.3155 | -0.098578 | 1.332% | -1.332%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0271 | -0.90499 | 0.99699 | -2.8904 | -5.263 | 5.263 | 7.4623 | 2.367 | -0.10072 | 1.332% | -1.332%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0264 | -0.96257 | 0.99452 | -3.0655 | -5.263 | 5.263 | 7.8798 | 2.4989 | -0.10621 | 1.33% | -1.33%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2525 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0255 | -1.0469 | 0.9909 | -3.3202 | -5.2525 | 5.2525 | 8.513 | 2.7002 | -0.11304 | 1.31% | -1.31%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1156 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0251 | -1.1093 | 0.98865 | -3.5035 | -5.1156 | 5.1156 | 8.9437 | 2.8391 | -0.11528 | 1.273% | -1.273%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.7051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.026 | -1.1358 | 0.98892 | -3.5611 | -4.7051 | 4.7051 | 9.074 | 2.8889 | -0.10702 | 1.166% | -1.166%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.142 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0273 | -1.1563 | 0.98999 | -3.5918 | -4.142 | 4.142 | 9.1357 | 2.9202 | -0.094298 | 1.022% | -1.022%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5736 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0286 | -1.1839 | 0.99088 | -3.6483 | -3.5736 | 3.5736 | 9.1769 | 2.9426 | -0.084109 | 0.9082% | -0.9082%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.2578 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0293 | -1.1947 | 0.99148 | -3.663 | -3.2578 | 3.2578 | 9.2154 | 2.9617 | -0.076616 | 0.8245% | -0.8245%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.3525 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0292 | -1.1872 | 0.99138 | -3.6411 | -3.3525 | 3.3525 | 9.2459 | 2.9722 | -0.076101 | 0.8164% | -0.8164%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5052 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0288 | -1.1858 | 0.99091 | -3.6455 | -3.5052 | 3.5052 | 9.2581 | 2.9729 | -0.079887 | 0.8555% | -0.8555%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.942 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0274 | -1.1961 | 0.98907 | -3.7072 | -3.942 | 3.942 | 9.3094 | 2.9767 | -0.094642 | 1.006% | -1.006%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.4578 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0259 | -1.1984 | 0.98703 | -3.7388 | -4.4578 | 4.4578 | 9.4885 | 3.0259 | -0.10548 | 1.099% | -1.099%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.9209 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0242 | -1.23 | 0.98403 | -3.8646 | -4.9209 | 4.9209 | 9.7616 | 3.1011 | -0.12144 | 1.229% | -1.229%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1893 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0233 | -1.2406 | 0.98262 | -3.9137 | -5.1893 | 5.1893 | 9.8699 | 3.1289 | -0.13007 | 1.301% | -1.301%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2577 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0232 | -1.2345 | 0.98266 | -3.899 | -5.2577 | 5.2577 | 9.8345 | 3.1161 | -0.13149 | 1.319% | -1.319%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0233 | -1.2193 | 0.98331 | -3.8525 | -5.263 | 5.263 | 9.7268 | 3.082 | -0.13025 | 1.321% | -1.321%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0237 | -1.1866 | 0.98476 | -3.7516 | -5.263 | 5.263 | 9.4928 | 3.0082 | -0.12723 | 1.323% | -1.323%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0245 | -1.1204 | 0.98767 | -3.548 | -5.263 | 5.263 | 9.0179 | 2.8584 | -0.12108 | 1.325% | -1.325%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0255 | -1.0392 | 0.99121 | -3.2994 | -5.263 | 5.263 | 8.4335 | 2.6739 | -0.11346 | 1.328% | -1.328%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0263 | -0.97089 | 0.99416 | -3.0909 | -5.263 | 5.263 | 7.94 | 2.518 | -0.107 | 1.33% | -1.33%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0268 | -0.9258 | 0.9961 | -2.9536 | -5.263 | 5.263 | 7.6133 | 2.4147 | -0.10271 | 1.331% | -1.331%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0271 | -0.89874 | 0.99726 | -2.8714 | -5.263 | 5.263 | 7.4169 | 2.3526 | -0.10013 | 1.332% | -1.332%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0273 | -0.8838 | 0.9979 | -2.826 | -5.263 | 5.263 | 7.3083 | 2.3183 | -0.098697 | 1.332% | -1.332%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0273 | -0.88258 | 0.99795 | -2.8223 | -5.263 | 5.263 | 7.2994 | 2.3155 | -0.098578 | 1.332% | -1.332%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0271 | -0.90499 | 0.99699 | -2.8904 | -5.263 | 5.263 | 7.4623 | 2.367 | -0.10072 | 1.332% | -1.332%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0264 | -0.96257 | 0.99452 | -3.0655 | -5.263 | 5.263 | 7.8798 | 2.4989 | -0.10621 | 1.33% | -1.33%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0254 | -1.05 | 0.99074 | -3.3324 | -5.263 | 5.263 | 8.5115 | 2.6985 | -0.11448 | 1.327% | -1.327%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0247 | -1.1095 | 0.98816 | -3.5143 | -5.2577 | 5.2577 | 8.9391 | 2.8336 | -0.11992 | 1.324% | -1.324%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0246 | -1.1274 | 0.98756 | -3.5661 | -5.2051 | 5.2051 | 9.0608 | 2.8732 | -0.12018 | 1.309% | -1.309%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0249 | -1.1333 | 0.98767 | -3.5757 | -5.0946 | 5.0946 | 9.1131 | 2.8932 | -0.11686 | 1.266% | -1.266%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0251 | -1.1403 | 0.98777 | -3.5905 | -4.9788 | 4.9788 | 9.1465 | 2.9062 | -0.11446 | 1.236% | -1.236%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0252 | -1.146 | 0.98774 | -3.6045 | -4.9156 | 4.9156 | 9.1787 | 2.9177 | -0.11331 | 1.219% | -1.219%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.025 | -1.1485 | 0.98739 | -3.6161 | -4.9841 | 4.9841 | 9.2067 | 2.9251 | -0.11531 | 1.237% | -1.237%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0249 | -1.15 | 0.98721 | -3.6224 | -5.0156 | 5.0156 | 9.2217 | 2.9292 | -0.11626 | 1.245% | -1.245%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0245 | -1.1559 | 0.98649 | -3.6482 | -5.1472 | 5.1472 | 9.2837 | 2.946 | -0.12025 | 1.279% | -1.279%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0239 | -1.1799 | 0.98512 | -3.727 | -5.2367 | 5.2367 | 9.4692 | 3.0026 | -0.1248 | 1.301% | -1.301%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0233 | -1.2229 | 0.98315 | -3.8635 | -5.263 | 5.263 | 9.7524 | 3.0901 | -0.13058 | 1.321% | -1.321%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.2391 | 0.98243 | -3.9135 | -5.263 | 5.263 | 9.8679 | 3.1265 | -0.13206 | 1.321% | -1.321%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0231 | -1.2344 | 0.98264 | -3.8989 | -5.263 | 5.263 | 9.8344 | 3.1159 | -0.13163 | 1.321% | -1.321%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0233 | -1.2193 | 0.98331 | -3.8525 | -5.263 | 5.263 | 9.7268 | 3.082 | -0.13025 | 1.321% | -1.321%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0237 | -1.1866 | 0.98476 | -3.7516 | -5.263 | 5.263 | 9.4928 | 3.0082 | -0.12723 | 1.323% | -1.323%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0245 | -1.1204 | 0.98767 | -3.548 | -5.263 | 5.263 | 9.0179 | 2.8584 | -0.12108 | 1.325% | -1.325%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0255 | -1.0392 | 0.99121 | -3.2994 | -5.263 | 5.263 | 8.4335 | 2.6739 | -0.11346 | 1.328% | -1.328%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0263 | -0.97089 | 0.99416 | -3.0909 | -5.263 | 5.263 | 7.94 | 2.518 | -0.107 | 1.33% | -1.33%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0268 | -0.9258 | 0.9961 | -2.9536 | -5.263 | 5.263 | 7.6133 | 2.4147 | -0.10271 | 1.331% | -1.331%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0271 | -0.89874 | 0.99726 | -2.8714 | -5.263 | 5.263 | 7.4169 | 2.3526 | -0.10013 | 1.332% | -1.332%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0273 | -0.8838 | 0.9979 | -2.826 | -5.263 | 5.263 | 7.3083 | 2.3183 | -0.098697 | 1.332% | -1.332%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0273 | -0.88258 | 0.99795 | -2.8223 | -5.263 | 5.263 | 7.2994 | 2.3155 | -0.098578 | 1.332% | -1.332%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0271 | -0.90499 | 0.99699 | -2.8904 | -5.263 | 5.263 | 7.4623 | 2.367 | -0.10072 | 1.332% | -1.332%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0264 | -0.96257 | 0.99452 | -3.0655 | -5.263 | 5.263 | 7.8798 | 2.4989 | -0.10621 | 1.33% | -1.33%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0254 | -1.05 | 0.99074 | -3.3324 | -5.263 | 5.263 | 8.5115 | 2.6985 | -0.11448 | 1.327% | -1.327%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0247 | -1.1094 | 0.98815 | -3.5143 | -5.263 | 5.263 | 8.939 | 2.8335 | -0.12005 | 1.325% | -1.325%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0245 | -1.1262 | 0.98742 | -3.5658 | -5.263 | 5.263 | 9.0594 | 2.8715 | -0.12161 | 1.325% | -1.325%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0244 | -1.133 | 0.98713 | -3.5865 | -5.2577 | 5.2577 | 9.1079 | 2.8869 | -0.12211 | 1.323% | -1.323%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2419 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0244 | -1.1376 | 0.98699 | -3.5997 | -5.2419 | 5.2419 | 9.1389 | 2.897 | -0.12211 | 1.319% | -1.319%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0244 | -1.1422 | 0.98684 | -3.6128 | -5.2262 | 5.2262 | 9.1699 | 2.9071 | -0.12211 | 1.314% | -1.314%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0243 | -1.1463 | 0.98666 | -3.6255 | -5.2262 | 5.2262 | 9.1995 | 2.9165 | -0.12249 | 1.314% | -1.314%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2367 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0243 | -1.1447 | 0.98667 | -3.619 | -5.2367 | 5.2367 | 9.2164 | 2.9228 | -0.12161 | 1.302% | -1.302%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2525 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0242 | -1.1534 | 0.98623 | -3.6466 | -5.2525 | 5.2525 | 9.2812 | 2.9429 | -0.12282 | 1.306% | -1.306%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0238 | -1.1831 | 0.98493 | -3.7406 | -5.2577 | 5.2577 | 9.4672 | 3.0003 | -0.12676 | 1.321% | -1.321%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0233 | -1.2229 | 0.98315 | -3.8635 | -5.263 | 5.263 | 9.7524 | 3.0901 | -0.13058 | 1.321% | -1.321%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.2391 | 0.98243 | -3.9135 | -5.263 | 5.263 | 9.8679 | 3.1265 | -0.13206 | 1.321% | -1.321%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0231 | -1.2344 | 0.98264 | -3.8989 | -5.263 | 5.263 | 9.8344 | 3.1159 | -0.13163 | 1.321% | -1.321%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0233 | -1.2193 | 0.98331 | -3.8525 | -5.263 | 5.263 | 9.7268 | 3.082 | -0.13025 | 1.321% | -1.321%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0237 | -1.1866 | 0.98476 | -3.7516 | -5.263 | 5.263 | 9.4928 | 3.0082 | -0.12723 | 1.323% | -1.323%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0245 | -1.1204 | 0.98767 | -3.548 | -5.263 | 5.263 | 9.0179 | 2.8584 | -0.12108 | 1.325% | -1.325%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0255 | -1.0392 | 0.99121 | -3.2994 | -5.263 | 5.263 | 8.4335 | 2.6739 | -0.11346 | 1.328% | -1.328%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0263 | -0.97089 | 0.99416 | -3.0909 | -5.263 | 5.263 | 7.94 | 2.518 | -0.107 | 1.33% | -1.33%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.013 | -0.80234 | 0.98272 | -2.8768 | -10.526 | 10.526 | 7.5055 | 2.2887 | -0.21055 | 2.729% | -2.729%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0133 | -0.77517 | 0.98386 | -2.7932 | -10.526 | 10.526 | 7.3118 | 2.2301 | -0.20519 | 2.73% | -2.73%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0135 | -0.76016 | 0.98449 | -2.747 | -10.526 | 10.526 | 7.2048 | 2.1977 | -0.20223 | 2.73% | -2.73%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0135 | -0.75894 | 0.98454 | -2.7433 | -10.526 | 10.526 | 7.196 | 2.1951 | -0.20198 | 2.73% | -2.73%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0132 | -0.78145 | 0.98359 | -2.8125 | -10.526 | 10.526 | 7.3566 | 2.2437 | -0.20643 | 2.729% | -2.729%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0126 | -0.83927 | 0.98116 | -2.9907 | -10.526 | 10.526 | 7.7682 | 2.3682 | -0.21781 | 2.727% | -2.727%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5049 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0116 | -0.92754 | 0.97748 | -3.2624 | -10.5049 | 10.5049 | 8.3915 | 2.5569 | -0.23449 | 2.718% | -2.718%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.2313 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0116 | -0.99302 | 0.97565 | -3.4488 | -10.2313 | 10.2313 | 8.8198 | 2.692 | -0.23923 | 2.641% | -2.641%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0136 | -1.0273 | 0.97707 | -3.5049 | -9.4102 | 9.4102 | 8.9594 | 2.7525 | -0.22164 | 2.414% | -2.414%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.284 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0166 | -1.058 | 0.97972 | -3.5309 | -8.284 | 8.284 | 9.0358 | 2.801 | -0.19417 | 2.104% | -2.104%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.1472 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0194 | -1.0979 | 0.98211 | -3.5907 | -7.1472 | 7.1472 | 9.0913 | 2.8402 | -0.16974 | 1.833% | -1.833%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.5156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.021 | -1.1153 | 0.98354 | -3.6068 | -6.5156 | 6.5156 | 9.1375 | 2.8685 | -0.15446 | 1.662% | -1.662%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.7051 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0206 | -1.1074 | 0.98315 | -3.5897 | -6.7051 | 6.7051 | 9.165 | 2.8752 | -0.157 | 1.684% | -1.684%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.0103 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0198 | -1.1023 | 0.98229 | -3.5917 | -7.0103 | 7.0103 | 9.1733 | 2.8713 | -0.16471 | 1.764% | -1.764%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.884 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1039 | 0.97954 | -3.6489 | -7.8127 | 7.884 | 9.2148 | 2.8636 | -0.18921 | 2.012% | -2.012%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.9155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1302 | 0.97839 | -3.7306 | -7.8146 | 8.9155 | 9.401 | 2.9209 | -0.19302 | 2.012% | -2.012%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.8418 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1703 | 0.97662 | -3.8552 | -7.8176 | 9.8418 | 9.6842 | 3.0081 | -0.19882 | 2.012% | -2.012%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.3786 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1866 | 0.97591 | -3.9059 | -7.8188 | 10.3786 | 9.7988 | 3.0433 | -0.20117 | 2.012% | -2.012%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5155 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1818 | 0.97611 | -3.8912 | -7.8185 | 10.5155 | 9.7655 | 3.0331 | -0.20048 | 2.012% | -2.012%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1667 | 0.97678 | -3.844 | -7.8173 | 10.526 | 9.6587 | 3.0002 | -0.1983 | 2.012% | -2.012%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1338 | 0.97823 | -3.7418 | -7.8148 | 10.526 | 9.4265 | 2.9288 | -0.19354 | 2.012% | -2.012%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0107 | -0.99778 | 0.9744 | -3.4817 | -10.526 | 10.526 | 8.8903 | 2.7068 | -0.24871 | 2.721% | -2.721%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0117 | -0.91623 | 0.97789 | -3.2286 | -10.526 | 10.526 | 8.3141 | 2.5331 | -0.23287 | 2.725% | -2.725%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0125 | -0.84762 | 0.9808 | -3.0165 | -10.526 | 10.526 | 7.8275 | 2.3861 | -0.21945 | 2.727% | -2.727%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.013 | -0.80234 | 0.98272 | -2.8768 | -10.526 | 10.526 | 7.5055 | 2.2887 | -0.21055 | 2.729% | -2.729%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0133 | -0.77517 | 0.98386 | -2.7932 | -10.526 | 10.526 | 7.3118 | 2.2301 | -0.20519 | 2.73% | -2.73%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0135 | -0.76016 | 0.98449 | -2.747 | -10.526 | 10.526 | 7.2048 | 2.1977 | -0.20223 | 2.73% | -2.73%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0135 | -0.75894 | 0.98454 | -2.7433 | -10.526 | 10.526 | 7.196 | 2.1951 | -0.20198 | 2.73% | -2.73%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0132 | -0.78145 | 0.98359 | -2.8125 | -10.526 | 10.526 | 7.3566 | 2.2437 | -0.20643 | 2.729% | -2.729%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0126 | -0.83927 | 0.98116 | -2.9907 | -10.526 | 10.526 | 7.7682 | 2.3682 | -0.21781 | 2.727% | -2.727%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0115 | -0.92709 | 0.97743 | -3.2623 | -10.526 | 10.526 | 8.391 | 2.5563 | -0.23498 | 2.724% | -2.724%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0109 | -0.98696 | 0.9749 | -3.4474 | -10.5155 | 10.5155 | 8.8127 | 2.6837 | -0.24631 | 2.719% | -2.719%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.011 | -1.006 | 0.97445 | -3.5003 | -10.4102 | 10.4102 | 8.9341 | 2.7226 | -0.24691 | 2.689% | -2.689%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0115 | -1.0175 | 0.97474 | -3.5223 | -10.1892 | 10.1892 | 8.9874 | 2.7436 | -0.24259 | 2.628% | -2.628%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.012 | -1.0267 | 0.97516 | -3.5366 | -9.9576 | 9.9576 | 9.0235 | 2.7597 | -0.23748 | 2.564% | -2.564%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0123 | -1.0336 | 0.97531 | -3.5505 | -9.8313 | 9.8313 | 9.057 | 2.7727 | -0.23503 | 2.529% | -2.529%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0119 | -1.0349 | 0.97477 | -3.5627 | -9.9681 | 9.9681 | 9.0827 | 2.7774 | -0.23928 | 2.567% | -2.567%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0947 | 0.97994 | -3.6206 | -7.8118 | 10.0313 | 9.1501 | 2.8437 | -0.18788 | 2.012% | -2.012%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1039 | 0.97954 | -3.6489 | -7.8127 | 10.2944 | 9.2148 | 2.8636 | -0.18921 | 2.012% | -2.012%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1302 | 0.97839 | -3.7306 | -7.8146 | 10.4734 | 9.401 | 2.9209 | -0.19302 | 2.012% | -2.012%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1703 | 0.97662 | -3.8552 | -7.8176 | 10.526 | 9.6842 | 3.0081 | -0.19882 | 2.012% | -2.012%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1866 | 0.97591 | -3.9059 | -7.8188 | 10.526 | 9.7988 | 3.0433 | -0.20117 | 2.012% | -2.012%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1818 | 0.97611 | -3.8912 | -7.8185 | 10.526 | 9.7655 | 3.0331 | -0.20048 | 2.012% | -2.012%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1667 | 0.97678 | -3.844 | -7.8173 | 10.526 | 9.6587 | 3.0002 | -0.1983 | 2.012% | -2.012%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1338 | 0.97823 | -3.7418 | -7.8148 | 10.526 | 9.4265 | 2.9288 | -0.19354 | 2.012% | -2.012%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0107 | -0.99778 | 0.9744 | -3.4817 | -10.526 | 10.526 | 8.8903 | 2.7068 | -0.24871 | 2.721% | -2.721%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0117 | -0.91623 | 0.97789 | -3.2286 | -10.526 | 10.526 | 8.3141 | 2.5331 | -0.23287 | 2.725% | -2.725%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0125 | -0.84762 | 0.9808 | -3.0165 | -10.526 | 10.526 | 7.8275 | 2.3861 | -0.21945 | 2.727% | -2.727%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.013 | -0.80234 | 0.98272 | -2.8768 | -10.526 | 10.526 | 7.5055 | 2.2887 | -0.21055 | 2.729% | -2.729%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0133 | -0.77517 | 0.98386 | -2.7932 | -10.526 | 10.526 | 7.3118 | 2.2301 | -0.20519 | 2.73% | -2.73%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0135 | -0.76016 | 0.98449 | -2.747 | -10.526 | 10.526 | 7.2048 | 2.1977 | -0.20223 | 2.73% | -2.73%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0135 | -0.75894 | 0.98454 | -2.7433 | -10.526 | 10.526 | 7.196 | 2.1951 | -0.20198 | 2.73% | -2.73%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0132 | -0.78145 | 0.98359 | -2.8125 | -10.526 | 10.526 | 7.3566 | 2.2437 | -0.20643 | 2.729% | -2.729%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0126 | -0.83927 | 0.98116 | -2.9907 | -10.526 | 10.526 | 7.7682 | 2.3682 | -0.21781 | 2.727% | -2.727%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0115 | -0.92709 | 0.97743 | -3.2623 | -10.526 | 10.526 | 8.391 | 2.5563 | -0.23498 | 2.724% | -2.724%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0108 | -0.98674 | 0.97488 | -3.4474 | -10.526 | 10.526 | 8.8124 | 2.6834 | -0.24657 | 2.722% | -2.722%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0106 | -1.0036 | 0.97415 | -3.4997 | -10.526 | 10.526 | 8.9312 | 2.7191 | -0.24983 | 2.721% | -2.721%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0106 | -1.0106 | 0.97389 | -3.5208 | -10.5155 | 10.5155 | 8.9791 | 2.7338 | -0.25088 | 2.718% | -2.718%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4839 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0106 | -1.0155 | 0.97379 | -3.5343 | -10.4839 | 10.4839 | 9.0101 | 2.7439 | -0.2509 | 2.709% | -2.709%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0107 | -1.0205 | 0.97368 | -3.5478 | -10.4523 | 10.4523 | 9.0411 | 2.7539 | -0.25091 | 2.7% | -2.7%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0106 | -1.0246 | 0.97351 | -3.5607 | -10.4523 | 10.4523 | 9.0703 | 2.7627 | -0.25171 | 2.7% | -2.7%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4734 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0947 | 0.97994 | -3.6206 | -7.8118 | 10.4734 | 9.1501 | 2.8437 | -0.18788 | 2.012% | -2.012%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5049 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1039 | 0.97954 | -3.6489 | -7.8127 | 10.5049 | 9.2148 | 2.8636 | -0.18921 | 2.012% | -2.012%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1302 | 0.97839 | -3.7306 | -7.8146 | 10.5155 | 9.401 | 2.9209 | -0.19302 | 2.012% | -2.012%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1703 | 0.97662 | -3.8552 | -7.8176 | 10.526 | 9.6842 | 3.0081 | -0.19882 | 2.012% | -2.012%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1866 | 0.97591 | -3.9059 | -7.8188 | 10.526 | 9.7988 | 3.0433 | -0.20117 | 2.012% | -2.012%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1818 | 0.97611 | -3.8912 | -7.8185 | 10.526 | 9.7655 | 3.0331 | -0.20048 | 2.012% | -2.012%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1667 | 0.97678 | -3.844 | -7.8173 | 10.526 | 9.6587 | 3.0002 | -0.1983 | 2.012% | -2.012%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1338 | 0.97823 | -3.7418 | -7.8148 | 10.526 | 9.4265 | 2.9288 | -0.19354 | 2.012% | -2.012%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0107 | -0.99778 | 0.9744 | -3.4817 | -10.526 | 10.526 | 8.8903 | 2.7068 | -0.24871 | 2.721% | -2.721%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0117 | -0.91623 | 0.97789 | -3.2286 | -10.526 | 10.526 | 8.3141 | 2.5331 | -0.23287 | 2.725% | -2.725%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0125 | -0.84762 | 0.9808 | -3.0165 | -10.526 | 10.526 | 7.8275 | 2.3861 | -0.21945 | 2.727% | -2.727%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99709 | -1.6035 | 0.98211 | -2.6571 | -5.263 | 5.263 | 7.5006 | 2.283 | -0.21545 | 2.792% | -2.792%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99783 | -1.5499 | 0.98325 | -2.5744 | -5.263 | 5.263 | 7.3071 | 2.2247 | -0.20992 | 2.793% | -2.793%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.99824 | -1.5204 | 0.98389 | -2.5288 | -5.263 | 5.263 | 7.2001 | 2.1924 | -0.20687 | 2.793% | -2.793%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99827 | -1.5179 | 0.98394 | -2.525 | -5.263 | 5.263 | 7.1914 | 2.1897 | -0.20661 | 2.793% | -2.793%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99766 | -1.5623 | 0.98299 | -2.5935 | -5.263 | 5.263 | 7.3518 | 2.2382 | -0.2112 | 2.793% | -2.793%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99608 | -1.6763 | 0.98054 | -2.7696 | -5.263 | 5.263 | 7.7631 | 2.3622 | -0.22295 | 2.792% | -2.792%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2525 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99371 | -1.8505 | 0.97685 | -3.0387 | -5.2525 | 5.2525 | 8.3858 | 2.5502 | -0.24018 | 2.784% | -2.784%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1156 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.9928 | -1.9782 | 0.97502 | -3.229 | -5.1156 | 5.1156 | 8.8138 | 2.685 | -0.24515 | 2.706% | -2.706%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.7051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99456 | -2.0408 | 0.9765 | -3.3029 | -4.7051 | 4.7051 | 8.9539 | 2.746 | -0.22714 | 2.474% | -2.474%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.142 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99743 | -2.0943 | 0.97923 | -3.3538 | -4.142 | 4.142 | 9.031 | 2.7953 | -0.19897 | 2.156% | -2.156%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5736 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 1.0001 | -2.168 | 0.98168 | -3.438 | -3.5736 | 3.5736 | 9.0871 | 2.8352 | -0.17393 | 1.878% | -1.878%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.2578 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 1.0016 | -2.1985 | 0.98315 | -3.4678 | -3.2578 | 3.2578 | 9.1337 | 2.8639 | -0.15827 | 1.703% | -1.703%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.3525 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 1.0012 | -2.1829 | 0.98275 | -3.4474 | -3.3525 | 3.3525 | 9.1611 | 2.8706 | -0.1609 | 1.726% | -1.726%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5052 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 1.0004 | -2.1745 | 0.98188 | -3.4428 | -3.5052 | 3.5052 | 9.1692 | 2.8664 | -0.16881 | 1.808% | -1.808%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.942 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9015 | 3.942 | 9.2103 | 2.8583 | -0.19366 | 2.059% | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.4578 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 4.4578 | 9.3963 | 2.9154 | -0.19767 | 2.06% | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.9209 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 4.9209 | 9.6792 | 3.0021 | -0.20378 | 2.062% | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1893 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 5.1893 | 9.7937 | 3.0372 | -0.20626 | 2.063% | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2577 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 5.2577 | 9.7605 | 3.027 | -0.20554 | 2.062% | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 5.263 | 9.6538 | 2.9943 | -0.20323 | 2.062% | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 5.263 | 9.4218 | 2.9232 | -0.19822 | 2.061% | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99169 | -1.9895 | 0.97376 | -3.2549 | -5.263 | 5.263 | 8.8841 | 2.6995 | -0.2549 | 2.789% | -2.789%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99396 | -1.8283 | 0.97726 | -3.0048 | -5.263 | 5.263 | 8.3085 | 2.5265 | -0.23851 | 2.791% | -2.791%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99585 | -1.6928 | 0.98019 | -2.7951 | -5.263 | 5.263 | 7.8224 | 2.3801 | -0.22464 | 2.792% | -2.792%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99709 | -1.6035 | 0.98211 | -2.6571 | -5.263 | 5.263 | 7.5005 | 2.283 | -0.21545 | 2.792% | -2.792%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99783 | -1.5499 | 0.98325 | -2.5744 | -5.263 | 5.263 | 7.3071 | 2.2247 | -0.20992 | 2.793% | -2.793%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.99824 | -1.5204 | 0.98389 | -2.5288 | -5.263 | 5.263 | 7.2001 | 2.1924 | -0.20687 | 2.793% | -2.793%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99827 | -1.5179 | 0.98394 | -2.525 | -5.263 | 5.263 | 7.1914 | 2.1897 | -0.20661 | 2.793% | -2.793%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99766 | -1.5623 | 0.98299 | -2.5935 | -5.263 | 5.263 | 7.3518 | 2.2382 | -0.2112 | 2.793% | -2.793%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99608 | -1.6763 | 0.98054 | -2.7696 | -5.263 | 5.263 | 7.7631 | 2.3622 | -0.22295 | 2.792% | -2.792%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99366 | -1.8497 | 0.9768 | -3.0381 | -5.263 | 5.263 | 8.3853 | 2.5496 | -0.2407 | 2.79% | -2.79%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99202 | -1.968 | 0.97426 | -3.2213 | -5.2577 | 5.2577 | 8.8066 | 2.6765 | -0.25242 | 2.786% | -2.786%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99184 | -2.0051 | 0.97382 | -3.2759 | -5.2051 | 5.2051 | 8.9279 | 2.7153 | -0.25306 | 2.756% | -2.756%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99225 | -2.0263 | 0.97412 | -3.3026 | -5.0946 | 5.0946 | 8.9814 | 2.7365 | -0.24864 | 2.694% | -2.694%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97996 | -3.4207 | -3.8997 | 4.9788 | 9.0704 | 2.8153 | -0.19064 | 2.059% | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 4.9156 | 9.1007 | 2.8246 | -0.1913 | 2.059% | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 4.9841 | 9.1301 | 2.8336 | -0.19193 | 2.059% | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 5.0156 | 9.1457 | 2.8384 | -0.19227 | 2.059% | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 5.1472 | 9.2103 | 2.8583 | -0.19366 | 2.059% | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 5.2367 | 9.3963 | 2.9154 | -0.19767 | 2.06% | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 5.263 | 9.6792 | 3.0021 | -0.20378 | 2.062% | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 5.263 | 9.7937 | 3.0372 | -0.20626 | 2.063% | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 5.263 | 9.7605 | 3.027 | -0.20554 | 2.062% | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 5.263 | 9.6538 | 2.9943 | -0.20323 | 2.062% | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 5.263 | 9.4218 | 2.9232 | -0.19822 | 2.061% | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99169 | -1.9895 | 0.97376 | -3.2549 | -5.263 | 5.263 | 8.8841 | 2.6995 | -0.2549 | 2.789% | -2.789%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99396 | -1.8283 | 0.97726 | -3.0048 | -5.263 | 5.263 | 8.3085 | 2.5265 | -0.23851 | 2.791% | -2.791%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99585 | -1.6928 | 0.98019 | -2.7951 | -5.263 | 5.263 | 7.8224 | 2.3801 | -0.22464 | 2.792% | -2.792%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99709 | -1.6035 | 0.98211 | -2.6571 | -5.263 | 5.263 | 7.5005 | 2.283 | -0.21545 | 2.792% | -2.792%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99783 | -1.5499 | 0.98325 | -2.5744 | -5.263 | 5.263 | 7.3071 | 2.2247 | -0.20992 | 2.793% | -2.793%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.99824 | -1.5204 | 0.98389 | -2.5288 | -5.263 | 5.263 | 7.2001 | 2.1924 | -0.20687 | 2.793% | -2.793%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99827 | -1.5179 | 0.98394 | -2.525 | -5.263 | 5.263 | 7.1914 | 2.1897 | -0.20661 | 2.793% | -2.793%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99766 | -1.5623 | 0.98299 | -2.5935 | -5.263 | 5.263 | 7.3518 | 2.2382 | -0.2112 | 2.793% | -2.793%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99608 | -1.6763 | 0.98054 | -2.7696 | -5.263 | 5.263 | 7.7631 | 2.3622 | -0.22295 | 2.792% | -2.792%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99366 | -1.8497 | 0.9768 | -3.0381 | -5.263 | 5.263 | 8.3853 | 2.5496 | -0.2407 | 2.79% | -2.79%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99199 | -1.9676 | 0.97423 | -3.221 | -5.263 | 5.263 | 8.8063 | 2.6761 | -0.25269 | 2.789% | -2.789%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99152 | -2.0009 | 0.97351 | -3.2728 | -5.263 | 5.263 | 8.9249 | 2.7118 | -0.25606 | 2.789% | -2.789%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99136 | -2.0147 | 0.97324 | -3.2939 | -5.2577 | 5.2577 | 8.9729 | 2.7264 | -0.25714 | 2.786% | -2.786%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2419 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97996 | -3.4207 | -3.8997 | 5.2419 | 9.0704 | 2.8153 | -0.19064 | 2.059% | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 5.2262 | 9.1007 | 2.8246 | -0.1913 | 2.059% | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 5.2262 | 9.1301 | 2.8336 | -0.19193 | 2.059% | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2367 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 5.2367 | 9.1457 | 2.8384 | -0.19227 | 2.059% | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2525 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 5.2525 | 9.2103 | 2.8583 | -0.19366 | 2.059% | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 5.2577 | 9.3963 | 2.9154 | -0.19767 | 2.06% | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 5.263 | 9.6792 | 3.0021 | -0.20378 | 2.062% | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 5.263 | 9.7937 | 3.0372 | -0.20626 | 2.063% | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 5.263 | 9.7605 | 3.027 | -0.20554 | 2.062% | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 5.263 | 9.6538 | 2.9943 | -0.20323 | 2.062% | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 5.263 | 9.4218 | 2.9232 | -0.19822 | 2.061% | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99169 | -1.9895 | 0.97376 | -3.2549 | -5.263 | 5.263 | 8.8841 | 2.6995 | -0.2549 | 2.789% | -2.789%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99396 | -1.8283 | 0.97726 | -3.0048 | -5.263 | 5.263 | 8.3085 | 2.5265 | -0.23851 | 2.791% | -2.791%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99585 | -1.6928 | 0.98019 | -2.7951 | -5.263 | 5.263 | 7.8224 | 2.3801 | -0.22464 | 2.792% | -2.792%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5665 | 0.97941 | -2.6273 | -5.7636 | 10.526 | 7.4788 | 2.2579 | -0.23715 | 3.073% | -3.073%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3539 | 0.97076 | -2.3995 | -7.6011 | 10.526 | 7.2093 | 2.1121 | -0.30771 | 4.094% | -4.094%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3245 | 0.9714 | -2.3536 | -7.5983 | 10.526 | 7.1039 | 2.0817 | -0.30312 | 4.092% | -4.092%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3221 | 0.97146 | -2.3499 | -7.5981 | 10.526 | 7.0953 | 2.0792 | -0.30274 | 4.092% | -4.092%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3663 | 0.9705 | -2.4188 | -7.6016 | 10.526 | 7.2534 | 2.1248 | -0.30963 | 4.094% | -4.094%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6393 | 0.97783 | -2.7401 | -5.7676 | 10.526 | 7.7404 | 2.3358 | -0.24562 | 3.076% | -3.076%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5049 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8124 | 0.97403 | -3.0091 | -5.7786 | 10.5049 | 8.3602 | 2.5202 | -0.26576 | 3.081% | -3.081%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.2313 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9302 | 0.97143 | -3.1926 | -5.7858 | 10.2313 | 8.7796 | 2.6447 | -0.27942 | 3.084% | -3.084%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9634 | 0.97069 | -3.2445 | -5.7879 | 9.4102 | 8.8977 | 2.6797 | -0.28327 | 3.085% | -3.085%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.284 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.9768 | 0.97039 | -3.2653 | -5.7887 | 8.284 | 8.9452 | 2.6938 | -0.28482 | 3.086% | -3.086%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.1472 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97997 | -3.4207 | -3.8996 | 7.1472 | 9.0704 | 2.8153 | -0.19064 | 2.059% | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.5156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 6.5156 | 9.1007 | 2.8246 | -0.1913 | 2.059% | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.7051 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 6.7051 | 9.1301 | 2.8336 | -0.19193 | 2.059% | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.0103 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 7.0103 | 9.1457 | 2.8384 | -0.19227 | 2.059% | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.884 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 7.884 | 9.2103 | 2.8583 | -0.19366 | 2.059% | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.9155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 8.9155 | 9.3963 | 2.9154 | -0.19767 | 2.06% | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.8418 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 9.8418 | 9.6792 | 3.0021 | -0.20378 | 2.062% | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.3786 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 10.3786 | 9.7937 | 3.0372 | -0.20626 | 2.063% | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5155 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 10.5155 | 9.7605 | 3.027 | -0.20554 | 2.062% | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 10.526 | 9.6538 | 2.9943 | -0.20323 | 2.062% | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 10.526 | 9.4218 | 2.9232 | -0.19822 | 2.061% | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.952 | 0.97094 | -3.2266 | -5.7873 | 10.526 | 8.8571 | 2.6677 | -0.28195 | 3.085% | -3.085%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.791 | 0.9745 | -2.9758 | -5.7772 | 10.526 | 8.2837 | 2.4975 | -0.26327 | 3.08% | -3.08%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6557 | 0.97747 | -2.7656 | -5.7689 | 10.526 | 7.7995 | 2.3534 | -0.24754 | 3.076% | -3.076%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5665 | 0.97941 | -2.6273 | -5.7635 | 10.526 | 7.4788 | 2.2579 | -0.23715 | 3.073% | -3.073%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3539 | 0.97076 | -2.3995 | -7.6011 | 10.526 | 7.2093 | 2.1121 | -0.30771 | 4.094% | -4.094%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3245 | 0.9714 | -2.3536 | -7.5983 | 10.526 | 7.1039 | 2.0817 | -0.30312 | 4.092% | -4.092%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3221 | 0.97146 | -2.3499 | -7.5981 | 10.526 | 7.0953 | 2.0792 | -0.30274 | 4.092% | -4.092%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3663 | 0.9705 | -2.4188 | -7.6016 | 10.526 | 7.2534 | 2.1248 | -0.30963 | 4.094% | -4.094%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6393 | 0.97783 | -2.7401 | -5.7676 | 10.526 | 7.7404 | 2.3358 | -0.24562 | 3.076% | -3.076%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8124 | 0.97403 | -3.0091 | -5.7786 | 10.526 | 8.3602 | 2.5202 | -0.26576 | 3.081% | -3.081%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9302 | 0.97143 | -3.1926 | -5.7858 | 10.5155 | 8.7796 | 2.6447 | -0.27942 | 3.084% | -3.084%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9634 | 0.97069 | -3.2445 | -5.7879 | 10.4102 | 8.8977 | 2.6797 | -0.28327 | 3.085% | -3.085%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.9768 | 0.97039 | -3.2653 | -5.7887 | 10.1892 | 8.9452 | 2.6938 | -0.28482 | 3.086% | -3.086%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97997 | -3.4207 | -3.8996 | 9.9576 | 9.0704 | 2.8153 | -0.19064 | 2.059% | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 9.8313 | 9.1007 | 2.8246 | -0.1913 | 2.059% | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 9.9681 | 9.1301 | 2.8336 | -0.19193 | 2.059% | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 10.0313 | 9.1457 | 2.8384 | -0.19227 | 2.059% | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 10.2944 | 9.2103 | 2.8583 | -0.19366 | 2.059% | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 10.4734 | 9.3963 | 2.9154 | -0.19767 | 2.06% | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 10.526 | 9.6792 | 3.0021 | -0.20378 | 2.062% | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 10.526 | 9.7937 | 3.0372 | -0.20626 | 2.063% | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 10.526 | 9.7605 | 3.027 | -0.20554 | 2.062% | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 10.526 | 9.6538 | 2.9943 | -0.20323 | 2.062% | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 10.526 | 9.4218 | 2.9232 | -0.19822 | 2.061% | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.952 | 0.97094 | -3.2266 | -5.7873 | 10.526 | 8.8571 | 2.6677 | -0.28195 | 3.085% | -3.085%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.791 | 0.9745 | -2.9758 | -5.7772 | 10.526 | 8.2837 | 2.4975 | -0.26327 | 3.08% | -3.08%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6557 | 0.97747 | -2.7656 | -5.7689 | 10.526 | 7.7995 | 2.3534 | -0.24754 | 3.076% | -3.076%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5665 | 0.97941 | -2.6273 | -5.7635 | 10.526 | 7.4788 | 2.2579 | -0.23715 | 3.073% | -3.073%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3539 | 0.97076 | -2.3995 | -7.6011 | 10.526 | 7.2093 | 2.1121 | -0.30771 | 4.094% | -4.094%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3245 | 0.9714 | -2.3536 | -7.5983 | 10.526 | 7.1039 | 2.0817 | -0.30312 | 4.092% | -4.092%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3221 | 0.97146 | -2.3499 | -7.5981 | 10.526 | 7.0953 | 2.0792 | -0.30274 | 4.092% | -4.092%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3663 | 0.9705 | -2.4188 | -7.6016 | 10.526 | 7.2534 | 2.1248 | -0.30963 | 4.094% | -4.094%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6393 | 0.97783 | -2.7401 | -5.7676 | 10.526 | 7.7404 | 2.3358 | -0.24562 | 3.076% | -3.076%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8124 | 0.97403 | -3.0091 | -5.7786 | 10.526 | 8.3602 | 2.5202 | -0.26576 | 3.081% | -3.081%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9302 | 0.97143 | -3.1926 | -5.7858 | 10.526 | 8.7796 | 2.6447 | -0.27942 | 3.084% | -3.084%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9634 | 0.97069 | -3.2445 | -5.7879 | 10.526 | 8.8977 | 2.6797 | -0.28327 | 3.085% | -3.085%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.9768 | 0.97039 | -3.2653 | -5.7887 | 10.5155 | 8.9452 | 2.6938 | -0.28482 | 3.086% | -3.086%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4839 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97997 | -3.4207 | -3.8996 | 10.4839 | 9.0704 | 2.8153 | -0.19064 | 2.059% | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 10.4523 | 9.1007 | 2.8246 | -0.1913 | 2.059% | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 10.4523 | 9.1301 | 2.8336 | -0.19193 | 2.059% | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4734 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 10.4734 | 9.1457 | 2.8384 | -0.19227 | 2.059% | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5049 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 10.5049 | 9.2103 | 2.8583 | -0.19366 | 2.059% | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 10.5155 | 9.3963 | 2.9154 | -0.19767 | 2.06% | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 10.526 | 9.6792 | 3.0021 | -0.20378 | 2.062% | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 10.526 | 9.7937 | 3.0372 | -0.20626 | 2.063% | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 10.526 | 9.7605 | 3.027 | -0.20554 | 2.062% | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 10.526 | 9.6538 | 2.9943 | -0.20323 | 2.062% | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 10.526 | 9.4218 | 2.9232 | -0.19822 | 2.061% | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.952 | 0.97094 | -3.2266 | -5.7873 | 10.526 | 8.8571 | 2.6677 | -0.28195 | 3.085% | -3.085%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.791 | 0.9745 | -2.9758 | -5.7772 | 10.526 | 8.2837 | 2.4975 | -0.26327 | 3.08% | -3.08%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6557 | 0.97747 | -2.7656 | -5.7689 | 10.526 | 7.7995 | 2.3534 | -0.24754 | 3.076% | -3.076%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0088 | -3.0638 | 1.0088 | -3.0638 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9616 | 5.263 | 7.4031 | 2.1706 | -0.31285 | 4.055% | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 5.263 | 7.2033 | 2.1052 | -0.3137 | 4.173% | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 5.263 | 7.0931 | 2.0693 | -0.31393 | 4.238% | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 5.263 | 7.0841 | 2.0664 | -0.31395 | 4.244% | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 5.263 | 7.2494 | 2.1203 | -0.31356 | 4.146% | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 5.263 | 7.6751 | 2.2603 | -0.31089 | 3.893% | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2525 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 5.2525 | 8.3238 | 2.4777 | -0.30218 | 3.503% | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1156 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 5.1156 | 8.766 | 2.6287 | -0.29301 | 3.234% | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.7051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 4.7051 | 8.8911 | 2.6719 | -0.28994 | 3.158% | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.142 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 4.142 | 8.9414 | 2.6893 | -0.28864 | 3.127% | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5736 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97213 | -3.1917 | 0.97213 | -3.1917 | -3.5736 | 3.5736 | 8.9939 | 2.7247 | -0.26707 | 2.884% | -2.884%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.2578 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97451 | -3.241 | 0.97451 | -3.241 | -3.2578 | 3.2578 | 9.0492 | 2.7634 | -0.24285 | 2.614% | -2.614%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.3525 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97355 | -3.2437 | 0.97355 | -3.2437 | -3.3525 | 3.3525 | 9.0707 | 2.7632 | -0.25127 | 2.695% | -2.695%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5052 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97221 | -3.2337 | 0.97221 | -3.2337 | -3.5052 | 3.5052 | 9.074 | 2.7534 | -0.26396 | 2.827% | -2.827%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.942 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 3.942 | 9.1202 | 2.7514 | -0.28376 | 3.017% | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.4578 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 4.4578 | 9.3161 | 2.8199 | -0.27792 | 2.897% | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.9209 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 4.9209 | 9.615 | 2.9254 | -0.26801 | 2.712% | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1893 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 5.1893 | 9.7364 | 2.9686 | -0.26364 | 2.636% | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2577 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 5.2577 | 9.7011 | 2.956 | -0.26493 | 2.658% | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 5.263 | 9.588 | 2.9159 | -0.26895 | 2.729% | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 5.263 | 9.3429 | 2.8294 | -0.27708 | 2.88% | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 5.263 | 8.848 | 2.657 | -0.29102 | 3.184% | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 5.263 | 8.2434 | 2.4505 | -0.30356 | 3.552% | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 5.263 | 7.7367 | 2.2808 | -0.3103 | 3.856% | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 5.263 | 7.4031 | 2.1706 | -0.31287 | 4.055% | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 5.263 | 7.2033 | 2.1052 | -0.3137 | 4.173% | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 5.263 | 7.0931 | 2.0693 | -0.31393 | 4.238% | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 5.263 | 7.0841 | 2.0664 | -0.31395 | 4.244% | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 5.263 | 7.2494 | 2.1203 | -0.31356 | 4.146% | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 5.263 | 7.6751 | 2.2603 | -0.31089 | 3.893% | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 5.263 | 8.3238 | 2.4777 | -0.30218 | 3.503% | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 5.2577 | 8.766 | 2.6287 | -0.29301 | 3.234% | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 5.2051 | 8.8911 | 2.6719 | -0.28994 | 3.158% | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 5.0946 | 8.9414 | 2.6893 | -0.28864 | 3.127% | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 4.9788 | 8.9732 | 2.7003 | -0.2878 | 3.108% | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 4.9156 | 9.005 | 2.7114 | -0.28695 | 3.088% | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 4.9841 | 9.0359 | 2.7221 | -0.28612 | 3.069% | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 5.0156 | 9.0523 | 2.7278 | -0.28566 | 3.059% | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 5.1472 | 9.1202 | 2.7514 | -0.28376 | 3.017% | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 5.2367 | 9.3161 | 2.8199 | -0.27792 | 2.897% | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 5.263 | 9.615 | 2.9254 | -0.26801 | 2.712% | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 5.263 | 9.7364 | 2.9686 | -0.26364 | 2.636% | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 5.263 | 9.7011 | 2.956 | -0.26493 | 2.658% | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 5.263 | 9.588 | 2.9159 | -0.26895 | 2.729% | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 5.263 | 9.3429 | 2.8294 | -0.27708 | 2.88% | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 5.263 | 8.848 | 2.657 | -0.29102 | 3.184% | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 5.263 | 8.2434 | 2.4505 | -0.30356 | 3.552% | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 5.263 | 7.7367 | 2.2808 | -0.3103 | 3.856% | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 5.263 | 7.4031 | 2.1706 | -0.31287 | 4.055% | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 5.263 | 7.2033 | 2.1052 | -0.3137 | 4.173% | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 5.263 | 7.0931 | 2.0693 | -0.31393 | 4.238% | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 5.263 | 7.0841 | 2.0664 | -0.31395 | 4.244% | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 5.263 | 7.2494 | 2.1203 | -0.31356 | 4.146% | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 5.263 | 7.6751 | 2.2603 | -0.31089 | 3.893% | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 5.263 | 8.3238 | 2.4777 | -0.30218 | 3.503% | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 5.263 | 8.766 | 2.6287 | -0.29301 | 3.234% | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 5.263 | 8.8911 | 2.6719 | -0.28994 | 3.158% | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 5.2577 | 8.9414 | 2.6893 | -0.28864 | 3.127% | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2419 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 5.2419 | 8.9732 | 2.7003 | -0.2878 | 3.108% | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 5.2262 | 9.005 | 2.7114 | -0.28695 | 3.088% | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 5.2262 | 9.0359 | 2.7221 | -0.28612 | 3.069% | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2367 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 5.2367 | 9.0523 | 2.7278 | -0.28566 | 3.059% | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2525 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 5.2525 | 9.1202 | 2.7514 | -0.28376 | 3.017% | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 5.2577 | 9.3161 | 2.8199 | -0.27792 | 2.897% | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 5.263 | 9.615 | 2.9254 | -0.26801 | 2.712% | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 5.263 | 9.7364 | 2.9686 | -0.26364 | 2.636% | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 5.263 | 9.7011 | 2.956 | -0.26493 | 2.658% | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 5.263 | 9.588 | 2.9159 | -0.26895 | 2.729% | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 5.263 | 9.3429 | 2.8294 | -0.27708 | 2.88% | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 5.263 | 8.848 | 2.657 | -0.29102 | 3.184% | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 5.263 | 8.2434 | 2.4505 | -0.30356 | 3.552% | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 5.263 | 7.7367 | 2.2808 | -0.3103 | 3.856% | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 10.526 | 7.4031 | 2.1706 | -0.31287 | 4.055% | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 10.526 | 7.2033 | 2.1052 | -0.3137 | 4.173% | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 10.526 | 7.0931 | 2.0693 | -0.31393 | 4.238% | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 10.526 | 7.0841 | 2.0664 | -0.31395 | 4.244% | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 10.526 | 7.2494 | 2.1203 | -0.31356 | 4.146% | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 10.526 | 7.6751 | 2.2603 | -0.31089 | 3.893% | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5049 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 10.5049 | 8.3238 | 2.4777 | -0.30218 | 3.503% | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.2313 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 10.2313 | 8.766 | 2.6287 | -0.29301 | 3.234% | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 9.4102 | 8.8911 | 2.6719 | -0.28994 | 3.158% | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.284 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 8.284 | 8.9414 | 2.6893 | -0.28864 | 3.127% | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.1472 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 7.1472 | 8.9732 | 2.7003 | -0.2878 | 3.108% | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.5156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 6.5156 | 9.005 | 2.7114 | -0.28695 | 3.088% | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.7051 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 6.7051 | 9.0359 | 2.7221 | -0.28612 | 3.069% | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.0103 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 7.0103 | 9.0523 | 2.7278 | -0.28566 | 3.059% | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.884 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 7.884 | 9.1202 | 2.7514 | -0.28376 | 3.017% | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.9155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 8.9155 | 9.3161 | 2.8199 | -0.27792 | 2.897% | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.8418 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 9.8418 | 9.615 | 2.9254 | -0.26801 | 2.712% | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.3786 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 10.3786 | 9.7364 | 2.9686 | -0.26364 | 2.636% | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5155 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 10.5155 | 9.7011 | 2.956 | -0.26493 | 2.658% | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 10.526 | 9.588 | 2.9159 | -0.26895 | 2.729% | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 10.526 | 9.3429 | 2.8294 | -0.27708 | 2.88% | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 10.526 | 8.848 | 2.657 | -0.29102 | 3.184% | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 10.526 | 8.2434 | 2.4505 | -0.30356 | 3.552% | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 10.526 | 7.7367 | 2.2808 | -0.3103 | 3.856% | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 10.526 | 7.4031 | 2.1706 | -0.31287 | 4.055% | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 10.526 | 7.2033 | 2.1052 | -0.3137 | 4.173% | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 10.526 | 7.0931 | 2.0693 | -0.31393 | 4.238% | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 10.526 | 7.0841 | 2.0664 | -0.31395 | 4.244% | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 10.526 | 7.2494 | 2.1203 | -0.31356 | 4.146% | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 10.526 | 7.6751 | 2.2603 | -0.31089 | 3.893% | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 10.526 | 8.3238 | 2.4777 | -0.30218 | 3.503% | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 10.5155 | 8.766 | 2.6287 | -0.29301 | 3.234% | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 10.4102 | 8.8911 | 2.6719 | -0.28994 | 3.158% | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 10.1892 | 8.9414 | 2.6893 | -0.28864 | 3.127% | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 9.9576 | 8.9732 | 2.7003 | -0.2878 | 3.108% | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 9.8313 | 9.005 | 2.7114 | -0.28695 | 3.088% | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 9.9681 | 9.0359 | 2.7221 | -0.28612 | 3.069% | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 10.0313 | 9.0523 | 2.7278 | -0.28566 | 3.059% | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 10.2944 | 9.1202 | 2.7514 | -0.28376 | 3.017% | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 10.4734 | 9.3161 | 2.8199 | -0.27792 | 2.897% | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 10.526 | 9.615 | 2.9254 | -0.26801 | 2.712% | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 10.526 | 9.7364 | 2.9686 | -0.26364 | 2.636% | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 10.526 | 9.7011 | 2.956 | -0.26493 | 2.658% | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 10.526 | 9.588 | 2.9159 | -0.26895 | 2.729% | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 10.526 | 9.3429 | 2.8294 | -0.27708 | 2.88% | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 10.526 | 8.848 | 2.657 | -0.29102 | 3.184% | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 10.526 | 8.2434 | 2.4505 | -0.30356 | 3.552% | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 10.526 | 7.7367 | 2.2808 | -0.3103 | 3.856% | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 10.526 | 7.4031 | 2.1706 | -0.31287 | 4.055% | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 10.526 | 7.2033 | 2.1052 | -0.3137 | 4.173% | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 10.526 | 7.0931 | 2.0693 | -0.31393 | 4.238% | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 10.526 | 7.0841 | 2.0664 | -0.31395 | 4.244% | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 10.526 | 7.2494 | 2.1203 | -0.31356 | 4.146% | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 10.526 | 7.6751 | 2.2603 | -0.31089 | 3.893% | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 10.526 | 8.3238 | 2.4777 | -0.30218 | 3.503% | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 10.526 | 8.766 | 2.6287 | -0.29301 | 3.234% | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 10.526 | 8.8911 | 2.6719 | -0.28994 | 3.158% | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 10.5155 | 8.9414 | 2.6893 | -0.28864 | 3.127% | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4839 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 10.4839 | 8.9732 | 2.7003 | -0.2878 | 3.108% | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 10.4523 | 9.005 | 2.7114 | -0.28695 | 3.088% | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 10.4523 | 9.0359 | 2.7221 | -0.28612 | 3.069% | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4734 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 10.4734 | 9.0523 | 2.7278 | -0.28566 | 3.059% | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5049 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 10.5049 | 9.1202 | 2.7514 | -0.28376 | 3.017% | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 10.5155 | 9.3161 | 2.8199 | -0.27792 | 2.897% | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 10.526 | 9.615 | 2.9254 | -0.26801 | 2.712% | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 10.526 | 9.7364 | 2.9686 | -0.26364 | 2.636% | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 10.526 | 9.7011 | 2.956 | -0.26493 | 2.658% | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 10.526 | 9.588 | 2.9159 | -0.26895 | 2.729% | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 10.526 | 9.3429 | 2.8294 | -0.27708 | 2.88% | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 10.526 | 8.848 | 2.657 | -0.29102 | 3.184% | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 10.526 | 8.2434 | 2.4505 | -0.30356 | 3.552% | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 10.526 | 7.7367 | 2.2808 | -0.3103 | 3.856% | -3.856%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1789 | 1.0293 | -0.94449 | 1.0038 | -3.0651 | -5.263 | 5.263 | 7.612 | 1.4919 | -0.104 | 1.348% | -1.348%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0296 | -0.91705 | 1.0048 | -2.9806 | -5.263 | 5.263 | 7.4157 | 1.4536 | -0.10129 | 1.348% | -1.348%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.9019 | 1.0053 | -2.9339 | -5.263 | 5.263 | 7.3072 | 1.4324 | -0.099825 | 1.348% | -1.348%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90066 | 1.0053 | -2.9301 | -5.263 | 5.263 | 7.2983 | 1.4307 | -0.099706 | 1.348% | -1.348%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92339 | 1.0046 | -3.0001 | -5.263 | 5.263 | 7.4611 | 1.4625 | -0.10191 | 1.347% | -1.347%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.029 | -0.98178 | 1.0025 | -3.1801 | -5.263 | 5.263 | 7.8784 | 1.544 | -0.10755 | 1.347% | -1.347%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2525 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0283 | -1.0672 | 0.99962 | -3.4415 | -5.2525 | 5.2525 | 8.5114 | 1.6684 | -0.11459 | 1.328% | -1.328%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1156 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0281 | -1.1304 | 0.99786 | -3.6295 | -5.1156 | 5.1156 | 8.942 | 1.7543 | -0.11697 | 1.291% | -1.291%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.7051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.029 | -1.1572 | 0.99829 | -3.6887 | -4.7051 | 4.7051 | 9.0724 | 1.785 | -0.10861 | 1.183% | -1.183%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.142 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0304 | -1.1778 | 0.99944 | -3.7207 | -4.142 | 4.142 | 9.1343 | 1.8043 | -0.095735 | 1.037% | -1.037%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5736 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0317 | -1.2057 | 1.0004 | -3.7778 | -3.5736 | 3.5736 | 9.1756 | 1.8181 | -0.085401 | 0.9222% | -0.9222%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.2578 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0324 | -1.2165 | 1.0011 | -3.7931 | -3.2578 | 3.2578 | 9.2142 | 1.8299 | -0.077797 | 0.8372% | -0.8372%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.3525 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0323 | -1.209 | 1.001 | -3.7714 | -3.3525 | 3.3525 | 9.2448 | 1.8364 | -0.07725 | 0.8287% | -0.8287%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5052 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0319 | -1.2075 | 1.0005 | -3.7758 | -3.5052 | 3.5052 | 9.2569 | 1.8368 | -0.081094 | 0.8684% | -0.8684%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.942 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0307 | -1.2062 | 0.99911 | -3.7966 | -3.942 | 3.942 | 9.3117 | 1.842 | -0.092322 | 0.9817% | -0.9817%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.4578 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0291 | -1.2204 | 0.99687 | -3.8707 | -4.4578 | 4.4578 | 9.4869 | 1.8696 | -0.10714 | 1.117% | -1.117%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.9209 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0275 | -1.2525 | 0.99416 | -3.9991 | -4.9209 | 4.9209 | 9.7595 | 1.9162 | -0.12347 | 1.249% | -1.249%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1893 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0266 | -1.2633 | 0.99287 | -4.0489 | -5.1893 | 5.1893 | 9.8677 | 1.9334 | -0.1323 | 1.323% | -1.323%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2577 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0265 | -1.2571 | 0.99286 | -4.0338 | -5.2577 | 5.2577 | 9.8323 | 1.9254 | -0.13373 | 1.342% | -1.342%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0266 | -1.2418 | 0.99339 | -3.9863 | -5.263 | 5.263 | 9.7246 | 1.9044 | -0.13243 | 1.344% | -1.344%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0269 | -1.2087 | 0.99457 | -3.8832 | -5.263 | 5.263 | 9.4907 | 1.8588 | -0.12929 | 1.344% | -1.344%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1417 | 0.99695 | -3.6749 | -5.263 | 5.263 | 9.0161 | 1.7662 | -0.1229 | 1.345% | -1.345%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0283 | -1.0594 | 0.99984 | -3.42 | -5.263 | 5.263 | 8.432 | 1.6521 | -0.11503 | 1.346% | -1.346%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99021 | 1.0023 | -3.2061 | -5.263 | 5.263 | 7.9386 | 1.5558 | -0.10837 | 1.347% | -1.347%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.9445 | 1.0038 | -3.0651 | -5.263 | 5.263 | 7.612 | 1.492 | -0.10395 | 1.347% | -1.347%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0296 | -0.91705 | 1.0048 | -2.9806 | -5.263 | 5.263 | 7.4157 | 1.4536 | -0.10129 | 1.348% | -1.348%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.9019 | 1.0053 | -2.9339 | -5.263 | 5.263 | 7.3072 | 1.4324 | -0.099825 | 1.348% | -1.348%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90066 | 1.0053 | -2.9301 | -5.263 | 5.263 | 7.2983 | 1.4307 | -0.099706 | 1.348% | -1.348%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92339 | 1.0046 | -3.0001 | -5.263 | 5.263 | 7.4611 | 1.4625 | -0.10191 | 1.347% | -1.347%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.029 | -0.98178 | 1.0025 | -3.1801 | -5.263 | 5.263 | 7.8784 | 1.544 | -0.10755 | 1.347% | -1.347%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0704 | 0.99946 | -3.454 | -5.263 | 5.263 | 8.5099 | 1.6674 | -0.11608 | 1.346% | -1.346%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0277 | -1.1306 | 0.99736 | -3.6404 | -5.2577 | 5.2577 | 8.9373 | 1.7509 | -0.12171 | 1.344% | -1.344%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0276 | -1.1487 | 0.99689 | -3.6934 | -5.2051 | 5.2051 | 9.059 | 1.7753 | -0.122 | 1.329% | -1.329%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0279 | -1.1546 | 0.99707 | -3.7034 | -5.0946 | 5.0946 | 9.1114 | 1.7877 | -0.11861 | 1.285% | -1.285%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0282 | -1.1617 | 0.99721 | -3.7187 | -4.9788 | 4.9788 | 9.1448 | 1.7957 | -0.11618 | 1.255% | -1.255%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0283 | -1.1675 | 0.99722 | -3.733 | -4.9156 | 4.9156 | 9.177 | 1.8028 | -0.11502 | 1.238% | -1.238%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0281 | -1.17 | 0.9969 | -3.7449 | -4.9841 | 4.9841 | 9.2049 | 1.8074 | -0.11706 | 1.256% | -1.256%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.028 | -1.1715 | 0.99674 | -3.7512 | -5.0156 | 5.0156 | 9.22 | 1.8099 | -0.11803 | 1.264% | -1.264%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0276 | -1.1775 | 0.99608 | -3.7776 | -5.1472 | 5.1472 | 9.2819 | 1.8203 | -0.1221 | 1.298% | -1.298%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0271 | -1.2018 | 0.99492 | -3.8582 | -5.2367 | 5.2367 | 9.4672 | 1.8553 | -0.12677 | 1.321% | -1.321%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0266 | -1.2454 | 0.99326 | -3.9976 | -5.263 | 5.263 | 9.7502 | 1.9094 | -0.13277 | 1.343% | -1.343%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0264 | -1.2618 | 0.99267 | -4.0486 | -5.263 | 5.263 | 9.8657 | 1.9319 | -0.13432 | 1.343% | -1.343%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.257 | 0.99284 | -4.0338 | -5.263 | 5.263 | 9.8321 | 1.9253 | -0.13387 | 1.343% | -1.343%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0266 | -1.2418 | 0.99339 | -3.9863 | -5.263 | 5.263 | 9.7246 | 1.9044 | -0.13243 | 1.344% | -1.344%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0269 | -1.2087 | 0.99457 | -3.8832 | -5.263 | 5.263 | 9.4907 | 1.8588 | -0.12929 | 1.344% | -1.344%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1417 | 0.99695 | -3.6749 | -5.263 | 5.263 | 9.0161 | 1.7662 | -0.1229 | 1.345% | -1.345%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0283 | -1.0594 | 0.99984 | -3.42 | -5.263 | 5.263 | 8.432 | 1.6521 | -0.11503 | 1.346% | -1.346%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99021 | 1.0023 | -3.2061 | -5.263 | 5.263 | 7.9386 | 1.5558 | -0.10837 | 1.347% | -1.347%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.9445 | 1.0038 | -3.0651 | -5.263 | 5.263 | 7.612 | 1.492 | -0.10395 | 1.347% | -1.347%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0296 | -0.91705 | 1.0048 | -2.9806 | -5.263 | 5.263 | 7.4157 | 1.4536 | -0.10129 | 1.348% | -1.348%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.9019 | 1.0053 | -2.9339 | -5.263 | 5.263 | 7.3072 | 1.4324 | -0.099825 | 1.348% | -1.348%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90066 | 1.0053 | -2.9301 | -5.263 | 5.263 | 7.2983 | 1.4307 | -0.099706 | 1.348% | -1.348%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92339 | 1.0046 | -3.0001 | -5.263 | 5.263 | 7.4611 | 1.4625 | -0.10191 | 1.347% | -1.347%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.029 | -0.98178 | 1.0025 | -3.1801 | -5.263 | 5.263 | 7.8784 | 1.544 | -0.10755 | 1.347% | -1.347%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0704 | 0.99946 | -3.454 | -5.263 | 5.263 | 8.5099 | 1.6674 | -0.11608 | 1.346% | -1.346%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1305 | 0.99734 | -3.6404 | -5.263 | 5.263 | 8.9372 | 1.7508 | -0.12184 | 1.345% | -1.345%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0275 | -1.1475 | 0.99674 | -3.6931 | -5.263 | 5.263 | 9.0575 | 1.7743 | -0.12346 | 1.345% | -1.345%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0274 | -1.1544 | 0.99651 | -3.7143 | -5.2577 | 5.2577 | 9.106 | 1.7838 | -0.12398 | 1.343% | -1.343%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2419 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0274 | -1.1591 | 0.9964 | -3.7278 | -5.2419 | 5.2419 | 9.137 | 1.79 | -0.12399 | 1.339% | -1.339%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0274 | -1.1637 | 0.99629 | -3.7413 | -5.2262 | 5.2262 | 9.168 | 1.7963 | -0.124 | 1.334% | -1.334%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0274 | -1.1679 | 0.99614 | -3.7542 | -5.2262 | 5.2262 | 9.1976 | 1.8021 | -0.12439 | 1.334% | -1.334%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2367 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0274 | -1.1662 | 0.99618 | -3.7476 | -5.2367 | 5.2367 | 9.2145 | 1.806 | -0.12346 | 1.322% | -1.322%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2525 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0273 | -1.175 | 0.99582 | -3.7759 | -5.2525 | 5.2525 | 9.2793 | 1.8184 | -0.12471 | 1.326% | -1.326%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.027 | -1.2052 | 0.99471 | -3.872 | -5.2577 | 5.2577 | 9.4652 | 1.8539 | -0.1288 | 1.343% | -1.343%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0266 | -1.2454 | 0.99326 | -3.9976 | -5.263 | 5.263 | 9.7502 | 1.9094 | -0.13277 | 1.343% | -1.343%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0264 | -1.2618 | 0.99267 | -4.0486 | -5.263 | 5.263 | 9.8657 | 1.9319 | -0.13432 | 1.343% | -1.343%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.257 | 0.99284 | -4.0338 | -5.263 | 5.263 | 9.8321 | 1.9253 | -0.13387 | 1.343% | -1.343%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0266 | -1.2418 | 0.99339 | -3.9863 | -5.263 | 5.263 | 9.7246 | 1.9044 | -0.13243 | 1.344% | -1.344%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0269 | -1.2087 | 0.99457 | -3.8832 | -5.263 | 5.263 | 9.4907 | 1.8588 | -0.12929 | 1.344% | -1.344%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1417 | 0.99695 | -3.6749 | -5.263 | 5.263 | 9.0161 | 1.7662 | -0.1229 | 1.345% | -1.345%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0283 | -1.0594 | 0.99984 | -3.42 | -5.263 | 5.263 | 8.432 | 1.6521 | -0.11503 | 1.346% | -1.346%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99021 | 1.0023 | -3.2061 | -5.263 | 5.263 | 7.9386 | 1.5558 | -0.10837 | 1.347% | -1.347%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.82044 | 0.99018 | -2.9845 | -10.526 | 10.526 | 7.5029 | 1.4143 | -0.21311 | 2.762% | -2.762%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0157 | -0.7929 | 0.99112 | -2.8986 | -10.526 | 10.526 | 7.3094 | 1.3781 | -0.20761 | 2.762% | -2.762%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0158 | -0.77769 | 0.99164 | -2.8513 | -10.526 | 10.526 | 7.2024 | 1.3581 | -0.20457 | 2.762% | -2.762%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.77645 | 0.99168 | -2.8474 | -10.526 | 10.526 | 7.1937 | 1.3565 | -0.20432 | 2.762% | -2.762%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0156 | -0.79927 | 0.99091 | -2.9185 | -10.526 | 10.526 | 7.3541 | 1.3865 | -0.20888 | 2.762% | -2.762%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0151 | -0.85786 | 0.9889 | -3.1012 | -10.526 | 10.526 | 7.7654 | 1.4635 | -0.22059 | 2.762% | -2.762%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5049 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0145 | -0.93958 | 0.98617 | -3.352 | -10.5049 | 10.5049 | 8.3907 | 1.5819 | -0.23533 | 2.728% | -2.728%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.2313 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0147 | -1.0062 | 0.98479 | -3.5444 | -10.2313 | 10.2313 | 8.8186 | 1.6654 | -0.24037 | 2.653% | -2.653%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0167 | -1.0433 | 0.98632 | -3.6111 | -9.4102 | 9.4102 | 8.9577 | 1.7022 | -0.22329 | 2.432% | -2.432%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.284 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0196 | -1.0789 | 0.98892 | -3.656 | -8.284 | 8.284 | 9.0328 | 1.7309 | -0.19717 | 2.136% | -2.136%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.1472 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0224 | -1.1191 | 0.9914 | -3.717 | -7.1472 | 7.1472 | 9.0886 | 1.755 | -0.17236 | 1.861% | -1.861%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.5156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.024 | -1.1367 | 0.99291 | -3.734 | -6.5156 | 6.5156 | 9.1351 | 1.7725 | -0.15685 | 1.688% | -1.688%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.7051 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0236 | -1.1287 | 0.99255 | -3.7168 | -6.7051 | 6.7051 | 9.1626 | 1.7767 | -0.1594 | 1.71% | -1.71%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.0103 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0228 | -1.1235 | 0.99169 | -3.7187 | -7.0103 | 7.0103 | 9.1708 | 1.7743 | -0.16723 | 1.791% | -1.791%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.884 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0204 | -1.1116 | 0.98914 | -3.7336 | -7.884 | 7.884 | 9.2137 | 1.7709 | -0.19032 | 2.024% | -2.024%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.9155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0175 | -1.1127 | 0.98557 | -3.7989 | -8.9155 | 8.9155 | 9.3735 | 1.7874 | -0.22051 | 2.298% | -2.298%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.8418 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0145 | -1.1369 | 0.98153 | -3.9342 | -9.8418 | 9.8418 | 9.6288 | 1.8213 | -0.25416 | 2.572% | -2.572%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.3786 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0129 | -1.142 | 0.97951 | -3.9839 | -10.3786 | 10.3786 | 9.7278 | 1.8317 | -0.27223 | 2.722% | -2.722%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5155 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0126 | -1.1343 | 0.97931 | -3.9683 | -10.5155 | 10.5155 | 9.6909 | 1.8228 | -0.27513 | 2.761% | -2.761%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0127 | -1.1188 | 0.97982 | -3.92 | -10.526 | 10.526 | 9.5846 | 1.8029 | -0.2724 | 2.764% | -2.764%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.013 | -1.0856 | 0.98099 | -3.8153 | -10.526 | 10.526 | 9.3542 | 1.76 | -0.26584 | 2.763% | -2.763%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -1.0183 | 0.98335 | -3.6037 | -10.526 | 10.526 | 8.8865 | 1.6728 | -0.25251 | 2.763% | -2.763%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0144 | -0.93579 | 0.98622 | -3.3449 | -10.526 | 10.526 | 8.3109 | 1.5654 | -0.23612 | 2.763% | -2.763%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.86632 | 0.98861 | -3.1276 | -10.526 | 10.526 | 7.8247 | 1.4745 | -0.22228 | 2.762% | -2.762%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.82044 | 0.99018 | -2.9845 | -10.526 | 10.526 | 7.5029 | 1.4143 | -0.21312 | 2.762% | -2.762%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0157 | -0.7929 | 0.99112 | -2.8986 | -10.526 | 10.526 | 7.3094 | 1.3781 | -0.20761 | 2.762% | -2.762%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0158 | -0.77769 | 0.99164 | -2.8513 | -10.526 | 10.526 | 7.2024 | 1.3581 | -0.20457 | 2.762% | -2.762%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.77645 | 0.99168 | -2.8474 | -10.526 | 10.526 | 7.1937 | 1.3565 | -0.20432 | 2.762% | -2.762%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0156 | -0.79927 | 0.99091 | -2.9185 | -10.526 | 10.526 | 7.3541 | 1.3865 | -0.20888 | 2.762% | -2.762%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0151 | -0.85786 | 0.9889 | -3.1012 | -10.526 | 10.526 | 7.7654 | 1.4635 | -0.22059 | 2.762% | -2.762%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0143 | -0.94678 | 0.98584 | -3.3793 | -10.526 | 10.526 | 8.3877 | 1.5797 | -0.23831 | 2.763% | -2.763%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0138 | -1.0074 | 0.98377 | -3.5687 | -10.5155 | 10.5155 | 8.809 | 1.6585 | -0.25003 | 2.76% | -2.76%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0139 | -1.0266 | 0.98346 | -3.6228 | -10.4102 | 10.4102 | 8.9303 | 1.6826 | -0.2507 | 2.731% | -2.731%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0146 | -1.031 | 0.98407 | -3.6194 | -10.1892 | 10.1892 | 8.9862 | 1.6973 | -0.24383 | 2.642% | -2.642%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0151 | -1.041 | 0.98452 | -3.6368 | -9.9576 | 9.9576 | 9.0221 | 1.7071 | -0.23886 | 2.579% | -2.579%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0154 | -1.0484 | 0.9847 | -3.6524 | -9.8313 | 9.8313 | 9.0555 | 1.7151 | -0.23649 | 2.545% | -2.545%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.015 | -1.0492 | 0.9842 | -3.6632 | -9.9681 | 9.9681 | 9.0813 | 1.7181 | -0.24068 | 2.582% | -2.582%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0148 | -1.0498 | 0.98396 | -3.6691 | -10.0313 | 10.0313 | 9.0953 | 1.7199 | -0.24268 | 2.599% | -2.599%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0141 | -1.0525 | 0.98295 | -3.6935 | -10.2944 | 10.2944 | 9.1529 | 1.7272 | -0.25106 | 2.67% | -2.67%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0133 | -1.0745 | 0.98156 | -3.7736 | -10.4734 | 10.4734 | 9.3333 | 1.7584 | -0.26073 | 2.718% | -2.718%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0127 | -1.1224 | 0.97969 | -3.9315 | -10.526 | 10.526 | 9.6099 | 1.8076 | -0.27312 | 2.764% | -2.764%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0125 | -1.1389 | 0.97911 | -3.9833 | -10.526 | 10.526 | 9.7236 | 1.8287 | -0.27637 | 2.764% | -2.764%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0126 | -1.1341 | 0.97928 | -3.9683 | -10.526 | 10.526 | 9.6906 | 1.8226 | -0.27542 | 2.764% | -2.764%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0127 | -1.1188 | 0.97982 | -3.92 | -10.526 | 10.526 | 9.5846 | 1.8029 | -0.2724 | 2.764% | -2.764%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.013 | -1.0856 | 0.98099 | -3.8153 | -10.526 | 10.526 | 9.3542 | 1.76 | -0.26584 | 2.763% | -2.763%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -1.0183 | 0.98335 | -3.6037 | -10.526 | 10.526 | 8.8865 | 1.6728 | -0.25251 | 2.763% | -2.763%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0144 | -0.93579 | 0.98622 | -3.3449 | -10.526 | 10.526 | 8.3109 | 1.5654 | -0.23612 | 2.763% | -2.763%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.86632 | 0.98861 | -3.1276 | -10.526 | 10.526 | 7.8247 | 1.4745 | -0.22228 | 2.762% | -2.762%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.82044 | 0.99018 | -2.9845 | -10.526 | 10.526 | 7.5029 | 1.4143 | -0.21312 | 2.762% | -2.762%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0157 | -0.7929 | 0.99112 | -2.8986 | -10.526 | 10.526 | 7.3094 | 1.3781 | -0.20761 | 2.762% | -2.762%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0158 | -0.77769 | 0.99164 | -2.8513 | -10.526 | 10.526 | 7.2024 | 1.3581 | -0.20457 | 2.762% | -2.762%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.77645 | 0.99168 | -2.8474 | -10.526 | 10.526 | 7.1937 | 1.3565 | -0.20432 | 2.762% | -2.762%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0156 | -0.79927 | 0.99091 | -2.9185 | -10.526 | 10.526 | 7.3541 | 1.3865 | -0.20888 | 2.762% | -2.762%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0151 | -0.85786 | 0.9889 | -3.1012 | -10.526 | 10.526 | 7.7654 | 1.4635 | -0.22059 | 2.762% | -2.762%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0143 | -0.94678 | 0.98584 | -3.3793 | -10.526 | 10.526 | 8.3877 | 1.5797 | -0.23831 | 2.763% | -2.763%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0137 | -1.0071 | 0.98374 | -3.5686 | -10.526 | 10.526 | 8.8087 | 1.6583 | -0.2503 | 2.763% | -2.763%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0136 | -1.0242 | 0.98315 | -3.6222 | -10.526 | 10.526 | 8.9273 | 1.6804 | -0.25367 | 2.763% | -2.763%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0136 | -1.0312 | 0.98294 | -3.6437 | -10.5155 | 10.5155 | 8.9752 | 1.6895 | -0.25476 | 2.76% | -2.76%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4839 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0136 | -1.0362 | 0.98287 | -3.6575 | -10.4839 | 10.4839 | 9.0062 | 1.6957 | -0.2548 | 2.751% | -2.751%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0136 | -1.0413 | 0.9828 | -3.6713 | -10.4523 | 10.4523 | 9.0372 | 1.7019 | -0.25484 | 2.743% | -2.743%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0136 | -1.0454 | 0.98266 | -3.6845 | -10.4523 | 10.4523 | 9.0663 | 1.7074 | -0.25566 | 2.743% | -2.743%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4734 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0137 | -1.039 | 0.98281 | -3.6618 | -10.4734 | 10.4734 | 9.0842 | 1.7119 | -0.25382 | 2.718% | -2.718%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5049 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0135 | -1.0473 | 0.98241 | -3.6901 | -10.5049 | 10.5049 | 9.1476 | 1.7233 | -0.2564 | 2.727% | -2.727%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0131 | -1.0822 | 0.98115 | -3.8039 | -10.5155 | 10.5155 | 9.3292 | 1.7555 | -0.26483 | 2.76% | -2.76%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0127 | -1.1224 | 0.97969 | -3.9315 | -10.526 | 10.526 | 9.6099 | 1.8076 | -0.27312 | 2.764% | -2.764%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0125 | -1.1389 | 0.97911 | -3.9833 | -10.526 | 10.526 | 9.7236 | 1.8287 | -0.27637 | 2.764% | -2.764%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0126 | -1.1341 | 0.97928 | -3.9683 | -10.526 | 10.526 | 9.6906 | 1.8226 | -0.27542 | 2.764% | -2.764%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0127 | -1.1188 | 0.97982 | -3.92 | -10.526 | 10.526 | 9.5846 | 1.8029 | -0.2724 | 2.764% | -2.764%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.013 | -1.0856 | 0.98099 | -3.8153 | -10.526 | 10.526 | 9.3542 | 1.76 | -0.26584 | 2.763% | -2.763%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -1.0183 | 0.98335 | -3.6037 | -10.526 | 10.526 | 8.8865 | 1.6728 | -0.25251 | 2.763% | -2.763%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0144 | -0.93579 | 0.98622 | -3.3449 | -10.526 | 10.526 | 8.3109 | 1.5654 | -0.23612 | 2.763% | -2.763%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.86632 | 0.98861 | -3.1276 | -10.526 | 10.526 | 7.8247 | 1.4745 | -0.22228 | 2.762% | -2.762%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0296 | -2.1143 | 1.0168 | -3.1788 | 1.0021 | -1.669 | 0.98964 | -2.7653 | -5.263 | 5.263 | 7.4985 | 1.4113 | -0.21748 | 2.819% | -2.819%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.614 | 0.99058 | -2.6804 | -5.263 | 5.263 | 7.3052 | 1.3752 | -0.21183 | 2.818% | -2.818%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5837 | 0.9911 | -2.6335 | -5.263 | 5.263 | 7.1983 | 1.3552 | -0.20871 | 2.818% | -2.818%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0031 | -1.5812 | 0.99114 | -2.6297 | -5.263 | 5.263 | 7.1895 | 1.3536 | -0.20845 | 2.818% | -2.818%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0026 | -1.6268 | 0.99036 | -2.7 | -5.263 | 5.263 | 7.3499 | 1.3835 | -0.21313 | 2.818% | -2.818%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0013 | -1.7438 | 0.98835 | -2.8808 | -5.263 | 5.263 | 7.7609 | 1.4602 | -0.22515 | 2.819% | -2.819%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2525 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99957 | -1.9059 | 0.98562 | -3.1296 | -5.2525 | 5.2525 | 8.3857 | 1.5783 | -0.24029 | 2.786% | -2.786%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1156 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99896 | -2.0375 | 0.98425 | -3.3261 | -5.1156 | 5.1156 | 8.8135 | 1.6617 | -0.24551 | 2.71% | -2.71%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.7051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 1.0008 | -2.1066 | 0.98582 | -3.4104 | -4.7051 | 4.7051 | 8.9529 | 1.6988 | -0.22807 | 2.484% | -2.484%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.142 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 1.0036 | -2.1713 | 0.98848 | -3.4799 | -4.142 | 4.142 | 9.0286 | 1.7278 | -0.2014 | 2.182% | -2.182%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5736 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 1.0063 | -2.2455 | 0.99102 | -3.5648 | -3.5736 | 3.5736 | 9.085 | 1.7524 | -0.17602 | 1.901% | -1.901%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.2578 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 1.0079 | -2.2766 | 0.99256 | -3.5956 | -3.2578 | 3.2578 | 9.1318 | 1.7701 | -0.16018 | 1.724% | -1.724%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.3525 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 1.0075 | -2.2608 | 0.9922 | -3.575 | -3.3525 | 3.3525 | 9.1592 | 1.7743 | -0.1628 | 1.746% | -1.746%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5052 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 1.0066 | -2.2524 | 0.99133 | -3.5702 | -3.5052 | 3.5052 | 9.1672 | 1.7717 | -0.1708 | 1.829% | -1.829%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.942 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 1.0041 | -2.2341 | 0.98872 | -3.5658 | -3.942 | 3.942 | 9.2096 | 1.7679 | -0.19442 | 2.067% | -2.067%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.4578 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 1.0008 | -2.2426 | 0.9851 | -3.6075 | -4.4578 | 4.4578 | 9.3687 | 1.7839 | -0.22529 | 2.348% | -2.348%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.9209 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.9972 | -2.2977 | 0.98098 | -3.7203 | -4.9209 | 4.9209 | 9.6232 | 1.8172 | -0.25977 | 2.628% | -2.628%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1893 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99534 | -2.3115 | 0.97893 | -3.7572 | -5.1893 | 5.1893 | 9.7217 | 1.8274 | -0.27827 | 2.783% | -2.783%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2577 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99507 | -2.2971 | 0.97872 | -3.7387 | -5.2577 | 5.2577 | 9.6848 | 1.8184 | -0.28123 | 2.822% | -2.822%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.9954 | -2.266 | 0.97924 | -3.6907 | -5.263 | 5.263 | 9.5786 | 1.7985 | -0.27842 | 2.825% | -2.825%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99616 | -2.1994 | 0.98042 | -3.5871 | -5.263 | 5.263 | 9.3483 | 1.7558 | -0.27166 | 2.824% | -2.824%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99769 | -2.0647 | 0.98278 | -3.3778 | -5.263 | 5.263 | 8.881 | 1.6689 | -0.25795 | 2.823% | -2.823%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99955 | -1.8996 | 0.98566 | -3.1218 | -5.263 | 5.263 | 8.3059 | 1.5618 | -0.2411 | 2.821% | -2.821%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0011 | -1.7607 | 0.98806 | -2.9069 | -5.263 | 5.263 | 7.8201 | 1.4713 | -0.22688 | 2.819% | -2.819%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0021 | -1.669 | 0.98964 | -2.7653 | -5.263 | 5.263 | 7.4985 | 1.4113 | -0.21748 | 2.819% | -2.819%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.614 | 0.99058 | -2.6804 | -5.263 | 5.263 | 7.3052 | 1.3752 | -0.21183 | 2.818% | -2.818%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5837 | 0.9911 | -2.6335 | -5.263 | 5.263 | 7.1983 | 1.3552 | -0.20871 | 2.818% | -2.818%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0031 | -1.5812 | 0.99114 | -2.6297 | -5.263 | 5.263 | 7.1895 | 1.3536 | -0.20845 | 2.818% | -2.818%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0026 | -1.6268 | 0.99036 | -2.7 | -5.263 | 5.263 | 7.3499 | 1.3835 | -0.21313 | 2.818% | -2.818%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0013 | -1.7438 | 0.98835 | -2.8808 | -5.263 | 5.263 | 7.7609 | 1.4602 | -0.22515 | 2.819% | -2.819%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.9993 | -1.9216 | 0.98528 | -3.1559 | -5.263 | 5.263 | 8.3827 | 1.5762 | -0.24334 | 2.821% | -2.821%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99797 | -2.0427 | 0.9832 | -3.3434 | -5.2577 | 5.2577 | 8.8036 | 1.6547 | -0.2554 | 2.819% | -2.819%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99788 | -2.0806 | 0.98289 | -3.3993 | -5.2051 | 5.2051 | 8.9249 | 1.6787 | -0.25611 | 2.79% | -2.79%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99853 | -2.0868 | 0.98353 | -3.4013 | -5.0946 | 5.0946 | 8.9809 | 1.6936 | -0.24907 | 2.698% | -2.698%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99906 | -2.1054 | 0.98399 | -3.4236 | -4.9788 | 4.9788 | 9.017 | 1.7035 | -0.244 | 2.635% | -2.635%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.9993 | -2.1194 | 0.98417 | -3.4419 | -4.9156 | 4.9156 | 9.0504 | 1.7114 | -0.24158 | 2.6% | -2.6%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99883 | -2.1218 | 0.98366 | -3.4495 | -4.9841 | 4.9841 | 9.0761 | 1.7144 | -0.24587 | 2.638% | -2.638%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99862 | -2.1236 | 0.98342 | -3.454 | -5.0156 | 5.0156 | 9.0901 | 1.7161 | -0.24792 | 2.655% | -2.655%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.9977 | -2.1306 | 0.9824 | -3.4722 | -5.1472 | 5.1472 | 9.1475 | 1.7233 | -0.25649 | 2.728% | -2.728%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99662 | -2.1758 | 0.98099 | -3.5474 | -5.2367 | 5.2367 | 9.3276 | 1.7543 | -0.26642 | 2.777% | -2.777%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99531 | -2.2733 | 0.97911 | -3.7021 | -5.263 | 5.263 | 9.6038 | 1.8032 | -0.27916 | 2.825% | -2.825%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99493 | -2.3062 | 0.97853 | -3.7533 | -5.263 | 5.263 | 9.7175 | 1.8243 | -0.2825 | 2.825% | -2.825%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99504 | -2.2967 | 0.9787 | -3.7384 | -5.263 | 5.263 | 9.6845 | 1.8182 | -0.28153 | 2.825% | -2.825%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.9954 | -2.266 | 0.97924 | -3.6907 | -5.263 | 5.263 | 9.5786 | 1.7985 | -0.27842 | 2.825% | -2.825%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99616 | -2.1994 | 0.98042 | -3.5871 | -5.263 | 5.263 | 9.3483 | 1.7558 | -0.27166 | 2.824% | -2.824%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99769 | -2.0647 | 0.98278 | -3.3778 | -5.263 | 5.263 | 8.881 | 1.6689 | -0.25795 | 2.823% | -2.823%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99955 | -1.8996 | 0.98566 | -3.1218 | -5.263 | 5.263 | 8.3059 | 1.5618 | -0.2411 | 2.821% | -2.821%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0011 | -1.7607 | 0.98806 | -2.9069 | -5.263 | 5.263 | 7.8201 | 1.4713 | -0.22688 | 2.819% | -2.819%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0021 | -1.669 | 0.98964 | -2.7653 | -5.263 | 5.263 | 7.4985 | 1.4113 | -0.21748 | 2.819% | -2.819%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.614 | 0.99058 | -2.6804 | -5.263 | 5.263 | 7.3052 | 1.3752 | -0.21183 | 2.818% | -2.818%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5837 | 0.9911 | -2.6335 | -5.263 | 5.263 | 7.1983 | 1.3552 | -0.20871 | 2.818% | -2.818%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0031 | -1.5812 | 0.99114 | -2.6297 | -5.263 | 5.263 | 7.1895 | 1.3536 | -0.20845 | 2.818% | -2.818%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0026 | -1.6268 | 0.99036 | -2.7 | -5.263 | 5.263 | 7.3499 | 1.3835 | -0.21313 | 2.818% | -2.818%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0013 | -1.7438 | 0.98835 | -2.8808 | -5.263 | 5.263 | 7.7609 | 1.4602 | -0.22515 | 2.819% | -2.819%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.9993 | -1.9216 | 0.98528 | -3.1559 | -5.263 | 5.263 | 8.3827 | 1.5762 | -0.24334 | 2.821% | -2.821%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99794 | -2.0423 | 0.98317 | -3.3431 | -5.263 | 5.263 | 8.8033 | 1.6545 | -0.25567 | 2.822% | -2.822%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99756 | -2.0764 | 0.98258 | -3.3961 | -5.263 | 5.263 | 8.9219 | 1.6765 | -0.25914 | 2.823% | -2.823%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99743 | -2.0905 | 0.98237 | -3.4176 | -5.2577 | 5.2577 | 8.9697 | 1.6856 | -0.26026 | 2.82% | -2.82%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2419 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99742 | -2.1003 | 0.9823 | -3.432 | -5.2419 | 5.2419 | 9.0007 | 1.6918 | -0.26031 | 2.811% | -2.811%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99741 | -2.1102 | 0.98223 | -3.4463 | -5.2262 | 5.2262 | 9.0316 | 1.698 | -0.26035 | 2.802% | -2.802%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99731 | -2.1186 | 0.98209 | -3.4594 | -5.2262 | 5.2262 | 9.0608 | 1.7034 | -0.2612 | 2.802% | -2.802%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2367 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99743 | -2.1046 | 0.98225 | -3.4368 | -5.2367 | 5.2367 | 9.0787 | 1.708 | -0.25931 | 2.777% | -2.777%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2525 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99713 | -2.1215 | 0.98184 | -3.4641 | -5.2525 | 5.2525 | 9.142 | 1.7193 | -0.26196 | 2.786% | -2.786%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99627 | -2.1925 | 0.98057 | -3.5761 | -5.2577 | 5.2577 | 9.3234 | 1.7513 | -0.27063 | 2.821% | -2.821%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99531 | -2.2733 | 0.97911 | -3.7021 | -5.263 | 5.263 | 9.6038 | 1.8032 | -0.27916 | 2.825% | -2.825%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99493 | -2.3062 | 0.97853 | -3.7533 | -5.263 | 5.263 | 9.7175 | 1.8243 | -0.2825 | 2.825% | -2.825%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99504 | -2.2967 | 0.9787 | -3.7384 | -5.263 | 5.263 | 9.6845 | 1.8182 | -0.28153 | 2.825% | -2.825%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.9954 | -2.266 | 0.97924 | -3.6907 | -5.263 | 5.263 | 9.5786 | 1.7985 | -0.27842 | 2.825% | -2.825%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99616 | -2.1994 | 0.98042 | -3.5871 | -5.263 | 5.263 | 9.3483 | 1.7558 | -0.27166 | 2.824% | -2.824%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99769 | -2.0647 | 0.98278 | -3.3778 | -5.263 | 5.263 | 8.881 | 1.6689 | -0.25795 | 2.823% | -2.823%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99955 | -1.8996 | 0.98566 | -3.1218 | -5.263 | 5.263 | 8.3059 | 1.5618 | -0.2411 | 2.821% | -2.821%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0011 | -1.7607 | 0.98806 | -2.9069 | -5.263 | 5.263 | 7.8201 | 1.4713 | -0.22688 | 2.819% | -2.819%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4761 | 0.97729 | -2.5916 | -7.5395 | 10.526 | 7.3999 | 1.342 | -0.31609 | 4.097% | -4.097%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99025 | -1.4212 | 0.97824 | -2.5062 | -7.5369 | 10.526 | 7.2092 | 1.3079 | -0.30776 | 4.094% | -4.094%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3908 | 0.97876 | -2.4591 | -7.5358 | 10.526 | 7.1038 | 1.289 | -0.30317 | 4.093% | -4.093%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3884 | 0.9788 | -2.4552 | -7.5357 | 10.526 | 7.0952 | 1.2875 | -0.30279 | 4.093% | -4.093%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4339 | 0.97802 | -2.5259 | -7.5375 | 10.526 | 7.2533 | 1.3158 | -0.30969 | 4.095% | -4.095%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5508 | 0.976 | -2.7078 | -7.5419 | 10.526 | 7.6586 | 1.3882 | -0.32739 | 4.1% | -4.1%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5049 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7284 | 0.97291 | -2.9847 | -7.5487 | 10.5049 | 8.2717 | 1.4976 | -0.35427 | 4.107% | -4.107%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.2313 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.849 | 0.97079 | -3.1731 | -7.5532 | 10.2313 | 8.6865 | 1.5714 | -0.37252 | 4.112% | -4.112%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.98501 | -1.8831 | 0.97019 | -3.2264 | -7.5544 | 9.4102 | 8.8033 | 1.5922 | -0.37766 | 4.114% | -4.114%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.284 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99486 | -2.0567 | 0.9798 | -3.3916 | -5.7255 | 8.284 | 8.945 | 1.6679 | -0.28496 | 3.087% | -3.087%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.1472 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0653 | 0.97965 | -3.405 | -5.7262 | 7.1472 | 8.9751 | 1.6734 | -0.28594 | 3.088% | -3.088%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.5156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.074 | 0.97949 | -3.4186 | -5.7264 | 6.5156 | 9.0051 | 1.6789 | -0.28693 | 3.088% | -3.088%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.7051 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0824 | 0.97934 | -3.4316 | -5.7267 | 6.7051 | 9.0341 | 1.6843 | -0.28788 | 3.088% | -3.088%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.0103 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0869 | 0.97926 | -3.4386 | -5.7268 | 7.0103 | 9.0496 | 1.6871 | -0.28838 | 3.088% | -3.088%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.884 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1054 | 0.97894 | -3.4674 | -5.7274 | 7.884 | 9.1135 | 1.6989 | -0.29048 | 3.089% | -3.089%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.9155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1587 | 0.97799 | -3.5504 | -5.7289 | 8.9155 | 9.2975 | 1.7327 | -0.29651 | 3.091% | -3.091%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.8418 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2399 | 0.97654 | -3.6771 | -5.7312 | 9.8418 | 9.5773 | 1.7841 | -0.3057 | 3.093% | -3.093%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.3786 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2729 | 0.97595 | -3.7285 | -5.7322 | 10.3786 | 9.6906 | 1.8049 | -0.30942 | 3.094% | -3.094%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5155 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.2633 | 0.97612 | -3.7135 | -5.7319 | 10.5155 | 9.6577 | 1.7989 | -0.30834 | 3.094% | -3.094%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2326 | 0.97667 | -3.6657 | -5.731 | 10.526 | 9.5521 | 1.7795 | -0.30487 | 3.093% | -3.093%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.166 | 0.97786 | -3.5618 | -5.7291 | 10.526 | 9.3227 | 1.7374 | -0.29733 | 3.091% | -3.091%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8714 | 0.97039 | -3.208 | -7.5544 | 10.526 | 8.7631 | 1.585 | -0.37589 | 4.113% | -4.113%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7064 | 0.97329 | -2.9504 | -7.5477 | 10.526 | 8.196 | 1.4841 | -0.35095 | 4.106% | -4.106%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5677 | 0.97571 | -2.7341 | -7.5424 | 10.526 | 7.717 | 1.3987 | -0.32995 | 4.1% | -4.1%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4761 | 0.97729 | -2.5916 | -7.539 | 10.526 | 7.3999 | 1.342 | -0.31609 | 4.096% | -4.096%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99025 | -1.4212 | 0.97824 | -2.5062 | -7.5369 | 10.526 | 7.2092 | 1.3079 | -0.30776 | 4.094% | -4.094%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3908 | 0.97876 | -2.4591 | -7.5358 | 10.526 | 7.1038 | 1.289 | -0.30317 | 4.093% | -4.093%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3884 | 0.9788 | -2.4552 | -7.5357 | 10.526 | 7.0952 | 1.2875 | -0.30279 | 4.093% | -4.093%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4339 | 0.97802 | -2.5259 | -7.5375 | 10.526 | 7.2533 | 1.3158 | -0.30969 | 4.095% | -4.095%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5508 | 0.976 | -2.7078 | -7.5419 | 10.526 | 7.6586 | 1.3882 | -0.32739 | 4.1% | -4.1%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7284 | 0.97291 | -2.9847 | -7.5487 | 10.526 | 8.2717 | 1.4976 | -0.35427 | 4.107% | -4.107%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.849 | 0.97079 | -3.1731 | -7.5532 | 10.5155 | 8.6865 | 1.5714 | -0.37252 | 4.112% | -4.112%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.98501 | -1.8831 | 0.97019 | -3.2264 | -7.5544 | 10.4102 | 8.8033 | 1.5922 | -0.37766 | 4.114% | -4.114%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99486 | -2.0567 | 0.9798 | -3.3916 | -5.7255 | 10.1892 | 8.945 | 1.6679 | -0.28496 | 3.087% | -3.087%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0653 | 0.97965 | -3.405 | -5.7262 | 9.9576 | 8.9751 | 1.6734 | -0.28594 | 3.088% | -3.088%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.074 | 0.97949 | -3.4186 | -5.7264 | 9.8313 | 9.0051 | 1.6789 | -0.28693 | 3.088% | -3.088%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0824 | 0.97934 | -3.4316 | -5.7267 | 9.9681 | 9.0341 | 1.6843 | -0.28788 | 3.088% | -3.088%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0869 | 0.97926 | -3.4386 | -5.7268 | 10.0313 | 9.0496 | 1.6871 | -0.28838 | 3.088% | -3.088%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1054 | 0.97894 | -3.4674 | -5.7274 | 10.2944 | 9.1135 | 1.6989 | -0.29048 | 3.089% | -3.089%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1587 | 0.97799 | -3.5504 | -5.7289 | 10.4734 | 9.2975 | 1.7327 | -0.29651 | 3.091% | -3.091%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2399 | 0.97654 | -3.6771 | -5.7312 | 10.526 | 9.5773 | 1.7841 | -0.3057 | 3.093% | -3.093%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2729 | 0.97595 | -3.7285 | -5.7322 | 10.526 | 9.6906 | 1.8049 | -0.30942 | 3.094% | -3.094%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.2633 | 0.97612 | -3.7135 | -5.7319 | 10.526 | 9.6577 | 1.7989 | -0.30834 | 3.094% | -3.094%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2326 | 0.97667 | -3.6657 | -5.731 | 10.526 | 9.5521 | 1.7795 | -0.30487 | 3.093% | -3.093%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.166 | 0.97786 | -3.5618 | -5.7291 | 10.526 | 9.3227 | 1.7374 | -0.29733 | 3.091% | -3.091%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8714 | 0.97039 | -3.208 | -7.5544 | 10.526 | 8.7631 | 1.585 | -0.37589 | 4.113% | -4.113%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7064 | 0.97329 | -2.9504 | -7.5477 | 10.526 | 8.196 | 1.4841 | -0.35095 | 4.106% | -4.106%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5677 | 0.97571 | -2.7341 | -7.5424 | 10.526 | 7.717 | 1.3987 | -0.32995 | 4.1% | -4.1%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4761 | 0.97729 | -2.5916 | -7.539 | 10.526 | 7.3999 | 1.342 | -0.31609 | 4.096% | -4.096%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99025 | -1.4212 | 0.97824 | -2.5062 | -7.5369 | 10.526 | 7.2092 | 1.3079 | -0.30776 | 4.094% | -4.094%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3908 | 0.97876 | -2.4591 | -7.5358 | 10.526 | 7.1038 | 1.289 | -0.30317 | 4.093% | -4.093%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3884 | 0.9788 | -2.4552 | -7.5357 | 10.526 | 7.0952 | 1.2875 | -0.30279 | 4.093% | -4.093%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4339 | 0.97802 | -2.5259 | -7.5375 | 10.526 | 7.2533 | 1.3158 | -0.30969 | 4.095% | -4.095%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5508 | 0.976 | -2.7078 | -7.5419 | 10.526 | 7.6586 | 1.3882 | -0.32739 | 4.1% | -4.1%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7284 | 0.97291 | -2.9847 | -7.5487 | 10.526 | 8.2717 | 1.4976 | -0.35427 | 4.107% | -4.107%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.849 | 0.97079 | -3.1731 | -7.5532 | 10.526 | 8.6865 | 1.5714 | -0.37252 | 4.112% | -4.112%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.98501 | -1.8831 | 0.97019 | -3.2264 | -7.5544 | 10.526 | 8.8033 | 1.5922 | -0.37766 | 4.114% | -4.114%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99486 | -2.0567 | 0.9798 | -3.3916 | -5.7255 | 10.5155 | 8.945 | 1.6679 | -0.28496 | 3.087% | -3.087%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4839 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0653 | 0.97965 | -3.405 | -5.7262 | 10.4839 | 8.9751 | 1.6734 | -0.28594 | 3.088% | -3.088%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.074 | 0.97949 | -3.4186 | -5.7264 | 10.4523 | 9.0051 | 1.6789 | -0.28693 | 3.088% | -3.088%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0824 | 0.97934 | -3.4316 | -5.7267 | 10.4523 | 9.0341 | 1.6843 | -0.28788 | 3.088% | -3.088%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4734 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0869 | 0.97926 | -3.4386 | -5.7268 | 10.4734 | 9.0496 | 1.6871 | -0.28838 | 3.088% | -3.088%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5049 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1054 | 0.97894 | -3.4674 | -5.7274 | 10.5049 | 9.1135 | 1.6989 | -0.29048 | 3.089% | -3.089%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1587 | 0.97799 | -3.5504 | -5.7289 | 10.5155 | 9.2975 | 1.7327 | -0.29651 | 3.091% | -3.091%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2399 | 0.97654 | -3.6771 | -5.7312 | 10.526 | 9.5773 | 1.7841 | -0.3057 | 3.093% | -3.093%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2729 | 0.97595 | -3.7285 | -5.7322 | 10.526 | 9.6906 | 1.8049 | -0.30942 | 3.094% | -3.094%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.2633 | 0.97612 | -3.7135 | -5.7319 | 10.526 | 9.6577 | 1.7989 | -0.30834 | 3.094% | -3.094%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2326 | 0.97667 | -3.6657 | -5.731 | 10.526 | 9.5521 | 1.7795 | -0.30487 | 3.093% | -3.093%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.166 | 0.97786 | -3.5618 | -5.7291 | 10.526 | 9.3227 | 1.7374 | -0.29733 | 3.091% | -3.091%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8714 | 0.97039 | -3.208 | -7.5544 | 10.526 | 8.7631 | 1.585 | -0.37589 | 4.113% | -4.113%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7064 | 0.97329 | -2.9504 | -7.5477 | 10.526 | 8.196 | 1.4841 | -0.35095 | 4.106% | -4.106%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5677 | 0.97571 | -2.7341 | -7.5424 | 10.526 | 7.717 | 1.3987 | -0.32995 | 4.1% | -4.1%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0168 | -3.1788 | 1.0168 | -3.1788 | 0.97509 | -2.3937 | 0.97509 | -2.3937 | -5.263 | 5.263 | 7.3823 | 1.3297 | -0.33368 | 4.325% | -4.325%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97605 | -2.3071 | 0.97605 | -2.3071 | -5.263 | 5.263 | 7.1923 | 1.296 | -0.32474 | 4.32% | -4.32%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97659 | -2.2594 | 0.97659 | -2.2594 | -5.263 | 5.263 | 7.0872 | 1.2774 | -0.3198 | 4.318% | -4.318%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97663 | -2.2555 | 0.97663 | -2.2555 | -5.263 | 5.263 | 7.0786 | 1.2759 | -0.3194 | 4.317% | -4.317%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97583 | -2.3271 | 0.97583 | -2.3271 | -5.263 | 5.263 | 7.2362 | 1.3038 | -0.32681 | 4.321% | -4.321%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97377 | -2.5119 | 0.97377 | -2.5119 | -5.263 | 5.263 | 7.6402 | 1.3753 | -0.34584 | 4.331% | -4.331%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2525 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.2525 | 5.2525 | 8.2457 | 1.4793 | -0.38031 | 4.409% | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1156 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 5.1156 | 8.679 | 1.5661 | -0.37996 | 4.194% | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.7051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97259 | -3.1094 | 0.97259 | -3.1094 | -4.7051 | 4.7051 | 8.8263 | 1.6084 | -0.35469 | 3.863% | -3.863%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.142 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97712 | -3.1972 | 0.97712 | -3.1972 | -4.142 | 4.142 | 8.9192 | 1.6495 | -0.31077 | 3.367% | -3.367%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5736 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.9813 | -3.3257 | 0.9813 | -3.3257 | -3.5736 | 3.5736 | 8.991 | 1.6848 | -0.26997 | 2.915% | -2.915%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.2578 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.98368 | -3.3863 | 0.98368 | -3.3863 | -3.2578 | 3.2578 | 9.0456 | 1.708 | -0.24636 | 2.651% | -2.651%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.3525 | 5 | 1.0089 | -3.8658 | 1.0089 | -3.8658 | 0.98277 | -3.3851 | 0.98277 | -3.3851 | -3.3525 | 3.3525 | 9.0675 | 1.7082 | -0.25453 | 2.73% | -2.73%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5052 | 5 | 1.0088 | -3.8727 | 1.0088 | -3.8727 | 0.98147 | -3.3691 | 0.98147 | -3.3691 | -3.5052 | 3.5052 | 9.0711 | 1.7025 | -0.26689 | 2.858% | -2.858%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.942 | 5 | 1.0085 | -3.9012 | 1.0085 | -3.9012 | 0.97792 | -3.2983 | 0.97792 | -3.2983 | -3.942 | 3.942 | 9.1036 | 1.6918 | -0.30042 | 3.195% | -3.195%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.4578 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97259 | -3.3242 | 0.97259 | -3.3242 | -4.4578 | 4.4578 | 9.2434 | 1.694 | -0.35062 | 3.655% | -3.655%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.9209 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 4.9209 | 9.5097 | 1.7357 | -0.3733 | 3.777% | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1893 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 5.1893 | 9.6283 | 1.7602 | -0.37171 | 3.717% | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2577 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 5.2577 | 9.5938 | 1.7531 | -0.37219 | 3.735% | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 5.263 | 9.4834 | 1.7302 | -0.37364 | 3.791% | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 5.263 | 9.2437 | 1.6809 | -0.37629 | 3.912% | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 5.263 | 8.7593 | 1.5824 | -0.37966 | 4.154% | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97101 | -2.7601 | 0.97101 | -2.7601 | -5.263 | 5.263 | 8.1758 | 1.4699 | -0.37122 | 4.343% | -4.343%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97347 | -2.5387 | 0.97347 | -2.5387 | -5.263 | 5.263 | 7.6984 | 1.3856 | -0.3486 | 4.332% | -4.332%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97509 | -2.3937 | 0.97509 | -2.3937 | -5.263 | 5.263 | 7.3823 | 1.3297 | -0.33369 | 4.325% | -4.325%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97605 | -2.3071 | 0.97605 | -2.3071 | -5.263 | 5.263 | 7.1923 | 1.296 | -0.32474 | 4.32% | -4.32%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97659 | -2.2594 | 0.97659 | -2.2594 | -5.263 | 5.263 | 7.0872 | 1.2774 | -0.3198 | 4.318% | -4.318%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97663 | -2.2555 | 0.97663 | -2.2555 | -5.263 | 5.263 | 7.0786 | 1.2759 | -0.3194 | 4.317% | -4.317%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97583 | -2.3271 | 0.97583 | -2.3271 | -5.263 | 5.263 | 7.2362 | 1.3038 | -0.32681 | 4.321% | -4.321%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97377 | -2.5119 | 0.97377 | -2.5119 | -5.263 | 5.263 | 7.6402 | 1.3753 | -0.34584 | 4.331% | -4.331%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.263 | 5.263 | 8.2457 | 1.4793 | -0.38031 | 4.409% | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 5.2577 | 8.679 | 1.5661 | -0.37996 | 4.194% | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 5.2051 | 8.8015 | 1.5909 | -0.37947 | 4.133% | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 5.0946 | 8.8508 | 1.6009 | -0.37923 | 4.109% | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 4.9788 | 8.8819 | 1.6072 | -0.37906 | 4.093% | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9156 | 4.9156 | 8.9131 | 1.6135 | -0.37888 | 4.077% | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 4.9841 | 8.9433 | 1.6196 | -0.3787 | 4.062% | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 5.0156 | 8.9594 | 1.6229 | -0.37859 | 4.054% | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 5.1472 | 9.0259 | 1.6364 | -0.37814 | 4.021% | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 5.2367 | 9.2175 | 1.6756 | -0.37654 | 3.925% | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 5.263 | 9.5097 | 1.7357 | -0.3733 | 3.777% | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 5.263 | 9.6283 | 1.7602 | -0.37171 | 3.717% | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 5.263 | 9.5938 | 1.7531 | -0.37219 | 3.735% | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 5.263 | 9.4834 | 1.7302 | -0.37364 | 3.791% | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 5.263 | 9.2437 | 1.6809 | -0.37629 | 3.912% | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 5.263 | 8.7593 | 1.5824 | -0.37966 | 4.154% | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97101 | -2.7601 | 0.97101 | -2.7601 | -5.263 | 5.263 | 8.1758 | 1.4699 | -0.37122 | 4.343% | -4.343%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97347 | -2.5387 | 0.97347 | -2.5387 | -5.263 | 5.263 | 7.6984 | 1.3856 | -0.3486 | 4.332% | -4.332%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97509 | -2.3937 | 0.97509 | -2.3937 | -5.263 | 5.263 | 7.3823 | 1.3297 | -0.33369 | 4.325% | -4.325%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97605 | -2.3071 | 0.97605 | -2.3071 | -5.263 | 5.263 | 7.1923 | 1.296 | -0.32474 | 4.32% | -4.32%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97659 | -2.2594 | 0.97659 | -2.2594 | -5.263 | 5.263 | 7.0872 | 1.2774 | -0.3198 | 4.318% | -4.318%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97663 | -2.2555 | 0.97663 | -2.2555 | -5.263 | 5.263 | 7.0786 | 1.2759 | -0.3194 | 4.317% | -4.317%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97583 | -2.3271 | 0.97583 | -2.3271 | -5.263 | 5.263 | 7.2362 | 1.3038 | -0.32681 | 4.321% | -4.321%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97377 | -2.5119 | 0.97377 | -2.5119 | -5.263 | 5.263 | 7.6402 | 1.3753 | -0.34584 | 4.331% | -4.331%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.263 | 5.263 | 8.2457 | 1.4793 | -0.38031 | 4.409% | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 5.263 | 8.679 | 1.5661 | -0.37996 | 4.194% | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 5.263 | 8.8015 | 1.5909 | -0.37947 | 4.133% | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 5.2577 | 8.8508 | 1.6009 | -0.37923 | 4.109% | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2419 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 5.2419 | 8.8819 | 1.6072 | -0.37906 | 4.093% | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 5.2262 | 8.9131 | 1.6135 | -0.37888 | 4.077% | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 5.2262 | 8.9433 | 1.6196 | -0.3787 | 4.062% | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2367 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 5.2367 | 8.9594 | 1.6229 | -0.37859 | 4.054% | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2525 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 5.2525 | 9.0259 | 1.6364 | -0.37814 | 4.021% | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 5.2577 | 9.2175 | 1.6756 | -0.37654 | 3.925% | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 5.263 | 9.5097 | 1.7357 | -0.3733 | 3.777% | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 5.263 | 9.6283 | 1.7602 | -0.37171 | 3.717% | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 5.263 | 9.5938 | 1.7531 | -0.37219 | 3.735% | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 5.263 | 9.4834 | 1.7302 | -0.37364 | 3.791% | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 5.263 | 9.2437 | 1.6809 | -0.37629 | 3.912% | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 5.263 | 8.7593 | 1.5824 | -0.37966 | 4.154% | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97101 | -2.7601 | 0.97101 | -2.7601 | -5.263 | 5.263 | 8.1758 | 1.4699 | -0.37122 | 4.343% | -4.343%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97347 | -2.5387 | 0.97347 | -2.5387 | -5.263 | 5.263 | 7.6984 | 1.3856 | -0.3486 | 4.332% | -4.332%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.3203 | 0.97 | -2.3203 | -5.8537 | 10.526 | 7.3417 | 1.3015 | -0.37426 | 4.85% | -4.85%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2192 | 0.97 | -2.2192 | -5.9647 | 10.526 | 7.1452 | 1.2634 | -0.37175 | 4.945% | -4.945%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1635 | 0.97 | -2.1635 | -6.0257 | 10.526 | 7.0368 | 1.2425 | -0.37018 | 4.998% | -4.998%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1589 | 0.97 | -2.1589 | -6.0306 | 10.526 | 7.028 | 1.2408 | -0.37005 | 5.002% | -5.002%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2426 | 0.97 | -2.2426 | -5.9391 | 10.526 | 7.1906 | 1.2722 | -0.37238 | 4.924% | -4.924%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4579 | 0.97 | -2.4579 | -5.7019 | 10.526 | 7.609 | 1.3536 | -0.37702 | 4.721% | -4.721%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5049 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.3356 | 10.5049 | 8.2457 | 1.4793 | -0.38033 | 4.409% | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.2313 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 10.2313 | 8.679 | 1.5661 | -0.37996 | 4.194% | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 9.4102 | 8.8015 | 1.5909 | -0.37947 | 4.133% | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.284 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 8.284 | 8.8508 | 1.6009 | -0.37923 | 4.109% | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.1472 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 7.1472 | 8.8819 | 1.6072 | -0.37906 | 4.093% | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.5156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 6.5156 | 8.9131 | 1.6135 | -0.37888 | 4.077% | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.7051 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 6.7051 | 8.9433 | 1.6196 | -0.3787 | 4.062% | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.0103 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 7.0103 | 8.9594 | 1.6229 | -0.37859 | 4.054% | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.884 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 7.884 | 9.0259 | 1.6364 | -0.37814 | 4.021% | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.9155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 8.9155 | 9.2175 | 1.6756 | -0.37654 | 3.925% | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.8418 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 9.8418 | 9.5097 | 1.7357 | -0.3733 | 3.777% | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.3786 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 10.3786 | 9.6283 | 1.7602 | -0.37171 | 3.717% | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5155 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 10.5155 | 9.5938 | 1.7531 | -0.37219 | 3.735% | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 10.526 | 9.4834 | 1.7302 | -0.37364 | 3.791% | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 10.526 | 9.2437 | 1.6809 | -0.37629 | 3.912% | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 10.526 | 8.7593 | 1.5824 | -0.37966 | 4.154% | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7456 | 0.97 | -2.7456 | -5.3813 | 10.526 | 8.1668 | 1.4636 | -0.38015 | 4.448% | -4.448%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.4891 | 0.97 | -2.4891 | -5.6674 | 10.526 | 7.6695 | 1.3654 | -0.37752 | 4.691% | -4.691%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.3203 | 0.97 | -2.3203 | -5.8538 | 10.526 | 7.3417 | 1.3015 | -0.37427 | 4.851% | -4.851%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2192 | 0.97 | -2.2192 | -5.9647 | 10.526 | 7.1452 | 1.2634 | -0.37175 | 4.945% | -4.945%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1635 | 0.97 | -2.1635 | -6.0257 | 10.526 | 7.0368 | 1.2425 | -0.37018 | 4.998% | -4.998%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1589 | 0.97 | -2.1589 | -6.0306 | 10.526 | 7.028 | 1.2408 | -0.37005 | 5.002% | -5.002%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2426 | 0.97 | -2.2426 | -5.9391 | 10.526 | 7.1906 | 1.2722 | -0.37238 | 4.924% | -4.924%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4579 | 0.97 | -2.4579 | -5.7019 | 10.526 | 7.609 | 1.3536 | -0.37702 | 4.721% | -4.721%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.3356 | 10.526 | 8.2457 | 1.4793 | -0.38033 | 4.409% | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 10.5155 | 8.679 | 1.5661 | -0.37996 | 4.194% | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 10.4102 | 8.8015 | 1.5909 | -0.37947 | 4.133% | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 10.1892 | 8.8508 | 1.6009 | -0.37923 | 4.109% | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 9.9576 | 8.8819 | 1.6072 | -0.37906 | 4.093% | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 9.8313 | 8.9131 | 1.6135 | -0.37888 | 4.077% | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 9.9681 | 8.9433 | 1.6196 | -0.3787 | 4.062% | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 10.0313 | 8.9594 | 1.6229 | -0.37859 | 4.054% | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 10.2944 | 9.0259 | 1.6364 | -0.37814 | 4.021% | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 10.4734 | 9.2175 | 1.6756 | -0.37654 | 3.925% | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 10.526 | 9.5097 | 1.7357 | -0.3733 | 3.777% | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 10.526 | 9.6283 | 1.7602 | -0.37171 | 3.717% | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 10.526 | 9.5938 | 1.7531 | -0.37219 | 3.735% | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 10.526 | 9.4834 | 1.7302 | -0.37364 | 3.791% | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 10.526 | 9.2437 | 1.6809 | -0.37629 | 3.912% | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 10.526 | 8.7593 | 1.5824 | -0.37966 | 4.154% | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7456 | 0.97 | -2.7456 | -5.3813 | 10.526 | 8.1668 | 1.4636 | -0.38015 | 4.448% | -4.448%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.4891 | 0.97 | -2.4891 | -5.6674 | 10.526 | 7.6695 | 1.3654 | -0.37752 | 4.691% | -4.691%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.3203 | 0.97 | -2.3203 | -5.8538 | 10.526 | 7.3417 | 1.3015 | -0.37427 | 4.851% | -4.851%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2192 | 0.97 | -2.2192 | -5.9647 | 10.526 | 7.1452 | 1.2634 | -0.37175 | 4.945% | -4.945%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1635 | 0.97 | -2.1635 | -6.0257 | 10.526 | 7.0368 | 1.2425 | -0.37018 | 4.998% | -4.998%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1589 | 0.97 | -2.1589 | -6.0306 | 10.526 | 7.028 | 1.2408 | -0.37005 | 5.002% | -5.002%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2426 | 0.97 | -2.2426 | -5.9391 | 10.526 | 7.1906 | 1.2722 | -0.37238 | 4.924% | -4.924%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4579 | 0.97 | -2.4579 | -5.7019 | 10.526 | 7.609 | 1.3536 | -0.37702 | 4.721% | -4.721%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.3356 | 10.526 | 8.2457 | 1.4793 | -0.38033 | 4.409% | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 10.526 | 8.679 | 1.5661 | -0.37996 | 4.194% | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 10.526 | 8.8015 | 1.5909 | -0.37947 | 4.133% | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 10.5155 | 8.8508 | 1.6009 | -0.37923 | 4.109% | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4839 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 10.4839 | 8.8819 | 1.6072 | -0.37906 | 4.093% | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 10.4523 | 8.9131 | 1.6135 | -0.37888 | 4.077% | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 10.4523 | 8.9433 | 1.6196 | -0.3787 | 4.062% | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4734 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 10.4734 | 8.9594 | 1.6229 | -0.37859 | 4.054% | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5049 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 10.5049 | 9.0259 | 1.6364 | -0.37814 | 4.021% | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 10.5155 | 9.2175 | 1.6756 | -0.37654 | 3.925% | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 10.526 | 9.5097 | 1.7357 | -0.3733 | 3.777% | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 10.526 | 9.6283 | 1.7602 | -0.37171 | 3.717% | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 10.526 | 9.5938 | 1.7531 | -0.37219 | 3.735% | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 10.526 | 9.4834 | 1.7302 | -0.37364 | 3.791% | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 10.526 | 9.2437 | 1.6809 | -0.37629 | 3.912% | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 10.526 | 8.7593 | 1.5824 | -0.37966 | 4.154% | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7456 | 0.97 | -2.7456 | -5.3813 | 10.526 | 8.1668 | 1.4636 | -0.38015 | 4.448% | -4.448%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.4891 | 0.97 | -2.4891 | -5.6674 | 10.526 | 7.6695 | 1.3654 | -0.37752 | 4.691% | -4.691%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0369 | -1.0325 | 0.99876 | -2.9186 | 1.0235 | -0.90736 | 0.9859 | -2.8254 | -5.263 | 5.263 | 7.6172 | 3.5941 | -0.098845 | 1.281% | -1.281%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.88064 | 0.98735 | -2.7457 | -5.263 | 5.263 | 7.4207 | 3.5018 | -0.096259 | 1.281% | -1.281%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0241 | -0.86588 | 0.98814 | -2.7018 | -5.263 | 5.263 | 7.3121 | 3.4507 | -0.0949 | 1.281% | -1.281%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0242 | -0.86467 | 0.98821 | -2.6982 | -5.263 | 5.263 | 7.3032 | 3.4465 | -0.094788 | 1.281% | -1.281%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.88681 | 0.98701 | -2.7641 | -5.263 | 5.263 | 7.4662 | 3.5232 | -0.096826 | 1.28% | -1.28%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.023 | -0.94372 | 0.98393 | -2.934 | -5.263 | 5.263 | 7.884 | 3.7198 | -0.10203 | 1.278% | -1.278%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0217 | -1.0305 | 0.97923 | -3.1934 | -5.2525 | 5.2525 | 8.5164 | 4.0174 | -0.10964 | 1.271% | -1.271%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9315 | 5.1156 | 8.9725 | 4.2602 | -0.086487 | 0.9547% | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 4.7051 | 9.0934 | 4.3174 | -0.087614 | 0.9543% | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.142 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 4.142 | 9.1419 | 4.3404 | -0.088066 | 0.9541% | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0246 | -1.1585 | 0.9785 | -3.4864 | -3.5736 | 3.5736 | 9.1808 | 4.367 | -0.080159 | 0.8656% | -0.8656%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0253 | -1.1698 | 0.97904 | -3.5027 | -3.2578 | 3.2578 | 9.2188 | 4.3923 | -0.073174 | 0.7875% | -0.7875%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.025 | -1.1718 | 0.97858 | -3.5139 | -3.3525 | 3.3525 | 9.2464 | 4.4032 | -0.075579 | 0.8108% | -0.8108%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0246 | -1.1706 | 0.97808 | -3.5189 | -3.5052 | 3.5052 | 9.2588 | 4.4056 | -0.079221 | 0.8484% | -0.8484%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.942 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 3.942 | 9.3143 | 4.422 | -0.089671 | 0.9535% | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 4.4578 | 9.5026 | 4.5111 | -0.091419 | 0.9529% | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 4.9209 | 9.7889 | 4.6466 | -0.094076 | 0.9519% | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 5.1893 | 9.9049 | 4.7014 | -0.09515 | 0.9515% | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 5.2577 | 9.8712 | 4.6855 | -0.094836 | 0.9516% | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 5.263 | 9.7632 | 4.6344 | -0.093839 | 0.952% | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 5.263 | 9.5283 | 4.5233 | -0.091658 | 0.9528% | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 5.263 | 9.0518 | 4.2977 | -0.087226 | 0.9544% | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0218 | -1.0195 | 0.97979 | -3.1611 | -5.263 | 5.263 | 8.4381 | 3.9804 | -0.1089 | 1.274% | -1.274%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.95195 | 0.98348 | -2.9586 | -5.263 | 5.263 | 7.9442 | 3.7481 | -0.10278 | 1.277% | -1.277%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0235 | -0.90737 | 0.9859 | -2.8254 | -5.263 | 5.263 | 7.6173 | 3.5943 | -0.098713 | 1.279% | -1.279%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.88064 | 0.98735 | -2.7457 | -5.263 | 5.263 | 7.4207 | 3.5018 | -0.096259 | 1.281% | -1.281%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0241 | -0.86588 | 0.98814 | -2.7018 | -5.263 | 5.263 | 7.3121 | 3.4507 | -0.0949 | 1.281% | -1.281%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0242 | -0.86467 | 0.98821 | -2.6982 | -5.263 | 5.263 | 7.3032 | 3.4465 | -0.094788 | 1.281% | -1.281%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.88681 | 0.98701 | -2.7641 | -5.263 | 5.263 | 7.4662 | 3.5232 | -0.096826 | 1.28% | -1.28%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.023 | -0.94372 | 0.98393 | -2.934 | -5.263 | 5.263 | 7.884 | 3.7198 | -0.10203 | 1.278% | -1.278%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0216 | -1.0302 | 0.9792 | -3.1933 | -5.263 | 5.263 | 8.5161 | 4.0171 | -0.10986 | 1.274% | -1.274%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9315 | 5.2577 | 8.9725 | 4.2602 | -0.086487 | 0.9547% | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 5.2051 | 9.0934 | 4.3174 | -0.087614 | 0.9543% | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 5.0946 | 9.1419 | 4.3404 | -0.088066 | 0.9541% | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 4.9788 | 9.1726 | 4.3549 | -0.088353 | 0.954% | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 4.9156 | 9.2034 | 4.3695 | -0.088639 | 0.9539% | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 4.9841 | 9.2331 | 4.3836 | -0.088914 | 0.9538% | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 5.0156 | 9.2489 | 4.3911 | -0.089063 | 0.9538% | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 5.1472 | 9.3143 | 4.422 | -0.089671 | 0.9535% | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 5.2367 | 9.5026 | 4.5111 | -0.091419 | 0.9529% | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 5.263 | 9.7889 | 4.6466 | -0.094076 | 0.9519% | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 5.263 | 9.9049 | 4.7014 | -0.09515 | 0.9515% | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 5.263 | 9.8712 | 4.6855 | -0.094836 | 0.9516% | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 5.263 | 9.7632 | 4.6344 | -0.093839 | 0.952% | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 5.263 | 9.5283 | 4.5233 | -0.091658 | 0.9528% | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 5.263 | 9.0518 | 4.2977 | -0.087226 | 0.9544% | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0218 | -1.0195 | 0.97979 | -3.1611 | -5.263 | 5.263 | 8.4381 | 3.9804 | -0.1089 | 1.274% | -1.274%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.95195 | 0.98348 | -2.9586 | -5.263 | 5.263 | 7.9442 | 3.7481 | -0.10278 | 1.277% | -1.277%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0235 | -0.90737 | 0.9859 | -2.8254 | -5.263 | 5.263 | 7.6173 | 3.5943 | -0.098713 | 1.279% | -1.279%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.88064 | 0.98735 | -2.7457 | -5.263 | 5.263 | 7.4207 | 3.5018 | -0.096259 | 1.281% | -1.281%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0241 | -0.86588 | 0.98814 | -2.7018 | -5.263 | 5.263 | 7.3121 | 3.4507 | -0.0949 | 1.281% | -1.281%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0242 | -0.86467 | 0.98821 | -2.6982 | -5.263 | 5.263 | 7.3032 | 3.4465 | -0.094788 | 1.281% | -1.281%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.88681 | 0.98701 | -2.7641 | -5.263 | 5.263 | 7.4662 | 3.5232 | -0.096826 | 1.28% | -1.28%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.023 | -0.94372 | 0.98393 | -2.934 | -5.263 | 5.263 | 7.884 | 3.7198 | -0.10203 | 1.278% | -1.278%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0216 | -1.0302 | 0.9792 | -3.1933 | -5.263 | 5.263 | 8.5161 | 4.0171 | -0.10986 | 1.274% | -1.274%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9315 | 5.263 | 8.9725 | 4.2602 | -0.086487 | 0.9547% | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 5.263 | 9.0934 | 4.3174 | -0.087614 | 0.9543% | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 5.2577 | 9.1419 | 4.3404 | -0.088066 | 0.9541% | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 5.2419 | 9.1726 | 4.3549 | -0.088353 | 0.954% | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 5.2262 | 9.2034 | 4.3695 | -0.088639 | 0.9539% | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 5.2262 | 9.2331 | 4.3836 | -0.088914 | 0.9538% | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 5.2367 | 9.2489 | 4.3911 | -0.089063 | 0.9538% | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 5.2525 | 9.3143 | 4.422 | -0.089671 | 0.9535% | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 5.2577 | 9.5026 | 4.5111 | -0.091419 | 0.9529% | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 5.263 | 9.7889 | 4.6466 | -0.094076 | 0.9519% | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 5.263 | 9.9049 | 4.7014 | -0.09515 | 0.9515% | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 5.263 | 9.8712 | 4.6855 | -0.094836 | 0.9516% | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 5.263 | 9.7632 | 4.6344 | -0.093839 | 0.952% | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 5.263 | 9.5283 | 4.5233 | -0.091658 | 0.9528% | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 5.263 | 9.0518 | 4.2977 | -0.087226 | 0.9544% | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0218 | -1.0195 | 0.97979 | -3.1611 | -5.263 | 5.263 | 8.4381 | 3.9804 | -0.1089 | 1.274% | -1.274%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.95195 | 0.98348 | -2.9586 | -5.263 | 5.263 | 7.9442 | 3.7481 | -0.10278 | 1.277% | -1.277%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84943 | 0.97951 | -2.7916 | -7.7761 | 10.526 | 7.5685 | 3.5239 | -0.14752 | 1.912% | -1.912%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0101 | -0.7552 | 0.97397 | -2.6618 | -10.526 | 10.526 | 7.3215 | 3.3593 | -0.19546 | 2.6% | -2.6%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0103 | -0.7404 | 0.97476 | -2.6171 | -10.526 | 10.526 | 7.2143 | 3.3104 | -0.19269 | 2.601% | -2.601%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0103 | -0.73919 | 0.97483 | -2.6135 | -10.526 | 10.526 | 7.2055 | 3.3064 | -0.19246 | 2.602% | -2.602%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.01 | -0.76139 | 0.97364 | -2.6805 | -10.526 | 10.526 | 7.3664 | 3.3798 | -0.19662 | 2.6% | -2.6%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88586 | 0.97754 | -2.9012 | -7.7778 | 10.526 | 7.8334 | 3.6467 | -0.15255 | 1.91% | -1.91%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97254 | 0.97283 | -3.1631 | -7.7823 | 10.5049 | 8.4616 | 3.9375 | -0.16442 | 1.906% | -1.906%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9314 | 10.2313 | 8.9725 | 4.2602 | -0.086487 | 0.9547% | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 9.4102 | 9.0934 | 4.3174 | -0.087614 | 0.9543% | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.284 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 8.284 | 9.1419 | 4.3404 | -0.088066 | 0.9541% | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 7.1472 | 9.1726 | 4.3549 | -0.088353 | 0.954% | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 6.5156 | 9.2034 | 4.3695 | -0.088639 | 0.9539% | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 6.7051 | 9.2331 | 4.3836 | -0.088914 | 0.9538% | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 7.0103 | 9.2489 | 4.3911 | -0.089063 | 0.9538% | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.884 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 7.884 | 9.3143 | 4.422 | -0.089671 | 0.9535% | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 8.9155 | 9.5026 | 4.5111 | -0.091419 | 0.9529% | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 9.8418 | 9.7889 | 4.6466 | -0.094076 | 0.9519% | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 10.3786 | 9.9049 | 4.7014 | -0.09515 | 0.9515% | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 10.5155 | 9.8712 | 4.6855 | -0.094836 | 0.9516% | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 10.526 | 9.7632 | 4.6344 | -0.093839 | 0.952% | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 10.526 | 9.5283 | 4.5233 | -0.091658 | 0.9528% | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 10.526 | 9.0518 | 4.2977 | -0.087226 | 0.9544% | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96182 | 0.97341 | -3.1306 | -7.7817 | 10.526 | 8.384 | 3.9017 | -0.16296 | 1.907% | -1.907%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.8941 | 0.9771 | -2.9261 | -7.7783 | 10.526 | 7.8933 | 3.6744 | -0.15369 | 1.91% | -1.91%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84943 | 0.97951 | -2.7916 | -7.776 | 10.526 | 7.5685 | 3.5239 | -0.14752 | 1.912% | -1.912%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0101 | -0.7552 | 0.97397 | -2.6618 | -10.526 | 10.526 | 7.3215 | 3.3593 | -0.19546 | 2.6% | -2.6%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0103 | -0.7404 | 0.97476 | -2.6171 | -10.526 | 10.526 | 7.2143 | 3.3104 | -0.19269 | 2.601% | -2.601%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0103 | -0.73919 | 0.97483 | -2.6135 | -10.526 | 10.526 | 7.2055 | 3.3064 | -0.19246 | 2.602% | -2.602%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.01 | -0.76139 | 0.97364 | -2.6805 | -10.526 | 10.526 | 7.3664 | 3.3798 | -0.19662 | 2.6% | -2.6%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88586 | 0.97754 | -2.9012 | -7.7778 | 10.526 | 7.8334 | 3.6467 | -0.15255 | 1.91% | -1.91%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97254 | 0.97283 | -3.1631 | -7.7823 | 10.526 | 8.4616 | 3.9375 | -0.16442 | 1.906% | -1.906%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9314 | 10.5155 | 8.9725 | 4.2602 | -0.086487 | 0.9547% | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 10.4102 | 9.0934 | 4.3174 | -0.087614 | 0.9543% | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 10.1892 | 9.1419 | 4.3404 | -0.088066 | 0.9541% | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 9.9576 | 9.1726 | 4.3549 | -0.088353 | 0.954% | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 9.8313 | 9.2034 | 4.3695 | -0.088639 | 0.9539% | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 9.9681 | 9.2331 | 4.3836 | -0.088914 | 0.9538% | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 10.0313 | 9.2489 | 4.3911 | -0.089063 | 0.9538% | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 10.2944 | 9.3143 | 4.422 | -0.089671 | 0.9535% | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 10.4734 | 9.5026 | 4.5111 | -0.091419 | 0.9529% | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 10.526 | 9.7889 | 4.6466 | -0.094076 | 0.9519% | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 10.526 | 9.9049 | 4.7014 | -0.09515 | 0.9515% | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 10.526 | 9.8712 | 4.6855 | -0.094836 | 0.9516% | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 10.526 | 9.7632 | 4.6344 | -0.093839 | 0.952% | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 10.526 | 9.5283 | 4.5233 | -0.091658 | 0.9528% | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 10.526 | 9.0518 | 4.2977 | -0.087226 | 0.9544% | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96182 | 0.97341 | -3.1306 | -7.7817 | 10.526 | 8.384 | 3.9017 | -0.16296 | 1.907% | -1.907%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.8941 | 0.9771 | -2.9261 | -7.7783 | 10.526 | 7.8933 | 3.6744 | -0.15369 | 1.91% | -1.91%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84943 | 0.97951 | -2.7916 | -7.776 | 10.526 | 7.5685 | 3.5239 | -0.14752 | 1.912% | -1.912%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0101 | -0.7552 | 0.97397 | -2.6618 | -10.526 | 10.526 | 7.3215 | 3.3593 | -0.19546 | 2.6% | -2.6%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0103 | -0.7404 | 0.97476 | -2.6171 | -10.526 | 10.526 | 7.2143 | 3.3104 | -0.19269 | 2.601% | -2.601%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0103 | -0.73919 | 0.97483 | -2.6135 | -10.526 | 10.526 | 7.2055 | 3.3064 | -0.19246 | 2.602% | -2.602%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.01 | -0.76139 | 0.97364 | -2.6805 | -10.526 | 10.526 | 7.3664 | 3.3798 | -0.19662 | 2.6% | -2.6%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88586 | 0.97754 | -2.9012 | -7.7778 | 10.526 | 7.8334 | 3.6467 | -0.15255 | 1.91% | -1.91%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97254 | 0.97283 | -3.1631 | -7.7823 | 10.526 | 8.4616 | 3.9375 | -0.16442 | 1.906% | -1.906%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9314 | 10.526 | 8.9725 | 4.2602 | -0.086487 | 0.9547% | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 10.526 | 9.0934 | 4.3174 | -0.087614 | 0.9543% | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 10.5155 | 9.1419 | 4.3404 | -0.088066 | 0.9541% | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 10.4839 | 9.1726 | 4.3549 | -0.088353 | 0.954% | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 10.4523 | 9.2034 | 4.3695 | -0.088639 | 0.9539% | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 10.4523 | 9.2331 | 4.3836 | -0.088914 | 0.9538% | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 10.4734 | 9.2489 | 4.3911 | -0.089063 | 0.9538% | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 10.5049 | 9.3143 | 4.422 | -0.089671 | 0.9535% | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 10.5155 | 9.5026 | 4.5111 | -0.091419 | 0.9529% | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 10.526 | 9.7889 | 4.6466 | -0.094076 | 0.9519% | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 10.526 | 9.9049 | 4.7014 | -0.09515 | 0.9515% | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 10.526 | 9.8712 | 4.6855 | -0.094836 | 0.9516% | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 10.526 | 9.7632 | 4.6344 | -0.093839 | 0.952% | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 10.526 | 9.5283 | 4.5233 | -0.091658 | 0.9528% | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 10.526 | 9.0518 | 4.2977 | -0.087226 | 0.9544% | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96182 | 0.97341 | -3.1306 | -7.7817 | 10.526 | 8.384 | 3.9017 | -0.16296 | 1.907% | -1.907%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.8941 | 0.9771 | -2.9261 | -7.7783 | 10.526 | 7.8933 | 3.6744 | -0.15369 | 1.91% | -1.91%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 5.263 | 7.5657 | 3.5199 | -0.15034 | 1.948% | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99118 | -1.471 | 0.97327 | -2.4423 | -5.263 | 5.263 | 7.3163 | 3.3518 | -0.20068 | 2.67% | -2.67%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99169 | -1.4424 | 0.97406 | -2.3981 | -5.263 | 5.263 | 7.2092 | 3.3031 | -0.1978 | 2.67% | -2.67%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99173 | -1.44 | 0.97412 | -2.3945 | -5.263 | 5.263 | 7.2004 | 3.2991 | -0.19756 | 2.671% | -2.671%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99096 | -1.483 | 0.97294 | -2.4608 | -5.263 | 5.263 | 7.3611 | 3.3722 | -0.20188 | 2.669% | -2.669%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 5.263 | 7.8304 | 3.6423 | -0.15558 | 1.948% | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 5.2525 | 8.458 | 3.9324 | -0.16798 | 1.947% | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 5.1156 | 8.9705 | 4.2573 | -0.088473 | 0.9766% | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 4.7051 | 9.0913 | 4.3144 | -0.089658 | 0.9766% | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.142 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 4.142 | 9.1399 | 4.3374 | -0.090133 | 0.9765% | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 3.5736 | 9.1706 | 4.3519 | -0.090433 | 0.9765% | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 3.2578 | 9.2013 | 4.3664 | -0.090735 | 0.9765% | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 3.3525 | 9.231 | 4.3804 | -0.091025 | 0.9765% | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 3.5052 | 9.2468 | 4.3879 | -0.091182 | 0.9765% | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.942 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 3.942 | 9.3122 | 4.4188 | -0.091822 | 0.9764% | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 4.4578 | 9.5003 | 4.5078 | -0.093662 | 0.9763% | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 4.9209 | 9.7865 | 4.643 | -0.096466 | 0.9761% | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 5.1893 | 9.9024 | 4.6978 | -0.097599 | 0.976% | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 5.2577 | 9.8687 | 4.6819 | -0.097268 | 0.976% | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 5.263 | 9.7608 | 4.6309 | -0.096213 | 0.9761% | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 5.263 | 9.5261 | 4.52 | -0.093915 | 0.9762% | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 5.263 | 9.0498 | 4.2948 | -0.08925 | 0.9766% | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 5.263 | 8.3806 | 3.8966 | -0.16645 | 1.947% | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 5.263 | 7.8902 | 3.67 | -0.15676 | 1.948% | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 5.263 | 7.5657 | 3.5199 | -0.15034 | 1.948% | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99118 | -1.471 | 0.97327 | -2.4423 | -5.263 | 5.263 | 7.3163 | 3.3518 | -0.20068 | 2.67% | -2.67%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99169 | -1.4424 | 0.97406 | -2.3981 | -5.263 | 5.263 | 7.2092 | 3.3031 | -0.1978 | 2.67% | -2.67%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99173 | -1.44 | 0.97412 | -2.3945 | -5.263 | 5.263 | 7.2004 | 3.2991 | -0.19756 | 2.671% | -2.671%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99096 | -1.483 | 0.97294 | -2.4608 | -5.263 | 5.263 | 7.3611 | 3.3722 | -0.20188 | 2.669% | -2.669%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 5.263 | 7.8304 | 3.6423 | -0.15558 | 1.948% | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 5.263 | 8.458 | 3.9324 | -0.16798 | 1.947% | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 5.2577 | 8.9705 | 4.2573 | -0.088473 | 0.9766% | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 5.2051 | 9.0913 | 4.3144 | -0.089658 | 0.9766% | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 5.0946 | 9.1399 | 4.3374 | -0.090133 | 0.9765% | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 4.9788 | 9.1706 | 4.3519 | -0.090433 | 0.9765% | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 4.9156 | 9.2013 | 4.3664 | -0.090735 | 0.9765% | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 4.9841 | 9.231 | 4.3804 | -0.091025 | 0.9765% | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 5.0156 | 9.2468 | 4.3879 | -0.091182 | 0.9765% | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 5.1472 | 9.3122 | 4.4188 | -0.091822 | 0.9764% | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 5.2367 | 9.5003 | 4.5078 | -0.093662 | 0.9763% | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 5.263 | 9.7865 | 4.643 | -0.096466 | 0.9761% | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 5.263 | 9.9024 | 4.6978 | -0.097599 | 0.976% | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 5.263 | 9.8687 | 4.6819 | -0.097268 | 0.976% | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 5.263 | 9.7608 | 4.6309 | -0.096213 | 0.9761% | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 5.263 | 9.5261 | 4.52 | -0.093915 | 0.9762% | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 5.263 | 9.0498 | 4.2948 | -0.08925 | 0.9766% | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 5.263 | 8.3806 | 3.8966 | -0.16645 | 1.947% | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 5.263 | 7.8902 | 3.67 | -0.15676 | 1.948% | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 5.263 | 7.5657 | 3.5199 | -0.15034 | 1.948% | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99118 | -1.471 | 0.97327 | -2.4423 | -5.263 | 5.263 | 7.3163 | 3.3518 | -0.20068 | 2.67% | -2.67%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99169 | -1.4424 | 0.97406 | -2.3981 | -5.263 | 5.263 | 7.2092 | 3.3031 | -0.1978 | 2.67% | -2.67%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99173 | -1.44 | 0.97412 | -2.3945 | -5.263 | 5.263 | 7.2004 | 3.2991 | -0.19756 | 2.671% | -2.671%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99096 | -1.483 | 0.97294 | -2.4608 | -5.263 | 5.263 | 7.3611 | 3.3722 | -0.20188 | 2.669% | -2.669%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 5.263 | 7.8304 | 3.6423 | -0.15558 | 1.948% | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 5.263 | 8.458 | 3.9324 | -0.16798 | 1.947% | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 5.263 | 8.9705 | 4.2573 | -0.088473 | 0.9766% | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 5.263 | 9.0913 | 4.3144 | -0.089658 | 0.9766% | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 5.2577 | 9.1399 | 4.3374 | -0.090133 | 0.9765% | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 5.2419 | 9.1706 | 4.3519 | -0.090433 | 0.9765% | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 5.2262 | 9.2013 | 4.3664 | -0.090735 | 0.9765% | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 5.2262 | 9.231 | 4.3804 | -0.091025 | 0.9765% | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 5.2367 | 9.2468 | 4.3879 | -0.091182 | 0.9765% | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 5.2525 | 9.3122 | 4.4188 | -0.091822 | 0.9764% | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 5.2577 | 9.5003 | 4.5078 | -0.093662 | 0.9763% | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 5.263 | 9.7865 | 4.643 | -0.096466 | 0.9761% | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 5.263 | 9.9024 | 4.6978 | -0.097599 | 0.976% | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 5.263 | 9.8687 | 4.6819 | -0.097268 | 0.976% | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 5.263 | 9.7608 | 4.6309 | -0.096213 | 0.9761% | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 5.263 | 9.5261 | 4.52 | -0.093915 | 0.9762% | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 5.263 | 9.0498 | 4.2948 | -0.08925 | 0.9766% | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 5.263 | 8.3806 | 3.8966 | -0.16645 | 1.947% | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 5.263 | 7.8902 | 3.67 | -0.15676 | 1.948% | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 10.526 | 7.5657 | 3.5199 | -0.15034 | 1.948% | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.4333 | 0.97078 | -2.4094 | -5.7277 | 10.526 | 7.298 | 3.3256 | -0.21899 | 2.913% | -2.913%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4048 | 0.97158 | -2.3652 | -5.7264 | 10.526 | 7.1912 | 3.2774 | -0.2158 | 2.913% | -2.913%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.4024 | 0.97165 | -2.3616 | -5.7263 | 10.526 | 7.1825 | 3.2734 | -0.21554 | 2.913% | -2.913%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4453 | 0.97045 | -2.4279 | -5.728 | 10.526 | 7.3427 | 3.3458 | -0.22032 | 2.913% | -2.913%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 10.526 | 7.8304 | 3.6423 | -0.15558 | 1.948% | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 10.5049 | 8.458 | 3.9324 | -0.16798 | 1.947% | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 10.2313 | 8.9705 | 4.2573 | -0.088473 | 0.9766% | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 9.4102 | 9.0913 | 4.3144 | -0.089658 | 0.9766% | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.284 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 8.284 | 9.1399 | 4.3374 | -0.090133 | 0.9765% | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 7.1472 | 9.1706 | 4.3519 | -0.090433 | 0.9765% | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 6.5156 | 9.2013 | 4.3664 | -0.090735 | 0.9765% | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 6.7051 | 9.231 | 4.3804 | -0.091025 | 0.9765% | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 7.0103 | 9.2468 | 4.3879 | -0.091182 | 0.9765% | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.884 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 7.884 | 9.3122 | 4.4188 | -0.091822 | 0.9764% | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 8.9155 | 9.5003 | 4.5078 | -0.093662 | 0.9763% | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 9.8418 | 9.7865 | 4.643 | -0.096466 | 0.9761% | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 10.3786 | 9.9024 | 4.6978 | -0.097599 | 0.976% | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 10.5155 | 9.8687 | 4.6819 | -0.097268 | 0.976% | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 10.526 | 9.7608 | 4.6309 | -0.096213 | 0.9761% | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 10.526 | 9.5261 | 4.52 | -0.093915 | 0.9762% | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 10.526 | 9.0498 | 4.2948 | -0.08925 | 0.9766% | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 10.526 | 8.3806 | 3.8966 | -0.16645 | 1.947% | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 10.526 | 7.8902 | 3.67 | -0.15676 | 1.948% | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 10.526 | 7.5657 | 3.5199 | -0.15034 | 1.948% | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.4333 | 0.97078 | -2.4094 | -5.7277 | 10.526 | 7.298 | 3.3256 | -0.21899 | 2.913% | -2.913%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4048 | 0.97158 | -2.3652 | -5.7264 | 10.526 | 7.1912 | 3.2774 | -0.2158 | 2.913% | -2.913%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.4024 | 0.97165 | -2.3616 | -5.7263 | 10.526 | 7.1825 | 3.2734 | -0.21554 | 2.913% | -2.913%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4453 | 0.97045 | -2.4279 | -5.728 | 10.526 | 7.3427 | 3.3458 | -0.22032 | 2.913% | -2.913%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 10.526 | 7.8304 | 3.6423 | -0.15558 | 1.948% | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 10.526 | 8.458 | 3.9324 | -0.16798 | 1.947% | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 10.5155 | 8.9705 | 4.2573 | -0.088473 | 0.9766% | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 10.4102 | 9.0913 | 4.3144 | -0.089658 | 0.9766% | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 10.1892 | 9.1399 | 4.3374 | -0.090133 | 0.9765% | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 9.9576 | 9.1706 | 4.3519 | -0.090433 | 0.9765% | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 9.8313 | 9.2013 | 4.3664 | -0.090735 | 0.9765% | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 9.9681 | 9.231 | 4.3804 | -0.091025 | 0.9765% | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 10.0313 | 9.2468 | 4.3879 | -0.091182 | 0.9765% | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 10.2944 | 9.3122 | 4.4188 | -0.091822 | 0.9764% | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 10.4734 | 9.5003 | 4.5078 | -0.093662 | 0.9763% | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 10.526 | 9.7865 | 4.643 | -0.096466 | 0.9761% | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 10.526 | 9.9024 | 4.6978 | -0.097599 | 0.976% | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 10.526 | 9.8687 | 4.6819 | -0.097268 | 0.976% | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 10.526 | 9.7608 | 4.6309 | -0.096213 | 0.9761% | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 10.526 | 9.5261 | 4.52 | -0.093915 | 0.9762% | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 10.526 | 9.0498 | 4.2948 | -0.08925 | 0.9766% | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 10.526 | 8.3806 | 3.8966 | -0.16645 | 1.947% | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 10.526 | 7.8902 | 3.67 | -0.15676 | 1.948% | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 10.526 | 7.5657 | 3.5199 | -0.15034 | 1.948% | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.4333 | 0.97078 | -2.4094 | -5.7277 | 10.526 | 7.298 | 3.3256 | -0.21899 | 2.913% | -2.913%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4048 | 0.97158 | -2.3652 | -5.7264 | 10.526 | 7.1912 | 3.2774 | -0.2158 | 2.913% | -2.913%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.4024 | 0.97165 | -2.3616 | -5.7263 | 10.526 | 7.1825 | 3.2734 | -0.21554 | 2.913% | -2.913%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4453 | 0.97045 | -2.4279 | -5.728 | 10.526 | 7.3427 | 3.3458 | -0.22032 | 2.913% | -2.913%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 10.526 | 7.8304 | 3.6423 | -0.15558 | 1.948% | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 10.526 | 8.458 | 3.9324 | -0.16798 | 1.947% | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 10.526 | 8.9705 | 4.2573 | -0.088473 | 0.9766% | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 10.526 | 9.0913 | 4.3144 | -0.089658 | 0.9766% | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 10.5155 | 9.1399 | 4.3374 | -0.090133 | 0.9765% | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 10.4839 | 9.1706 | 4.3519 | -0.090433 | 0.9765% | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 10.4523 | 9.2013 | 4.3664 | -0.090735 | 0.9765% | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 10.4523 | 9.231 | 4.3804 | -0.091025 | 0.9765% | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 10.4734 | 9.2468 | 4.3879 | -0.091182 | 0.9765% | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 10.5049 | 9.3122 | 4.4188 | -0.091822 | 0.9764% | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 10.5155 | 9.5003 | 4.5078 | -0.093662 | 0.9763% | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 10.526 | 9.7865 | 4.643 | -0.096466 | 0.9761% | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 10.526 | 9.9024 | 4.6978 | -0.097599 | 0.976% | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 10.526 | 9.8687 | 4.6819 | -0.097268 | 0.976% | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 10.526 | 9.7608 | 4.6309 | -0.096213 | 0.9761% | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 10.526 | 9.5261 | 4.52 | -0.093915 | 0.9762% | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 10.526 | 9.0498 | 4.2948 | -0.08925 | 0.9766% | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 10.526 | 8.3806 | 3.8966 | -0.16645 | 1.947% | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 10.526 | 7.8902 | 3.67 | -0.15676 | 1.948% | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 5.263 | 7.4963 | 3.4201 | -0.21975 | 2.848% | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 5.263 | 7.2922 | 3.3173 | -0.22478 | 2.99% | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 5.263 | 7.1797 | 3.2609 | -0.22728 | 3.068% | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 5.263 | 7.1705 | 3.2563 | -0.22748 | 3.075% | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 5.263 | 7.3393 | 3.341 | -0.22367 | 2.957% | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 5.263 | 7.7741 | 3.5611 | -0.21192 | 2.654% | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 5.2525 | 8.4374 | 3.9024 | -0.18856 | 2.186% | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 5.1156 | 8.8902 | 4.1394 | -0.16883 | 1.864% | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 4.7051 | 9.0183 | 4.2071 | -0.16269 | 1.772% | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.142 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 4.142 | 9.0698 | 4.2344 | -0.16015 | 1.735% | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 3.5736 | 9.1025 | 4.2517 | -0.15852 | 1.712% | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 3.2578 | 9.1351 | 4.2691 | -0.15688 | 1.688% | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 3.3525 | 9.1667 | 4.2859 | -0.15527 | 1.666% | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 3.5052 | 9.1836 | 4.2948 | -0.15441 | 1.654% | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.942 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 3.942 | 9.2532 | 4.3319 | -0.1508 | 1.604% | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 4.4578 | 9.454 | 4.4393 | -0.13997 | 1.459% | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 4.9209 | 9.7607 | 4.6047 | -0.12227 | 1.237% | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 5.1893 | 9.8853 | 4.6724 | -0.11468 | 1.147% | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 5.2577 | 9.8491 | 4.6527 | -0.11691 | 1.173% | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 5.263 | 9.7331 | 4.5898 | -0.12392 | 1.257% | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 5.263 | 9.4816 | 4.4541 | -0.13844 | 1.439% | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 5.263 | 8.9742 | 4.1838 | -0.16483 | 1.804% | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 5.263 | 8.3552 | 3.8597 | -0.19181 | 2.244% | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 5.263 | 7.837 | 3.5931 | -0.20999 | 2.609% | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 5.263 | 7.4962 | 3.4201 | -0.21975 | 2.848% | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 5.263 | 7.2922 | 3.3173 | -0.22478 | 2.99% | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 5.263 | 7.1797 | 3.2609 | -0.22728 | 3.068% | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 5.263 | 7.1705 | 3.2563 | -0.22748 | 3.075% | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 5.263 | 7.3393 | 3.341 | -0.22367 | 2.957% | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 5.263 | 7.7741 | 3.5611 | -0.21192 | 2.654% | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 5.263 | 8.4374 | 3.9024 | -0.18856 | 2.186% | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 5.2577 | 8.8902 | 4.1394 | -0.16883 | 1.864% | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 5.2051 | 9.0183 | 4.2071 | -0.16269 | 1.772% | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 5.0946 | 9.0698 | 4.2344 | -0.16015 | 1.735% | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 4.9788 | 9.1025 | 4.2517 | -0.15852 | 1.712% | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 4.9156 | 9.1351 | 4.2691 | -0.15688 | 1.688% | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 4.9841 | 9.1667 | 4.2859 | -0.15527 | 1.666% | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 5.0156 | 9.1836 | 4.2948 | -0.15441 | 1.654% | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 5.1472 | 9.2532 | 4.3319 | -0.1508 | 1.604% | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 5.2367 | 9.454 | 4.4393 | -0.13997 | 1.459% | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 5.263 | 9.7607 | 4.6047 | -0.12227 | 1.237% | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 5.263 | 9.8853 | 4.6724 | -0.11468 | 1.147% | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 5.263 | 9.8491 | 4.6527 | -0.11691 | 1.173% | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 5.263 | 9.7331 | 4.5898 | -0.12392 | 1.257% | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 5.263 | 9.4816 | 4.4541 | -0.13844 | 1.439% | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 5.263 | 8.9742 | 4.1838 | -0.16483 | 1.804% | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 5.263 | 8.3552 | 3.8597 | -0.19181 | 2.244% | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 5.263 | 7.837 | 3.5931 | -0.20999 | 2.609% | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 5.263 | 7.4962 | 3.4201 | -0.21975 | 2.848% | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 5.263 | 7.2922 | 3.3173 | -0.22478 | 2.99% | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 5.263 | 7.1797 | 3.2609 | -0.22728 | 3.068% | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 5.263 | 7.1705 | 3.2563 | -0.22748 | 3.075% | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 5.263 | 7.3393 | 3.341 | -0.22367 | 2.957% | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 5.263 | 7.7741 | 3.5611 | -0.21192 | 2.654% | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 5.263 | 8.4374 | 3.9024 | -0.18856 | 2.186% | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 5.263 | 8.8902 | 4.1394 | -0.16883 | 1.864% | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 5.263 | 9.0183 | 4.2071 | -0.16269 | 1.772% | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 5.2577 | 9.0698 | 4.2344 | -0.16015 | 1.735% | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 5.2419 | 9.1025 | 4.2517 | -0.15852 | 1.712% | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 5.2262 | 9.1351 | 4.2691 | -0.15688 | 1.688% | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 5.2262 | 9.1667 | 4.2859 | -0.15527 | 1.666% | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 5.2367 | 9.1836 | 4.2948 | -0.15441 | 1.654% | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 5.2525 | 9.2532 | 4.3319 | -0.1508 | 1.604% | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 5.2577 | 9.454 | 4.4393 | -0.13997 | 1.459% | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 5.263 | 9.7607 | 4.6047 | -0.12227 | 1.237% | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 5.263 | 9.8853 | 4.6724 | -0.11468 | 1.147% | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 5.263 | 9.8491 | 4.6527 | -0.11691 | 1.173% | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 5.263 | 9.7331 | 4.5898 | -0.12392 | 1.257% | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 5.263 | 9.4816 | 4.4541 | -0.13844 | 1.439% | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 5.263 | 8.9742 | 4.1838 | -0.16483 | 1.804% | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 5.263 | 8.3552 | 3.8597 | -0.19181 | 2.244% | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 5.263 | 7.837 | 3.5931 | -0.20999 | 2.609% | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 10.526 | 7.4962 | 3.4201 | -0.21975 | 2.848% | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 10.526 | 7.2922 | 3.3173 | -0.22478 | 2.99% | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 10.526 | 7.1797 | 3.2609 | -0.22728 | 3.068% | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 10.526 | 7.1705 | 3.2563 | -0.22748 | 3.075% | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 10.526 | 7.3393 | 3.341 | -0.22367 | 2.957% | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 10.526 | 7.7741 | 3.5611 | -0.21192 | 2.654% | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 10.5049 | 8.4374 | 3.9024 | -0.18856 | 2.186% | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 10.2313 | 8.8902 | 4.1394 | -0.16883 | 1.864% | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 9.4102 | 9.0183 | 4.2071 | -0.16269 | 1.772% | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.284 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 8.284 | 9.0698 | 4.2344 | -0.16015 | 1.735% | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 7.1472 | 9.1025 | 4.2517 | -0.15852 | 1.712% | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 6.5156 | 9.1351 | 4.2691 | -0.15688 | 1.688% | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 6.7051 | 9.1667 | 4.2859 | -0.15527 | 1.666% | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 7.0103 | 9.1836 | 4.2948 | -0.15441 | 1.654% | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.884 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 7.884 | 9.2532 | 4.3319 | -0.1508 | 1.604% | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 8.9155 | 9.454 | 4.4393 | -0.13997 | 1.459% | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 9.8418 | 9.7607 | 4.6047 | -0.12227 | 1.237% | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 10.3786 | 9.8853 | 4.6724 | -0.11468 | 1.147% | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 10.5155 | 9.8491 | 4.6527 | -0.11691 | 1.173% | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 10.526 | 9.7331 | 4.5898 | -0.12392 | 1.257% | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 10.526 | 9.4816 | 4.4541 | -0.13844 | 1.439% | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 10.526 | 8.9742 | 4.1838 | -0.16483 | 1.804% | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 10.526 | 8.3552 | 3.8597 | -0.19181 | 2.244% | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 10.526 | 7.837 | 3.5931 | -0.20999 | 2.609% | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 10.526 | 7.4962 | 3.4201 | -0.21975 | 2.848% | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 10.526 | 7.2922 | 3.3173 | -0.22478 | 2.99% | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 10.526 | 7.1797 | 3.2609 | -0.22728 | 3.068% | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 10.526 | 7.1705 | 3.2563 | -0.22748 | 3.075% | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 10.526 | 7.3393 | 3.341 | -0.22367 | 2.957% | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 10.526 | 7.7741 | 3.5611 | -0.21192 | 2.654% | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 10.526 | 8.4374 | 3.9024 | -0.18856 | 2.186% | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 10.5155 | 8.8902 | 4.1394 | -0.16883 | 1.864% | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 10.4102 | 9.0183 | 4.2071 | -0.16269 | 1.772% | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 10.1892 | 9.0698 | 4.2344 | -0.16015 | 1.735% | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 9.9576 | 9.1025 | 4.2517 | -0.15852 | 1.712% | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 9.8313 | 9.1351 | 4.2691 | -0.15688 | 1.688% | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 9.9681 | 9.1667 | 4.2859 | -0.15527 | 1.666% | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 10.0313 | 9.1836 | 4.2948 | -0.15441 | 1.654% | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 10.2944 | 9.2532 | 4.3319 | -0.1508 | 1.604% | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 10.4734 | 9.454 | 4.4393 | -0.13997 | 1.459% | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 10.526 | 9.7607 | 4.6047 | -0.12227 | 1.237% | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 10.526 | 9.8853 | 4.6724 | -0.11468 | 1.147% | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 10.526 | 9.8491 | 4.6527 | -0.11691 | 1.173% | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 10.526 | 9.7331 | 4.5898 | -0.12392 | 1.257% | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 10.526 | 9.4816 | 4.4541 | -0.13844 | 1.439% | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 10.526 | 8.9742 | 4.1838 | -0.16483 | 1.804% | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 10.526 | 8.3552 | 3.8597 | -0.19181 | 2.244% | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 10.526 | 7.837 | 3.5931 | -0.20999 | 2.609% | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 10.526 | 7.4962 | 3.4201 | -0.21975 | 2.848% | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 10.526 | 7.2922 | 3.3173 | -0.22478 | 2.99% | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 10.526 | 7.1797 | 3.2609 | -0.22728 | 3.068% | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 10.526 | 7.1705 | 3.2563 | -0.22748 | 3.075% | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 10.526 | 7.3393 | 3.341 | -0.22367 | 2.957% | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 10.526 | 7.7741 | 3.5611 | -0.21192 | 2.654% | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 10.526 | 8.4374 | 3.9024 | -0.18856 | 2.186% | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 10.526 | 8.8902 | 4.1394 | -0.16883 | 1.864% | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 10.526 | 9.0183 | 4.2071 | -0.16269 | 1.772% | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 10.5155 | 9.0698 | 4.2344 | -0.16015 | 1.735% | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 10.4839 | 9.1025 | 4.2517 | -0.15852 | 1.712% | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 10.4523 | 9.1351 | 4.2691 | -0.15688 | 1.688% | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 10.4523 | 9.1667 | 4.2859 | -0.15527 | 1.666% | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 10.4734 | 9.1836 | 4.2948 | -0.15441 | 1.654% | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 10.5049 | 9.2532 | 4.3319 | -0.1508 | 1.604% | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 10.5155 | 9.454 | 4.4393 | -0.13997 | 1.459% | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 10.526 | 9.7607 | 4.6047 | -0.12227 | 1.237% | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 10.526 | 9.8853 | 4.6724 | -0.11468 | 1.147% | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 10.526 | 9.8491 | 4.6527 | -0.11691 | 1.173% | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 10.526 | 9.7331 | 4.5898 | -0.12392 | 1.257% | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 10.526 | 9.4816 | 4.4541 | -0.13844 | 1.439% | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 10.526 | 8.9742 | 4.1838 | -0.16483 | 1.804% | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 10.526 | 8.3552 | 3.8597 | -0.19181 | 2.244% | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 10.526 | 7.837 | 3.5931 | -0.20999 | 2.609% | -2.609%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0267 | -0.93035 | 0.99578 | -2.9668 | -5.263 | 5.263 | 7.616 | 2.4396 | -0.10004 | 1.297% | -1.297%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.90316 | 0.99694 | -2.8842 | -5.263 | 5.263 | 7.4195 | 2.3768 | -0.097491 | 1.297% | -1.297%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.88815 | 0.99759 | -2.8386 | -5.263 | 5.263 | 7.3109 | 2.3421 | -0.096093 | 1.297% | -1.297%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.88692 | 0.99764 | -2.8349 | -5.263 | 5.263 | 7.302 | 2.3392 | -0.095977 | 1.297% | -1.297%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.027 | -0.90944 | 0.99667 | -2.9033 | -5.263 | 5.263 | 7.4649 | 2.3913 | -0.098076 | 1.297% | -1.297%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.96731 | 0.99418 | -3.0793 | -5.263 | 5.263 | 7.8826 | 2.5248 | -0.10345 | 1.295% | -1.295%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.0545 | 0.99048 | -3.3433 | -5.2525 | 5.2525 | 8.5154 | 2.7275 | -0.11059 | 1.282% | -1.282%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.025 | -1.1174 | 0.98821 | -3.528 | -5.1156 | 5.1156 | 8.9461 | 2.8671 | -0.11289 | 1.246% | -1.246%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0259 | -1.144 | 0.9885 | -3.5861 | -4.7051 | 4.7051 | 9.076 | 2.9148 | -0.10498 | 1.143% | -1.143%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.142 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0272 | -1.1642 | 0.9896 | -3.6163 | -4.142 | 4.142 | 9.1373 | 2.9429 | -0.092715 | 1.004% | -1.004%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0285 | -1.1849 | 0.99066 | -3.6504 | -3.5736 | 3.5736 | 9.1795 | 2.964 | -0.081503 | 0.8801% | -0.8801%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0293 | -1.1963 | 0.99127 | -3.6673 | -3.2578 | 3.2578 | 9.2176 | 2.9811 | -0.074406 | 0.8007% | -0.8007%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0291 | -1.1954 | 0.99102 | -3.6668 | -3.3525 | 3.3525 | 9.2468 | 2.9902 | -0.075229 | 0.807% | -0.807%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0287 | -1.194 | 0.99054 | -3.6712 | -3.5052 | 3.5052 | 9.2591 | 2.9918 | -0.078886 | 0.8448% | -0.8448%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.942 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0274 | -1.1928 | 0.98905 | -3.6923 | -3.942 | 3.942 | 9.3144 | 3.0029 | -0.089597 | 0.9528% | -0.9528%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0258 | -1.2069 | 0.9866 | -3.7651 | -4.4578 | 4.4578 | 9.4903 | 3.0514 | -0.10365 | 1.08% | -1.08%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0241 | -1.2368 | 0.98359 | -3.8853 | -4.9209 | 4.9209 | 9.7643 | 3.1312 | -0.11873 | 1.201% | -1.201%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.247 | 0.98217 | -3.9325 | -5.1893 | 5.1893 | 9.8731 | 3.1615 | -0.12695 | 1.269% | -1.269%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.023 | -1.2407 | 0.98221 | -3.9172 | -5.2577 | 5.2577 | 9.8377 | 3.149 | -0.12827 | 1.287% | -1.287%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0232 | -1.2254 | 0.98287 | -3.8704 | -5.263 | 5.263 | 9.73 | 3.1146 | -0.12704 | 1.289% | -1.289%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1925 | 0.98433 | -3.769 | -5.263 | 5.263 | 9.4959 | 3.0399 | -0.12406 | 1.29% | -1.29%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.1259 | 0.98727 | -3.5644 | -5.263 | 5.263 | 9.021 | 2.8883 | -0.11802 | 1.291% | -1.291%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0443 | 0.99084 | -3.3143 | -5.263 | 5.263 | 8.4365 | 2.7017 | -0.11055 | 1.293% | -1.293%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.97567 | 0.99382 | -3.1048 | -5.263 | 5.263 | 7.9428 | 2.544 | -0.10422 | 1.295% | -1.295%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0267 | -0.93035 | 0.99577 | -2.9668 | -5.263 | 5.263 | 7.616 | 2.4396 | -0.10002 | 1.296% | -1.296%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.90316 | 0.99694 | -2.8842 | -5.263 | 5.263 | 7.4195 | 2.3768 | -0.097491 | 1.297% | -1.297%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.88815 | 0.99759 | -2.8386 | -5.263 | 5.263 | 7.3109 | 2.3421 | -0.096093 | 1.297% | -1.297%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.88692 | 0.99764 | -2.8349 | -5.263 | 5.263 | 7.302 | 2.3392 | -0.095977 | 1.297% | -1.297%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.027 | -0.90944 | 0.99667 | -2.9033 | -5.263 | 5.263 | 7.4649 | 2.3913 | -0.098076 | 1.297% | -1.297%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.96731 | 0.99418 | -3.0793 | -5.263 | 5.263 | 7.8826 | 2.5248 | -0.10345 | 1.295% | -1.295%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.0552 | 0.99036 | -3.3476 | -5.263 | 5.263 | 8.5145 | 2.7266 | -0.11154 | 1.293% | -1.293%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0246 | -1.115 | 0.98777 | -3.5305 | -5.2577 | 5.2577 | 8.9421 | 2.8632 | -0.11689 | 1.29% | -1.29%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0245 | -1.1331 | 0.98716 | -3.5829 | -5.2051 | 5.2051 | 9.0638 | 2.9029 | -0.11719 | 1.276% | -1.276%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0248 | -1.1415 | 0.98722 | -3.6007 | -5.0946 | 5.0946 | 9.1155 | 2.9216 | -0.11448 | 1.24% | -1.24%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.025 | -1.1485 | 0.98733 | -3.6157 | -4.9788 | 4.9788 | 9.1488 | 2.934 | -0.11218 | 1.211% | -1.211%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0251 | -1.1543 | 0.9873 | -3.6298 | -4.9156 | 4.9156 | 9.1809 | 2.9452 | -0.11108 | 1.195% | -1.195%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0249 | -1.1568 | 0.98694 | -3.6415 | -4.9841 | 4.9841 | 9.209 | 2.9531 | -0.11302 | 1.212% | -1.212%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0248 | -1.1583 | 0.98676 | -3.6478 | -5.0156 | 5.0156 | 9.2241 | 2.9575 | -0.11394 | 1.22% | -1.22%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0243 | -1.1643 | 0.98603 | -3.6737 | -5.1472 | 5.1472 | 9.2862 | 2.9753 | -0.11781 | 1.253% | -1.253%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0238 | -1.1884 | 0.98464 | -3.7532 | -5.2367 | 5.2367 | 9.4717 | 3.0332 | -0.12226 | 1.274% | -1.274%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0232 | -1.229 | 0.98271 | -3.8815 | -5.263 | 5.263 | 9.7556 | 3.1227 | -0.12736 | 1.289% | -1.289%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.023 | -1.2453 | 0.98198 | -3.9317 | -5.263 | 5.263 | 9.8712 | 3.1596 | -0.12883 | 1.288% | -1.288%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.023 | -1.2406 | 0.98219 | -3.9171 | -5.263 | 5.263 | 9.8376 | 3.1489 | -0.1284 | 1.288% | -1.288%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0232 | -1.2254 | 0.98287 | -3.8704 | -5.263 | 5.263 | 9.73 | 3.1146 | -0.12704 | 1.289% | -1.289%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1925 | 0.98433 | -3.769 | -5.263 | 5.263 | 9.4959 | 3.0399 | -0.12406 | 1.29% | -1.29%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.1259 | 0.98727 | -3.5644 | -5.263 | 5.263 | 9.021 | 2.8883 | -0.11802 | 1.291% | -1.291%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0443 | 0.99084 | -3.3143 | -5.263 | 5.263 | 8.4365 | 2.7017 | -0.11055 | 1.293% | -1.293%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.97567 | 0.99382 | -3.1048 | -5.263 | 5.263 | 7.9428 | 2.544 | -0.10422 | 1.295% | -1.295%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0267 | -0.93035 | 0.99577 | -2.9668 | -5.263 | 5.263 | 7.616 | 2.4396 | -0.10002 | 1.296% | -1.296%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.90316 | 0.99694 | -2.8842 | -5.263 | 5.263 | 7.4195 | 2.3768 | -0.097491 | 1.297% | -1.297%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.88815 | 0.99759 | -2.8386 | -5.263 | 5.263 | 7.3109 | 2.3421 | -0.096093 | 1.297% | -1.297%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.88692 | 0.99764 | -2.8349 | -5.263 | 5.263 | 7.302 | 2.3392 | -0.095977 | 1.297% | -1.297%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.027 | -0.90944 | 0.99667 | -2.9033 | -5.263 | 5.263 | 7.4649 | 2.3913 | -0.098076 | 1.297% | -1.297%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.96731 | 0.99418 | -3.0793 | -5.263 | 5.263 | 7.8826 | 2.5248 | -0.10345 | 1.295% | -1.295%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.0552 | 0.99036 | -3.3476 | -5.263 | 5.263 | 8.5145 | 2.7266 | -0.11154 | 1.293% | -1.293%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0245 | -1.1149 | 0.98775 | -3.5304 | -5.263 | 5.263 | 8.942 | 2.8631 | -0.11701 | 1.292% | -1.292%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0243 | -1.1317 | 0.98701 | -3.5822 | -5.263 | 5.263 | 9.0625 | 2.9016 | -0.11854 | 1.291% | -1.291%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0243 | -1.1386 | 0.98673 | -3.603 | -5.2577 | 5.2577 | 9.111 | 2.9171 | -0.11904 | 1.29% | -1.29%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0243 | -1.1433 | 0.98658 | -3.6164 | -5.2419 | 5.2419 | 9.1419 | 2.9273 | -0.11905 | 1.286% | -1.286%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0243 | -1.1479 | 0.98643 | -3.6297 | -5.2262 | 5.2262 | 9.1729 | 2.9374 | -0.11907 | 1.281% | -1.281%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0242 | -1.1521 | 0.98625 | -3.6425 | -5.2262 | 5.2262 | 9.2026 | 2.9468 | -0.11944 | 1.281% | -1.281%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0242 | -1.153 | 0.98621 | -3.6443 | -5.2367 | 5.2367 | 9.2189 | 2.9524 | -0.11909 | 1.275% | -1.275%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0241 | -1.1618 | 0.98577 | -3.6721 | -5.2525 | 5.2525 | 9.2837 | 2.9729 | -0.12028 | 1.279% | -1.279%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0237 | -1.189 | 0.9845 | -3.758 | -5.2577 | 5.2577 | 9.4704 | 3.0318 | -0.12361 | 1.288% | -1.288%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0232 | -1.229 | 0.98271 | -3.8815 | -5.263 | 5.263 | 9.7556 | 3.1227 | -0.12736 | 1.289% | -1.289%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.023 | -1.2453 | 0.98198 | -3.9317 | -5.263 | 5.263 | 9.8712 | 3.1596 | -0.12883 | 1.288% | -1.288%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.023 | -1.2406 | 0.98219 | -3.9171 | -5.263 | 5.263 | 9.8376 | 3.1489 | -0.1284 | 1.288% | -1.288%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0232 | -1.2254 | 0.98287 | -3.8704 | -5.263 | 5.263 | 9.73 | 3.1146 | -0.12704 | 1.289% | -1.289%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1925 | 0.98433 | -3.769 | -5.263 | 5.263 | 9.4959 | 3.0399 | -0.12406 | 1.29% | -1.29%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.1259 | 0.98727 | -3.5644 | -5.263 | 5.263 | 9.021 | 2.8883 | -0.11802 | 1.291% | -1.291%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0443 | 0.99084 | -3.3143 | -5.263 | 5.263 | 8.4365 | 2.7017 | -0.11055 | 1.293% | -1.293%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.97567 | 0.99382 | -3.1048 | -5.263 | 5.263 | 7.9428 | 2.544 | -0.10422 | 1.295% | -1.295%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0128 | -0.80449 | 0.9822 | -2.8808 | -10.526 | 10.526 | 7.5129 | 2.3405 | -0.20311 | 2.632% | -2.632%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.77724 | 0.98335 | -2.797 | -10.526 | 10.526 | 7.319 | 2.2804 | -0.19796 | 2.634% | -2.634%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.7622 | 0.98399 | -2.7507 | -10.526 | 10.526 | 7.2119 | 2.2472 | -0.19511 | 2.634% | -2.634%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.76097 | 0.98404 | -2.747 | -10.526 | 10.526 | 7.2031 | 2.2445 | -0.19488 | 2.634% | -2.634%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0131 | -0.78354 | 0.98309 | -2.8164 | -10.526 | 10.526 | 7.3638 | 2.2943 | -0.19915 | 2.633% | -2.633%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.84153 | 0.98062 | -2.9949 | -10.526 | 10.526 | 7.7759 | 2.422 | -0.2101 | 2.631% | -2.631%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.9301 | 0.97689 | -3.2674 | -10.5049 | 10.5049 | 8.3998 | 2.6155 | -0.22616 | 2.622% | -2.622%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0114 | -0.99632 | 0.97501 | -3.4563 | -10.2313 | 10.2313 | 8.8281 | 2.7522 | -0.23089 | 2.549% | -2.549%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0134 | -1.0324 | 0.97644 | -3.5184 | -9.4102 | 9.4102 | 8.9666 | 2.808 | -0.21444 | 2.336% | -2.336%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.284 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0164 | -1.0655 | 0.9791 | -3.5527 | -8.284 | 8.284 | 9.0414 | 2.8492 | -0.18863 | 2.044% | -2.044%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0192 | -1.0996 | 0.98167 | -3.5939 | -7.1472 | 7.1472 | 9.097 | 2.8833 | -0.16403 | 1.771% | -1.771%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0209 | -1.1184 | 0.98311 | -3.6146 | -6.5156 | 6.5156 | 9.1424 | 2.9075 | -0.14963 | 1.61% | -1.61%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0204 | -1.1158 | 0.9826 | -3.6147 | -6.7051 | 6.7051 | 9.1689 | 2.9139 | -0.15312 | 1.643% | -1.643%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0196 | -1.1107 | 0.98173 | -3.6168 | -7.0103 | 7.0103 | 9.1775 | 2.9119 | -0.16053 | 1.719% | -1.719%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.884 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1055 | 0.97923 | -3.648 | -7.7578 | 7.884 | 9.2229 | 2.9134 | -0.18112 | 1.926% | -1.926%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1319 | 0.97807 | -3.7297 | -7.7583 | 8.9155 | 9.4093 | 2.9719 | -0.18472 | 1.925% | -1.925%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1721 | 0.97629 | -3.8545 | -7.759 | 9.8418 | 9.6928 | 3.061 | -0.19019 | 1.924% | -1.924%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1884 | 0.97557 | -3.9051 | -7.7593 | 10.3786 | 9.8076 | 3.097 | -0.1924 | 1.924% | -1.924%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1836 | 0.97578 | -3.8904 | -7.7592 | 10.5155 | 9.7742 | 3.0865 | -0.19176 | 1.924% | -1.924%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1684 | 0.97645 | -3.8432 | -7.7589 | 10.526 | 9.6673 | 3.053 | -0.18969 | 1.924% | -1.924%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1355 | 0.97791 | -3.7409 | -7.7583 | 10.526 | 9.4348 | 2.9799 | -0.18521 | 1.925% | -1.925%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -1.0005 | 0.97376 | -3.4871 | -10.526 | 10.526 | 8.8992 | 2.7696 | -0.23985 | 2.624% | -2.624%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0115 | -0.91871 | 0.9773 | -3.2334 | -10.526 | 10.526 | 8.3224 | 2.5912 | -0.2246 | 2.628% | -2.628%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.8499 | 0.98026 | -3.0208 | -10.526 | 10.526 | 7.8353 | 2.4404 | -0.21168 | 2.631% | -2.631%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0128 | -0.80449 | 0.9822 | -2.8808 | -10.526 | 10.526 | 7.5129 | 2.3405 | -0.20312 | 2.632% | -2.632%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.77724 | 0.98335 | -2.797 | -10.526 | 10.526 | 7.319 | 2.2804 | -0.19796 | 2.634% | -2.634%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.7622 | 0.98399 | -2.7507 | -10.526 | 10.526 | 7.2119 | 2.2472 | -0.19511 | 2.634% | -2.634%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.76097 | 0.98404 | -2.747 | -10.526 | 10.526 | 7.2031 | 2.2445 | -0.19488 | 2.634% | -2.634%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0131 | -0.78354 | 0.98309 | -2.8164 | -10.526 | 10.526 | 7.3638 | 2.2943 | -0.19915 | 2.633% | -2.633%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.84153 | 0.98062 | -2.9949 | -10.526 | 10.526 | 7.7759 | 2.422 | -0.2101 | 2.631% | -2.631%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.9296 | 0.97683 | -3.2672 | -10.526 | 10.526 | 8.3994 | 2.615 | -0.22663 | 2.627% | -2.627%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0107 | -0.98967 | 0.97427 | -3.4529 | -10.5155 | 10.5155 | 8.8215 | 2.7457 | -0.23754 | 2.622% | -2.622%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0108 | -1.009 | 0.97381 | -3.5066 | -10.4102 | 10.4102 | 8.9428 | 2.7849 | -0.23818 | 2.594% | -2.594%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0113 | -1.021 | 0.97409 | -3.5303 | -10.1892 | 10.1892 | 8.9958 | 2.8048 | -0.23415 | 2.537% | -2.537%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0118 | -1.0307 | 0.97451 | -3.5464 | -9.9576 | 9.9576 | 9.0316 | 2.8196 | -0.22938 | 2.477% | -2.477%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0176 | -1.0899 | 0.97991 | -3.6 | -7.7574 | 9.8313 | 9.113 | 2.8788 | -0.17899 | 1.926% | -1.926%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0175 | -1.0941 | 0.97973 | -3.6128 | -7.7575 | 9.9681 | 9.1424 | 2.8881 | -0.17956 | 1.926% | -1.926%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0963 | 0.97963 | -3.6197 | -7.7576 | 10.0313 | 9.1581 | 2.893 | -0.17987 | 1.926% | -1.926%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1055 | 0.97923 | -3.648 | -7.7578 | 10.2944 | 9.2229 | 2.9134 | -0.18112 | 1.926% | -1.926%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1319 | 0.97807 | -3.7297 | -7.7583 | 10.4734 | 9.4093 | 2.9719 | -0.18472 | 1.925% | -1.925%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1721 | 0.97629 | -3.8545 | -7.759 | 10.526 | 9.6928 | 3.061 | -0.19019 | 1.924% | -1.924%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1884 | 0.97557 | -3.9051 | -7.7593 | 10.526 | 9.8076 | 3.097 | -0.1924 | 1.924% | -1.924%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1836 | 0.97578 | -3.8904 | -7.7592 | 10.526 | 9.7742 | 3.0865 | -0.19176 | 1.924% | -1.924%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1684 | 0.97645 | -3.8432 | -7.7589 | 10.526 | 9.6673 | 3.053 | -0.18969 | 1.924% | -1.924%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1355 | 0.97791 | -3.7409 | -7.7583 | 10.526 | 9.4348 | 2.9799 | -0.18521 | 1.925% | -1.925%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -1.0005 | 0.97376 | -3.4871 | -10.526 | 10.526 | 8.8992 | 2.7696 | -0.23985 | 2.624% | -2.624%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0115 | -0.91871 | 0.9773 | -3.2334 | -10.526 | 10.526 | 8.3224 | 2.5912 | -0.2246 | 2.628% | -2.628%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.8499 | 0.98026 | -3.0208 | -10.526 | 10.526 | 7.8353 | 2.4404 | -0.21168 | 2.631% | -2.631%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0128 | -0.80449 | 0.9822 | -2.8808 | -10.526 | 10.526 | 7.5129 | 2.3405 | -0.20312 | 2.632% | -2.632%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.77724 | 0.98335 | -2.797 | -10.526 | 10.526 | 7.319 | 2.2804 | -0.19796 | 2.634% | -2.634%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.7622 | 0.98399 | -2.7507 | -10.526 | 10.526 | 7.2119 | 2.2472 | -0.19511 | 2.634% | -2.634%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.76097 | 0.98404 | -2.747 | -10.526 | 10.526 | 7.2031 | 2.2445 | -0.19488 | 2.634% | -2.634%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0131 | -0.78354 | 0.98309 | -2.8164 | -10.526 | 10.526 | 7.3638 | 2.2943 | -0.19915 | 2.633% | -2.633%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.84153 | 0.98062 | -2.9949 | -10.526 | 10.526 | 7.7759 | 2.422 | -0.2101 | 2.631% | -2.631%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.9296 | 0.97683 | -3.2672 | -10.526 | 10.526 | 8.3994 | 2.615 | -0.22663 | 2.627% | -2.627%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0106 | -0.98943 | 0.97424 | -3.4527 | -10.526 | 10.526 | 8.8212 | 2.7455 | -0.23779 | 2.625% | -2.625%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0104 | -1.0063 | 0.9735 | -3.5052 | -10.526 | 10.526 | 8.9401 | 2.7822 | -0.24093 | 2.624% | -2.624%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0104 | -1.0134 | 0.97324 | -3.5265 | -10.5155 | 10.5155 | 8.9881 | 2.7972 | -0.24194 | 2.621% | -2.621%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0104 | -1.0184 | 0.97313 | -3.5402 | -10.4839 | 10.4839 | 9.019 | 2.8073 | -0.24198 | 2.613% | -2.613%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0176 | -1.0899 | 0.97991 | -3.6 | -7.7574 | 10.4523 | 9.113 | 2.8788 | -0.17899 | 1.926% | -1.926%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0175 | -1.0941 | 0.97973 | -3.6128 | -7.7575 | 10.4523 | 9.1424 | 2.8881 | -0.17956 | 1.926% | -1.926%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0963 | 0.97963 | -3.6197 | -7.7576 | 10.4734 | 9.1581 | 2.893 | -0.17987 | 1.926% | -1.926%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1055 | 0.97923 | -3.648 | -7.7578 | 10.5049 | 9.2229 | 2.9134 | -0.18112 | 1.926% | -1.926%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1319 | 0.97807 | -3.7297 | -7.7583 | 10.5155 | 9.4093 | 2.9719 | -0.18472 | 1.925% | -1.925%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1721 | 0.97629 | -3.8545 | -7.759 | 10.526 | 9.6928 | 3.061 | -0.19019 | 1.924% | -1.924%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1884 | 0.97557 | -3.9051 | -7.7593 | 10.526 | 9.8076 | 3.097 | -0.1924 | 1.924% | -1.924%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1836 | 0.97578 | -3.8904 | -7.7592 | 10.526 | 9.7742 | 3.0865 | -0.19176 | 1.924% | -1.924%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1684 | 0.97645 | -3.8432 | -7.7589 | 10.526 | 9.6673 | 3.053 | -0.18969 | 1.924% | -1.924%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1355 | 0.97791 | -3.7409 | -7.7583 | 10.526 | 9.4348 | 2.9799 | -0.18521 | 1.925% | -1.925%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -1.0005 | 0.97376 | -3.4871 | -10.526 | 10.526 | 8.8992 | 2.7696 | -0.23985 | 2.624% | -2.624%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0115 | -0.91871 | 0.9773 | -3.2334 | -10.526 | 10.526 | 8.3224 | 2.5912 | -0.2246 | 2.628% | -2.628%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.8499 | 0.98026 | -3.0208 | -10.526 | 10.526 | 7.8353 | 2.4404 | -0.21168 | 2.631% | -2.631%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99673 | -1.606 | 0.98157 | -2.6607 | -5.263 | 5.263 | 7.5082 | 2.336 | -0.20784 | 2.694% | -2.694%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99749 | -1.5523 | 0.98274 | -2.5778 | -5.263 | 5.263 | 7.3145 | 2.2761 | -0.20252 | 2.694% | -2.694%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.9979 | -1.5227 | 0.98338 | -2.532 | -5.263 | 5.263 | 7.2074 | 2.2429 | -0.19958 | 2.694% | -2.694%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99793 | -1.5203 | 0.98343 | -2.5283 | -5.263 | 5.263 | 7.1987 | 2.2402 | -0.19934 | 2.694% | -2.694%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99731 | -1.5647 | 0.98247 | -2.5969 | -5.263 | 5.263 | 7.3593 | 2.2899 | -0.20375 | 2.694% | -2.694%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99571 | -1.679 | 0.97998 | -2.7735 | -5.263 | 5.263 | 7.7709 | 2.4172 | -0.21505 | 2.693% | -2.693%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99331 | -1.8537 | 0.97624 | -3.0434 | -5.2525 | 5.2525 | 8.3943 | 2.6101 | -0.23166 | 2.686% | -2.686%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99236 | -1.983 | 0.97437 | -3.2362 | -5.1156 | 5.1156 | 8.8224 | 2.7466 | -0.23662 | 2.612% | -2.612%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99413 | -2.0495 | 0.97585 | -3.3162 | -4.7051 | 4.7051 | 8.9612 | 2.8028 | -0.21978 | 2.394% | -2.394%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.142 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8432 | 4.142 | 9.0495 | 2.8571 | -0.18049 | 1.955% | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99979 | -2.17 | 0.98123 | -3.4409 | -3.5736 | 3.5736 | 9.0929 | 2.8794 | -0.16807 | 1.815% | -1.815%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 1.0014 | -2.2035 | 0.98271 | -3.4754 | -3.2578 | 3.2578 | 9.1387 | 2.9039 | -0.15331 | 1.65% | -1.65%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 1.0009 | -2.1988 | 0.98219 | -3.472 | -3.3525 | 3.3525 | 9.1651 | 2.9102 | -0.15687 | 1.683% | -1.683%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 1 | -2.1904 | 0.9813 | -3.4673 | -3.5052 | 3.5052 | 9.1735 | 2.9081 | -0.16446 | 1.761% | -1.761%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.942 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 3.942 | 9.2201 | 2.9106 | -0.1839 | 1.955% | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 4.4578 | 9.4064 | 2.9691 | -0.18761 | 1.956% | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 4.9209 | 9.6897 | 3.058 | -0.19327 | 1.956% | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 5.1893 | 9.8044 | 3.0939 | -0.19556 | 1.956% | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 5.2577 | 9.7711 | 3.0835 | -0.19489 | 1.956% | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 5.263 | 9.6642 | 3.05 | -0.19276 | 1.956% | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 5.263 | 9.4319 | 2.9771 | -0.18812 | 1.956% | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99124 | -1.993 | 0.97309 | -3.2601 | -5.263 | 5.263 | 8.8932 | 2.7638 | -0.24582 | 2.69% | -2.69%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99355 | -1.8313 | 0.97665 | -3.0093 | -5.263 | 5.263 | 8.317 | 2.5859 | -0.23004 | 2.691% | -2.691%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99548 | -1.6956 | 0.97962 | -2.799 | -5.263 | 5.263 | 7.8303 | 2.4356 | -0.21669 | 2.693% | -2.693%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99673 | -1.606 | 0.98157 | -2.6607 | -5.263 | 5.263 | 7.5082 | 2.336 | -0.20784 | 2.694% | -2.694%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99749 | -1.5523 | 0.98274 | -2.5778 | -5.263 | 5.263 | 7.3145 | 2.2761 | -0.20252 | 2.694% | -2.694%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.9979 | -1.5227 | 0.98338 | -2.532 | -5.263 | 5.263 | 7.2074 | 2.2429 | -0.19958 | 2.694% | -2.694%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99793 | -1.5203 | 0.98343 | -2.5283 | -5.263 | 5.263 | 7.1987 | 2.2402 | -0.19934 | 2.694% | -2.694%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99731 | -1.5647 | 0.98247 | -2.5969 | -5.263 | 5.263 | 7.3593 | 2.2899 | -0.20375 | 2.694% | -2.694%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99571 | -1.679 | 0.97998 | -2.7735 | -5.263 | 5.263 | 7.7709 | 2.4172 | -0.21505 | 2.693% | -2.693%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99325 | -1.8528 | 0.97618 | -3.0426 | -5.263 | 5.263 | 8.3939 | 2.6097 | -0.23214 | 2.691% | -2.691%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99159 | -1.9715 | 0.9736 | -3.2264 | -5.2577 | 5.2577 | 8.8156 | 2.74 | -0.24344 | 2.687% | -2.687%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.9914 | -2.0091 | 0.97315 | -3.2819 | -5.2051 | 5.2051 | 8.9369 | 2.7791 | -0.24413 | 2.659% | -2.659%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8432 | 5.0946 | 9.0495 | 2.8571 | -0.18049 | 1.955% | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 4.9788 | 9.0799 | 2.8666 | -0.1811 | 1.955% | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 4.9156 | 9.1103 | 2.8762 | -0.1817 | 1.955% | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 4.9841 | 9.1397 | 2.8854 | -0.18229 | 1.955% | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 5.0156 | 9.1554 | 2.8903 | -0.1826 | 1.956% | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 5.1472 | 9.2201 | 2.9106 | -0.18389 | 1.955% | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 5.2367 | 9.4064 | 2.9691 | -0.18761 | 1.956% | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 5.263 | 9.6897 | 3.058 | -0.19327 | 1.956% | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 5.263 | 9.8044 | 3.0939 | -0.19556 | 1.956% | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 5.263 | 9.7711 | 3.0835 | -0.19489 | 1.956% | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 5.263 | 9.6642 | 3.05 | -0.19276 | 1.956% | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 5.263 | 9.4319 | 2.9771 | -0.18812 | 1.956% | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99124 | -1.993 | 0.97309 | -3.2601 | -5.263 | 5.263 | 8.8932 | 2.7638 | -0.24582 | 2.69% | -2.69%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99355 | -1.8313 | 0.97665 | -3.0093 | -5.263 | 5.263 | 8.317 | 2.5859 | -0.23004 | 2.691% | -2.691%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99548 | -1.6956 | 0.97962 | -2.799 | -5.263 | 5.263 | 7.8303 | 2.4356 | -0.21669 | 2.693% | -2.693%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99673 | -1.606 | 0.98157 | -2.6607 | -5.263 | 5.263 | 7.5082 | 2.336 | -0.20784 | 2.694% | -2.694%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99749 | -1.5523 | 0.98274 | -2.5778 | -5.263 | 5.263 | 7.3145 | 2.2761 | -0.20252 | 2.694% | -2.694%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.9979 | -1.5227 | 0.98338 | -2.532 | -5.263 | 5.263 | 7.2074 | 2.2429 | -0.19958 | 2.694% | -2.694%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99793 | -1.5203 | 0.98343 | -2.5283 | -5.263 | 5.263 | 7.1987 | 2.2402 | -0.19934 | 2.694% | -2.694%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99731 | -1.5647 | 0.98247 | -2.5969 | -5.263 | 5.263 | 7.3593 | 2.2899 | -0.20375 | 2.694% | -2.694%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99571 | -1.679 | 0.97998 | -2.7735 | -5.263 | 5.263 | 7.7709 | 2.4172 | -0.21505 | 2.693% | -2.693%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99325 | -1.8528 | 0.97618 | -3.0426 | -5.263 | 5.263 | 8.3939 | 2.6097 | -0.23214 | 2.691% | -2.691%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99156 | -1.9711 | 0.97358 | -3.2261 | -5.263 | 5.263 | 8.8153 | 2.7398 | -0.24369 | 2.69% | -2.69%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99108 | -2.0045 | 0.97284 | -3.278 | -5.263 | 5.263 | 8.9341 | 2.7764 | -0.24694 | 2.69% | -2.69%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 5.2577 | 9.0495 | 2.8571 | -0.18049 | 1.955% | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 5.2419 | 9.0799 | 2.8666 | -0.1811 | 1.955% | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 5.2262 | 9.1103 | 2.8762 | -0.1817 | 1.955% | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 5.2262 | 9.1397 | 2.8854 | -0.18229 | 1.955% | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 5.2367 | 9.1554 | 2.8903 | -0.1826 | 1.956% | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 5.2525 | 9.2201 | 2.9106 | -0.18389 | 1.955% | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 5.2577 | 9.4064 | 2.9691 | -0.18761 | 1.956% | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 5.263 | 9.6897 | 3.058 | -0.19327 | 1.956% | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 5.263 | 9.8044 | 3.0939 | -0.19556 | 1.956% | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 5.263 | 9.7711 | 3.0835 | -0.19489 | 1.956% | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 5.263 | 9.6642 | 3.05 | -0.19276 | 1.956% | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 5.263 | 9.4319 | 2.9771 | -0.18812 | 1.956% | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99124 | -1.993 | 0.97309 | -3.2601 | -5.263 | 5.263 | 8.8932 | 2.7638 | -0.24582 | 2.69% | -2.69%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99355 | -1.8313 | 0.97665 | -3.0093 | -5.263 | 5.263 | 8.317 | 2.5859 | -0.23004 | 2.691% | -2.691%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99548 | -1.6956 | 0.97962 | -2.799 | -5.263 | 5.263 | 7.8303 | 2.4356 | -0.21669 | 2.693% | -2.693%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5706 | 0.97922 | -2.6295 | -5.697 | 10.526 | 7.4904 | 2.319 | -0.22556 | 2.923% | -2.923%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3594 | 0.97052 | -2.4027 | -7.5155 | 10.526 | 7.225 | 2.1906 | -0.29202 | 3.885% | -3.885%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3299 | 0.97116 | -2.3568 | -7.5143 | 10.526 | 7.1193 | 2.1588 | -0.28774 | 3.885% | -3.885%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3274 | 0.97122 | -2.353 | -7.5142 | 10.526 | 7.1106 | 2.1562 | -0.28739 | 3.885% | -3.885%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3719 | 0.97025 | -2.422 | -7.5154 | 10.526 | 7.2692 | 2.2039 | -0.2938 | 3.885% | -3.885%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6436 | 0.97763 | -2.7425 | -5.698 | 10.526 | 7.7525 | 2.3996 | -0.23345 | 2.923% | -2.923%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8173 | 0.97381 | -3.012 | -5.7018 | 10.5049 | 8.3738 | 2.5903 | -0.25218 | 2.923% | -2.923%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9354 | 0.9712 | -3.1957 | -5.7039 | 10.2313 | 8.7942 | 2.7192 | -0.26484 | 2.924% | -2.924%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9688 | 0.97045 | -3.2477 | -5.7045 | 9.4102 | 8.9126 | 2.7555 | -0.26841 | 2.924% | -2.924%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.284 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 8.284 | 9.0495 | 2.8571 | -0.18049 | 1.955% | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 7.1472 | 9.0799 | 2.8666 | -0.1811 | 1.955% | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 6.5156 | 9.1103 | 2.8762 | -0.1817 | 1.955% | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 6.7051 | 9.1397 | 2.8854 | -0.18229 | 1.955% | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 7.0103 | 9.1554 | 2.8903 | -0.1826 | 1.956% | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.884 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 7.884 | 9.2201 | 2.9106 | -0.18389 | 1.955% | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 8.9155 | 9.4064 | 2.9691 | -0.18761 | 1.956% | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 9.8418 | 9.6897 | 3.058 | -0.19327 | 1.956% | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 10.3786 | 9.8044 | 3.0939 | -0.19556 | 1.956% | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 10.5155 | 9.7711 | 3.0835 | -0.19489 | 1.956% | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 10.526 | 9.6642 | 3.05 | -0.19276 | 1.956% | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 10.526 | 9.4319 | 2.9771 | -0.18812 | 1.956% | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.9573 | 0.97071 | -3.2298 | -5.7044 | 10.526 | 8.8718 | 2.743 | -0.26718 | 2.924% | -2.924%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7958 | 0.97428 | -2.9786 | -5.7013 | 10.526 | 8.2971 | 2.5668 | -0.24987 | 2.923% | -2.923%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6601 | 0.97727 | -2.7681 | -5.6987 | 10.526 | 7.8118 | 2.4177 | -0.23524 | 2.923% | -2.923%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5706 | 0.97922 | -2.6296 | -5.697 | 10.526 | 7.4904 | 2.319 | -0.22556 | 2.923% | -2.923%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3594 | 0.97052 | -2.4027 | -7.5155 | 10.526 | 7.225 | 2.1906 | -0.29202 | 3.885% | -3.885%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3299 | 0.97116 | -2.3568 | -7.5143 | 10.526 | 7.1193 | 2.1588 | -0.28774 | 3.885% | -3.885%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3274 | 0.97122 | -2.353 | -7.5142 | 10.526 | 7.1106 | 2.1562 | -0.28739 | 3.885% | -3.885%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3719 | 0.97025 | -2.422 | -7.5154 | 10.526 | 7.2692 | 2.2039 | -0.2938 | 3.885% | -3.885%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6436 | 0.97763 | -2.7425 | -5.698 | 10.526 | 7.7525 | 2.3996 | -0.23345 | 2.923% | -2.923%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8173 | 0.97381 | -3.012 | -5.7018 | 10.526 | 8.3738 | 2.5903 | -0.25218 | 2.923% | -2.923%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9354 | 0.9712 | -3.1957 | -5.7039 | 10.5155 | 8.7942 | 2.7192 | -0.26484 | 2.924% | -2.924%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9688 | 0.97045 | -3.2477 | -5.7045 | 10.4102 | 8.9126 | 2.7555 | -0.26841 | 2.924% | -2.924%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 10.1892 | 9.0495 | 2.8571 | -0.18049 | 1.955% | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 9.9576 | 9.0799 | 2.8666 | -0.1811 | 1.955% | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 9.8313 | 9.1103 | 2.8762 | -0.1817 | 1.955% | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 9.9681 | 9.1397 | 2.8854 | -0.18229 | 1.955% | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 10.0313 | 9.1554 | 2.8903 | -0.1826 | 1.956% | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 10.2944 | 9.2201 | 2.9106 | -0.18389 | 1.955% | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 10.4734 | 9.4064 | 2.9691 | -0.18761 | 1.956% | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 10.526 | 9.6897 | 3.058 | -0.19327 | 1.956% | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 10.526 | 9.8044 | 3.0939 | -0.19556 | 1.956% | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 10.526 | 9.7711 | 3.0835 | -0.19489 | 1.956% | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 10.526 | 9.6642 | 3.05 | -0.19276 | 1.956% | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 10.526 | 9.4319 | 2.9771 | -0.18812 | 1.956% | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.9573 | 0.97071 | -3.2298 | -5.7044 | 10.526 | 8.8718 | 2.743 | -0.26718 | 2.924% | -2.924%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7958 | 0.97428 | -2.9786 | -5.7013 | 10.526 | 8.2971 | 2.5668 | -0.24987 | 2.923% | -2.923%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6601 | 0.97727 | -2.7681 | -5.6987 | 10.526 | 7.8118 | 2.4177 | -0.23524 | 2.923% | -2.923%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5706 | 0.97922 | -2.6296 | -5.697 | 10.526 | 7.4904 | 2.319 | -0.22556 | 2.923% | -2.923%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3594 | 0.97052 | -2.4027 | -7.5155 | 10.526 | 7.225 | 2.1906 | -0.29202 | 3.885% | -3.885%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3299 | 0.97116 | -2.3568 | -7.5143 | 10.526 | 7.1193 | 2.1588 | -0.28774 | 3.885% | -3.885%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3274 | 0.97122 | -2.353 | -7.5142 | 10.526 | 7.1106 | 2.1562 | -0.28739 | 3.885% | -3.885%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3719 | 0.97025 | -2.422 | -7.5154 | 10.526 | 7.2692 | 2.2039 | -0.2938 | 3.885% | -3.885%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6436 | 0.97763 | -2.7425 | -5.698 | 10.526 | 7.7525 | 2.3996 | -0.23345 | 2.923% | -2.923%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8173 | 0.97381 | -3.012 | -5.7018 | 10.526 | 8.3738 | 2.5903 | -0.25218 | 2.923% | -2.923%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9354 | 0.9712 | -3.1957 | -5.7039 | 10.526 | 8.7942 | 2.7192 | -0.26484 | 2.924% | -2.924%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9688 | 0.97045 | -3.2477 | -5.7045 | 10.526 | 8.9126 | 2.7555 | -0.26841 | 2.924% | -2.924%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 10.5155 | 9.0495 | 2.8571 | -0.18049 | 1.955% | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 10.4839 | 9.0799 | 2.8666 | -0.1811 | 1.955% | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 10.4523 | 9.1103 | 2.8762 | -0.1817 | 1.955% | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 10.4523 | 9.1397 | 2.8854 | -0.18229 | 1.955% | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 10.4734 | 9.1554 | 2.8903 | -0.1826 | 1.956% | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 10.5049 | 9.2201 | 2.9106 | -0.18389 | 1.955% | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 10.5155 | 9.4064 | 2.9691 | -0.18761 | 1.956% | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 10.526 | 9.6897 | 3.058 | -0.19327 | 1.956% | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 10.526 | 9.8044 | 3.0939 | -0.19556 | 1.956% | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 10.526 | 9.7711 | 3.0835 | -0.19489 | 1.956% | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 10.526 | 9.6642 | 3.05 | -0.19276 | 1.956% | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 10.526 | 9.4319 | 2.9771 | -0.18812 | 1.956% | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.9573 | 0.97071 | -3.2298 | -5.7044 | 10.526 | 8.8718 | 2.743 | -0.26718 | 2.924% | -2.924%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7958 | 0.97428 | -2.9786 | -5.7013 | 10.526 | 8.2971 | 2.5668 | -0.24987 | 2.923% | -2.923%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6601 | 0.97727 | -2.7681 | -5.6987 | 10.526 | 7.8118 | 2.4177 | -0.23524 | 2.923% | -2.923%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0088 | -3.0638 | 1.0088 | -3.0638 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 5.263 | 7.4211 | 2.2527 | -0.29491 | 3.822% | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 5.263 | 7.2212 | 2.187 | -0.29583 | 3.935% | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 5.263 | 7.1109 | 2.1509 | -0.29611 | 3.998% | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 5.263 | 7.1019 | 2.1479 | -0.29613 | 4.003% | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 5.263 | 7.2673 | 2.2021 | -0.29567 | 3.909% | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 5.263 | 7.6931 | 2.3425 | -0.2929 | 3.668% | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 5.2525 | 8.3417 | 2.5593 | -0.28433 | 3.296% | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 5.1156 | 8.7835 | 2.7089 | -0.27545 | 3.041% | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 4.7051 | 8.9085 | 2.7515 | -0.2725 | 2.968% | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.142 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 4.142 | 8.9587 | 2.7687 | -0.27125 | 2.939% | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97143 | -3.195 | 0.97143 | -3.195 | -3.5736 | 3.5736 | 9.0036 | 2.7923 | -0.25744 | 2.78% | -2.78%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97383 | -3.2509 | 0.97383 | -3.2509 | -3.2578 | 3.2578 | 9.0573 | 2.8245 | -0.23469 | 2.526% | -2.526%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97287 | -3.251 | 0.97287 | -3.251 | -3.3525 | 3.3525 | 9.0794 | 2.8266 | -0.24259 | 2.602% | -2.602%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97152 | -3.2373 | 0.97152 | -3.2373 | -3.5052 | 3.5052 | 9.0835 | 2.8202 | -0.25449 | 2.725% | -2.725%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.942 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 3.942 | 9.1374 | 2.83 | -0.26657 | 2.835% | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 4.4578 | 9.333 | 2.8974 | -0.26098 | 2.72% | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 4.9209 | 9.6315 | 3.0008 | -0.25152 | 2.545% | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 5.1893 | 9.7526 | 3.043 | -0.24735 | 2.474% | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 5.2577 | 9.7174 | 3.0307 | -0.24858 | 2.494% | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 5.263 | 9.6046 | 2.9915 | -0.25241 | 2.561% | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 5.263 | 9.3598 | 2.9066 | -0.26018 | 2.705% | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 5.263 | 8.8655 | 2.7369 | -0.27354 | 2.993% | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 5.263 | 8.2613 | 2.5322 | -0.28567 | 3.342% | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 5.263 | 7.7547 | 2.363 | -0.29231 | 3.633% | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 5.263 | 7.4211 | 2.2527 | -0.29493 | 3.822% | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 5.263 | 7.2212 | 2.187 | -0.29583 | 3.935% | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 5.263 | 7.1109 | 2.1509 | -0.29611 | 3.998% | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 5.263 | 7.1019 | 2.1479 | -0.29613 | 4.003% | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 5.263 | 7.2673 | 2.2021 | -0.29567 | 3.909% | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 5.263 | 7.6931 | 2.3425 | -0.2929 | 3.668% | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 5.263 | 8.3417 | 2.5593 | -0.28433 | 3.296% | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 5.2577 | 8.7835 | 2.7089 | -0.27545 | 3.041% | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 5.2051 | 8.9085 | 2.7515 | -0.2725 | 2.968% | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 5.0946 | 8.9587 | 2.7687 | -0.27125 | 2.939% | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 4.9788 | 8.9906 | 2.7796 | -0.27045 | 2.92% | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 4.9156 | 9.0224 | 2.7905 | -0.26963 | 2.902% | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 4.9841 | 9.0532 | 2.8011 | -0.26883 | 2.884% | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 5.0156 | 9.0696 | 2.8067 | -0.2684 | 2.874% | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 5.1472 | 9.1374 | 2.83 | -0.26657 | 2.835% | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 5.2367 | 9.333 | 2.8974 | -0.26098 | 2.72% | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 5.263 | 9.6315 | 3.0008 | -0.25152 | 2.545% | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 5.263 | 9.7526 | 3.043 | -0.24735 | 2.474% | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 5.263 | 9.7174 | 3.0307 | -0.24858 | 2.494% | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 5.263 | 9.6046 | 2.9915 | -0.25241 | 2.561% | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 5.263 | 9.3598 | 2.9066 | -0.26018 | 2.705% | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 5.263 | 8.8655 | 2.7369 | -0.27354 | 2.993% | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 5.263 | 8.2613 | 2.5322 | -0.28567 | 3.342% | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 5.263 | 7.7547 | 2.363 | -0.29231 | 3.633% | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 5.263 | 7.4211 | 2.2527 | -0.29493 | 3.822% | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 5.263 | 7.2212 | 2.187 | -0.29583 | 3.935% | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 5.263 | 7.1109 | 2.1509 | -0.29611 | 3.998% | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 5.263 | 7.1019 | 2.1479 | -0.29613 | 4.003% | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 5.263 | 7.2673 | 2.2021 | -0.29567 | 3.909% | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 5.263 | 7.6931 | 2.3425 | -0.2929 | 3.668% | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 5.263 | 8.3417 | 2.5593 | -0.28433 | 3.296% | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 5.263 | 8.7835 | 2.7089 | -0.27545 | 3.041% | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 5.263 | 8.9085 | 2.7515 | -0.2725 | 2.968% | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 5.2577 | 8.9587 | 2.7687 | -0.27125 | 2.939% | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 5.2419 | 8.9906 | 2.7796 | -0.27045 | 2.92% | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 5.2262 | 9.0224 | 2.7905 | -0.26963 | 2.902% | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 5.2262 | 9.0532 | 2.8011 | -0.26883 | 2.884% | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 5.2367 | 9.0696 | 2.8067 | -0.2684 | 2.874% | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 5.2525 | 9.1374 | 2.83 | -0.26657 | 2.835% | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 5.2577 | 9.333 | 2.8974 | -0.26098 | 2.72% | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 5.263 | 9.6315 | 3.0008 | -0.25152 | 2.545% | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 5.263 | 9.7526 | 3.043 | -0.24735 | 2.474% | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 5.263 | 9.7174 | 3.0307 | -0.24858 | 2.494% | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 5.263 | 9.6046 | 2.9915 | -0.25241 | 2.561% | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 5.263 | 9.3598 | 2.9066 | -0.26018 | 2.705% | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 5.263 | 8.8655 | 2.7369 | -0.27354 | 2.993% | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 5.263 | 8.2613 | 2.5322 | -0.28567 | 3.342% | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 5.263 | 7.7547 | 2.363 | -0.29231 | 3.633% | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 10.526 | 7.4211 | 2.2527 | -0.29493 | 3.822% | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 10.526 | 7.2212 | 2.187 | -0.29583 | 3.935% | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 10.526 | 7.1109 | 2.1509 | -0.29611 | 3.998% | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 10.526 | 7.1019 | 2.1479 | -0.29613 | 4.003% | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 10.526 | 7.2673 | 2.2021 | -0.29567 | 3.909% | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 10.526 | 7.6931 | 2.3425 | -0.2929 | 3.668% | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 10.5049 | 8.3417 | 2.5593 | -0.28433 | 3.296% | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 10.2313 | 8.7835 | 2.7089 | -0.27545 | 3.041% | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 9.4102 | 8.9085 | 2.7515 | -0.2725 | 2.968% | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.284 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 8.284 | 8.9587 | 2.7687 | -0.27125 | 2.939% | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 7.1472 | 8.9906 | 2.7796 | -0.27045 | 2.92% | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 6.5156 | 9.0224 | 2.7905 | -0.26963 | 2.902% | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 6.7051 | 9.0532 | 2.8011 | -0.26883 | 2.884% | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 7.0103 | 9.0696 | 2.8067 | -0.2684 | 2.874% | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.884 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 7.884 | 9.1374 | 2.83 | -0.26657 | 2.835% | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 8.9155 | 9.333 | 2.8974 | -0.26098 | 2.72% | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 9.8418 | 9.6315 | 3.0008 | -0.25152 | 2.545% | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 10.3786 | 9.7526 | 3.043 | -0.24735 | 2.474% | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 10.5155 | 9.7174 | 3.0307 | -0.24858 | 2.494% | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 10.526 | 9.6046 | 2.9915 | -0.25241 | 2.561% | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 10.526 | 9.3598 | 2.9066 | -0.26018 | 2.705% | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 10.526 | 8.8655 | 2.7369 | -0.27354 | 2.993% | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 10.526 | 8.2613 | 2.5322 | -0.28567 | 3.342% | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 10.526 | 7.7547 | 2.363 | -0.29231 | 3.633% | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 10.526 | 7.4211 | 2.2527 | -0.29493 | 3.822% | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 10.526 | 7.2212 | 2.187 | -0.29583 | 3.935% | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 10.526 | 7.1109 | 2.1509 | -0.29611 | 3.998% | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 10.526 | 7.1019 | 2.1479 | -0.29613 | 4.003% | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 10.526 | 7.2673 | 2.2021 | -0.29567 | 3.909% | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 10.526 | 7.6931 | 2.3425 | -0.2929 | 3.668% | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 10.526 | 8.3417 | 2.5593 | -0.28433 | 3.296% | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 10.5155 | 8.7835 | 2.7089 | -0.27545 | 3.041% | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 10.4102 | 8.9085 | 2.7515 | -0.2725 | 2.968% | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 10.1892 | 8.9587 | 2.7687 | -0.27125 | 2.939% | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 9.9576 | 8.9906 | 2.7796 | -0.27045 | 2.92% | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 9.8313 | 9.0224 | 2.7905 | -0.26963 | 2.902% | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 9.9681 | 9.0532 | 2.8011 | -0.26883 | 2.884% | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 10.0313 | 9.0696 | 2.8067 | -0.2684 | 2.874% | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 10.2944 | 9.1374 | 2.83 | -0.26657 | 2.835% | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 10.4734 | 9.333 | 2.8974 | -0.26098 | 2.72% | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 10.526 | 9.6315 | 3.0008 | -0.25152 | 2.545% | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 10.526 | 9.7526 | 3.043 | -0.24735 | 2.474% | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 10.526 | 9.7174 | 3.0307 | -0.24858 | 2.494% | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 10.526 | 9.6046 | 2.9915 | -0.25241 | 2.561% | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 10.526 | 9.3598 | 2.9066 | -0.26018 | 2.705% | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 10.526 | 8.8655 | 2.7369 | -0.27354 | 2.993% | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 10.526 | 8.2613 | 2.5322 | -0.28567 | 3.342% | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 10.526 | 7.7547 | 2.363 | -0.29231 | 3.633% | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 10.526 | 7.4211 | 2.2527 | -0.29493 | 3.822% | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 10.526 | 7.2212 | 2.187 | -0.29583 | 3.935% | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 10.526 | 7.1109 | 2.1509 | -0.29611 | 3.998% | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 10.526 | 7.1019 | 2.1479 | -0.29613 | 4.003% | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 10.526 | 7.2673 | 2.2021 | -0.29567 | 3.909% | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 10.526 | 7.6931 | 2.3425 | -0.2929 | 3.668% | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 10.526 | 8.3417 | 2.5593 | -0.28433 | 3.296% | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 10.526 | 8.7835 | 2.7089 | -0.27545 | 3.041% | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 10.526 | 8.9085 | 2.7515 | -0.2725 | 2.968% | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 10.5155 | 8.9587 | 2.7687 | -0.27125 | 2.939% | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 10.4839 | 8.9906 | 2.7796 | -0.27045 | 2.92% | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 10.4523 | 9.0224 | 2.7905 | -0.26963 | 2.902% | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 10.4523 | 9.0532 | 2.8011 | -0.26883 | 2.884% | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 10.4734 | 9.0696 | 2.8067 | -0.2684 | 2.874% | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 10.5049 | 9.1374 | 2.83 | -0.26657 | 2.835% | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 10.5155 | 9.333 | 2.8974 | -0.26098 | 2.72% | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 10.526 | 9.6315 | 3.0008 | -0.25152 | 2.545% | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 10.526 | 9.7526 | 3.043 | -0.24735 | 2.474% | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 10.526 | 9.7174 | 3.0307 | -0.24858 | 2.494% | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 10.526 | 9.6046 | 2.9915 | -0.25241 | 2.561% | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 10.526 | 9.3598 | 2.9066 | -0.26018 | 2.705% | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 10.526 | 8.8655 | 2.7369 | -0.27354 | 2.993% | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 10.526 | 8.2613 | 2.5322 | -0.28567 | 3.342% | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 10.526 | 7.7547 | 2.363 | -0.29231 | 3.633% | -3.633%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1789 | 1.0293 | -0.94925 | 1.0036 | -3.0794 | -5.263 | 5.263 | 7.6149 | 1.5073 | -0.10107 | 1.31% | -1.31%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0295 | -0.92167 | 1.0045 | -2.9945 | -5.263 | 5.263 | 7.4186 | 1.4685 | -0.098441 | 1.31% | -1.31%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.90644 | 1.0051 | -2.9476 | -5.263 | 5.263 | 7.31 | 1.4471 | -0.097011 | 1.31% | -1.31%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90519 | 1.0051 | -2.9438 | -5.263 | 5.263 | 7.3011 | 1.4453 | -0.096896 | 1.31% | -1.31%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92805 | 1.0043 | -3.0141 | -5.263 | 5.263 | 7.464 | 1.4775 | -0.099039 | 1.31% | -1.31%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.98673 | 1.0023 | -3.195 | -5.263 | 5.263 | 7.8815 | 1.5599 | -0.10453 | 1.309% | -1.309%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0751 | 0.99929 | -3.4661 | -5.2525 | 5.2525 | 8.5141 | 1.6853 | -0.11186 | 1.297% | -1.297%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.028 | -1.1388 | 0.99751 | -3.6555 | -5.1156 | 5.1156 | 8.9447 | 1.7715 | -0.11427 | 1.261% | -1.261%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0289 | -1.1656 | 0.99796 | -3.7151 | -4.7051 | 4.7051 | 9.0747 | 1.801 | -0.10628 | 1.158% | -1.158%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.142 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0303 | -1.186 | 0.99913 | -3.7461 | -4.142 | 4.142 | 9.1361 | 1.8183 | -0.093877 | 1.017% | -1.017%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0316 | -1.2068 | 1.0002 | -3.7808 | -3.5736 | 3.5736 | 9.1785 | 1.8313 | -0.082523 | 0.8911% | -0.8911%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0324 | -1.2183 | 1.0009 | -3.7982 | -3.2578 | 3.2578 | 9.2167 | 1.8419 | -0.075344 | 0.8108% | -0.8108%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0322 | -1.2174 | 1.0007 | -3.798 | -3.3525 | 3.3525 | 9.2458 | 1.8475 | -0.076178 | 0.8172% | -0.8172%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0318 | -1.2161 | 1.0002 | -3.8025 | -3.5052 | 3.5052 | 9.2581 | 1.8485 | -0.079882 | 0.8554% | -0.8554%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.942 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0306 | -1.2149 | 0.99879 | -3.824 | -3.942 | 3.942 | 9.3133 | 1.8554 | -0.090747 | 0.965% | -0.965%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.029 | -1.2293 | 0.99653 | -3.8984 | -4.4578 | 4.4578 | 9.489 | 1.8854 | -0.10501 | 1.095% | -1.095%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0274 | -1.2596 | 0.99382 | -4.0211 | -4.9209 | 4.9209 | 9.7626 | 1.9347 | -0.12035 | 1.218% | -1.218%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0265 | -1.2699 | 0.99253 | -4.0692 | -5.1893 | 5.1893 | 9.8713 | 1.9534 | -0.12871 | 1.287% | -1.287%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2636 | 0.99252 | -4.0535 | -5.2577 | 5.2577 | 9.836 | 1.9457 | -0.13004 | 1.305% | -1.305%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0265 | -1.2481 | 0.99306 | -4.0057 | -5.263 | 5.263 | 9.7282 | 1.9244 | -0.12877 | 1.306% | -1.306%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.2148 | 0.99425 | -3.902 | -5.263 | 5.263 | 9.4943 | 1.8783 | -0.1257 | 1.307% | -1.307%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1474 | 0.99665 | -3.6926 | -5.263 | 5.263 | 9.0195 | 1.7846 | -0.11947 | 1.307% | -1.307%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0648 | 0.99957 | -3.4363 | -5.263 | 5.263 | 8.4352 | 1.6693 | -0.1118 | 1.308% | -1.308%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99521 | 1.002 | -3.2212 | -5.263 | 5.263 | 7.9417 | 1.5718 | -0.10532 | 1.309% | -1.309%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.94926 | 1.0036 | -3.0795 | -5.263 | 5.263 | 7.615 | 1.5073 | -0.10102 | 1.309% | -1.309%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0295 | -0.92167 | 1.0045 | -2.9945 | -5.263 | 5.263 | 7.4186 | 1.4685 | -0.098441 | 1.31% | -1.31%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.90644 | 1.0051 | -2.9476 | -5.263 | 5.263 | 7.31 | 1.4471 | -0.097011 | 1.31% | -1.31%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90519 | 1.0051 | -2.9438 | -5.263 | 5.263 | 7.3011 | 1.4453 | -0.096896 | 1.31% | -1.31%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92805 | 1.0043 | -3.0141 | -5.263 | 5.263 | 7.464 | 1.4775 | -0.099039 | 1.31% | -1.31%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.98673 | 1.0023 | -3.195 | -5.263 | 5.263 | 7.8815 | 1.5599 | -0.10453 | 1.309% | -1.309%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0281 | -1.0758 | 0.99918 | -3.4704 | -5.263 | 5.263 | 8.5132 | 1.6847 | -0.11283 | 1.308% | -1.308%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1364 | 0.99706 | -3.6579 | -5.2577 | 5.2577 | 8.9407 | 1.7691 | -0.11831 | 1.306% | -1.306%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0276 | -1.1547 | 0.99659 | -3.7115 | -5.2051 | 5.2051 | 9.0624 | 1.7936 | -0.11864 | 1.292% | -1.292%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0278 | -1.1632 | 0.99672 | -3.73 | -5.0946 | 5.0946 | 9.1141 | 1.8052 | -0.1159 | 1.256% | -1.256%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0281 | -1.1703 | 0.99686 | -3.7453 | -4.9788 | 4.9788 | 9.1474 | 1.8128 | -0.11358 | 1.226% | -1.226%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0282 | -1.1761 | 0.99687 | -3.7598 | -4.9156 | 4.9156 | 9.1795 | 1.8198 | -0.11248 | 1.21% | -1.21%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.028 | -1.1787 | 0.99654 | -3.7717 | -4.9841 | 4.9841 | 9.2076 | 1.8247 | -0.11445 | 1.228% | -1.228%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0279 | -1.1802 | 0.99638 | -3.7782 | -5.0156 | 5.0156 | 9.2226 | 1.8273 | -0.11538 | 1.236% | -1.236%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0275 | -1.1862 | 0.99572 | -3.8047 | -5.1472 | 5.1472 | 9.2847 | 1.8384 | -0.11931 | 1.269% | -1.269%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.027 | -1.2107 | 0.99454 | -3.886 | -5.2367 | 5.2367 | 9.4701 | 1.8741 | -0.12385 | 1.291% | -1.291%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0265 | -1.2518 | 0.99293 | -4.0171 | -5.263 | 5.263 | 9.7539 | 1.9295 | -0.1291 | 1.306% | -1.306%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0263 | -1.2682 | 0.99234 | -4.0684 | -5.263 | 5.263 | 9.8694 | 1.9523 | -0.13061 | 1.306% | -1.306%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2634 | 0.99251 | -4.0535 | -5.263 | 5.263 | 9.8358 | 1.9457 | -0.13017 | 1.306% | -1.306%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0265 | -1.2481 | 0.99306 | -4.0057 | -5.263 | 5.263 | 9.7282 | 1.9244 | -0.12877 | 1.306% | -1.306%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.2148 | 0.99425 | -3.902 | -5.263 | 5.263 | 9.4943 | 1.8783 | -0.1257 | 1.307% | -1.307%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1474 | 0.99665 | -3.6926 | -5.263 | 5.263 | 9.0195 | 1.7846 | -0.11947 | 1.307% | -1.307%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0648 | 0.99957 | -3.4363 | -5.263 | 5.263 | 8.4352 | 1.6693 | -0.1118 | 1.308% | -1.308%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99521 | 1.002 | -3.2212 | -5.263 | 5.263 | 7.9417 | 1.5718 | -0.10532 | 1.309% | -1.309%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.94926 | 1.0036 | -3.0795 | -5.263 | 5.263 | 7.615 | 1.5073 | -0.10102 | 1.309% | -1.309%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0295 | -0.92167 | 1.0045 | -2.9945 | -5.263 | 5.263 | 7.4186 | 1.4685 | -0.098441 | 1.31% | -1.31%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.90644 | 1.0051 | -2.9476 | -5.263 | 5.263 | 7.31 | 1.4471 | -0.097011 | 1.31% | -1.31%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90519 | 1.0051 | -2.9438 | -5.263 | 5.263 | 7.3011 | 1.4453 | -0.096896 | 1.31% | -1.31%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92805 | 1.0043 | -3.0141 | -5.263 | 5.263 | 7.464 | 1.4775 | -0.099039 | 1.31% | -1.31%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.98673 | 1.0023 | -3.195 | -5.263 | 5.263 | 7.8815 | 1.5599 | -0.10453 | 1.309% | -1.309%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0281 | -1.0758 | 0.99918 | -3.4704 | -5.263 | 5.263 | 8.5132 | 1.6847 | -0.11283 | 1.308% | -1.308%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1363 | 0.99705 | -3.6578 | -5.263 | 5.263 | 8.9406 | 1.769 | -0.11844 | 1.307% | -1.307%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0274 | -1.1533 | 0.99644 | -3.7108 | -5.263 | 5.263 | 9.061 | 1.7928 | -0.12002 | 1.307% | -1.307%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0273 | -1.1603 | 0.99621 | -3.7322 | -5.2577 | 5.2577 | 9.1095 | 1.8024 | -0.12053 | 1.306% | -1.306%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0274 | -1.165 | 0.9961 | -3.7458 | -5.2419 | 5.2419 | 9.1405 | 1.8087 | -0.12055 | 1.302% | -1.302%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0274 | -1.1697 | 0.99599 | -3.7595 | -5.2262 | 5.2262 | 9.1714 | 1.8149 | -0.12057 | 1.298% | -1.298%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0273 | -1.1739 | 0.99584 | -3.7726 | -5.2262 | 5.2262 | 9.201 | 1.8208 | -0.12095 | 1.298% | -1.298%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0273 | -1.1749 | 0.99582 | -3.7746 | -5.2367 | 5.2367 | 9.2174 | 1.8242 | -0.12059 | 1.291% | -1.291%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0272 | -1.1837 | 0.99545 | -3.803 | -5.2525 | 5.2525 | 9.2822 | 1.8369 | -0.12181 | 1.295% | -1.295%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0269 | -1.2113 | 0.9944 | -3.8908 | -5.2577 | 5.2577 | 9.4688 | 1.8733 | -0.12523 | 1.305% | -1.305%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0265 | -1.2518 | 0.99293 | -4.0171 | -5.263 | 5.263 | 9.7539 | 1.9295 | -0.1291 | 1.306% | -1.306%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0263 | -1.2682 | 0.99234 | -4.0684 | -5.263 | 5.263 | 9.8694 | 1.9523 | -0.13061 | 1.306% | -1.306%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2634 | 0.99251 | -4.0535 | -5.263 | 5.263 | 9.8358 | 1.9457 | -0.13017 | 1.306% | -1.306%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0265 | -1.2481 | 0.99306 | -4.0057 | -5.263 | 5.263 | 9.7282 | 1.9244 | -0.12877 | 1.306% | -1.306%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.2148 | 0.99425 | -3.902 | -5.263 | 5.263 | 9.4943 | 1.8783 | -0.1257 | 1.307% | -1.307%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1474 | 0.99665 | -3.6926 | -5.263 | 5.263 | 9.0195 | 1.7846 | -0.11947 | 1.307% | -1.307%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0648 | 0.99957 | -3.4363 | -5.263 | 5.263 | 8.4352 | 1.6693 | -0.1118 | 1.308% | -1.308%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99521 | 1.002 | -3.2212 | -5.263 | 5.263 | 7.9417 | 1.5718 | -0.10532 | 1.309% | -1.309%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0153 | -0.82299 | 0.98984 | -2.9909 | -10.526 | 10.526 | 7.5108 | 1.4463 | -0.20515 | 2.659% | -2.659%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.79536 | 0.99079 | -2.9048 | -10.526 | 10.526 | 7.3171 | 1.4091 | -0.19989 | 2.659% | -2.659%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.7801 | 0.99131 | -2.8573 | -10.526 | 10.526 | 7.21 | 1.3886 | -0.19698 | 2.659% | -2.659%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0157 | -0.77886 | 0.99136 | -2.8534 | -10.526 | 10.526 | 7.2013 | 1.3869 | -0.19674 | 2.659% | -2.659%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0155 | -0.80174 | 0.99057 | -2.9247 | -10.526 | 10.526 | 7.3619 | 1.4177 | -0.20111 | 2.659% | -2.659%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.86052 | 0.98855 | -3.1079 | -10.526 | 10.526 | 7.7737 | 1.4966 | -0.21231 | 2.658% | -2.658%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0143 | -0.948 | 0.98566 | -3.3774 | -10.5049 | 10.5049 | 8.3986 | 1.617 | -0.22741 | 2.636% | -2.636%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0145 | -1.0151 | 0.98426 | -3.5713 | -10.2313 | 10.2313 | 8.8266 | 1.7015 | -0.23235 | 2.565% | -2.565%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0165 | -1.0522 | 0.98581 | -3.6382 | -9.4102 | 9.4102 | 8.9649 | 1.7358 | -0.2161 | 2.354% | -2.354%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.284 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0194 | -1.0868 | 0.98847 | -3.68 | -8.284 | 8.284 | 9.039 | 1.7606 | -0.19099 | 2.069% | -2.069%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0223 | -1.1212 | 0.99112 | -3.7221 | -7.1472 | 7.1472 | 9.0949 | 1.7816 | -0.16609 | 1.793% | -1.793%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0239 | -1.14 | 0.99261 | -3.7435 | -6.5156 | 6.5156 | 9.1405 | 1.7965 | -0.15151 | 1.631% | -1.631%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0235 | -1.1374 | 0.99213 | -3.7439 | -6.7051 | 6.7051 | 9.1669 | 1.8005 | -0.15505 | 1.663% | -1.663%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0227 | -1.1323 | 0.99127 | -3.7459 | -7.0103 | 7.0103 | 9.1754 | 1.7993 | -0.16255 | 1.741% | -1.741%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.884 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0203 | -1.1205 | 0.98867 | -3.761 | -7.884 | 7.884 | 9.2193 | 1.7995 | -0.18468 | 1.964% | -1.964%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0173 | -1.122 | 0.98505 | -3.8274 | -8.9155 | 8.9155 | 9.3804 | 1.8207 | -0.21358 | 2.226% | -2.226%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0144 | -1.142 | 0.98105 | -3.9487 | -9.8418 | 9.8418 | 9.6382 | 1.8605 | -0.24478 | 2.477% | -2.477%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0128 | -1.1459 | 0.97903 | -3.9945 | -10.3786 | 10.3786 | 9.7383 | 1.874 | -0.26173 | 2.617% | -2.617%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0124 | -1.1379 | 0.97883 | -3.9778 | -10.5155 | 10.5155 | 9.7016 | 1.8655 | -0.26441 | 2.653% | -2.653%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0126 | -1.1223 | 0.97935 | -3.9293 | -10.526 | 10.526 | 9.5952 | 1.8451 | -0.2618 | 2.656% | -2.656%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.0129 | -1.089 | 0.98054 | -3.8243 | -10.526 | 10.526 | 9.3645 | 1.801 | -0.25554 | 2.656% | -2.656%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0135 | -1.0215 | 0.98293 | -3.612 | -10.526 | 10.526 | 8.8962 | 1.7115 | -0.24281 | 2.657% | -2.657%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0143 | -0.9387 | 0.98583 | -3.3524 | -10.526 | 10.526 | 8.3198 | 1.6012 | -0.22715 | 2.658% | -2.658%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0149 | -0.86901 | 0.98825 | -3.1344 | -10.526 | 10.526 | 7.8331 | 1.508 | -0.21392 | 2.658% | -2.658%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0153 | -0.82298 | 0.98984 | -2.9909 | -10.526 | 10.526 | 7.5108 | 1.4463 | -0.20516 | 2.659% | -2.659%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.79536 | 0.99079 | -2.9048 | -10.526 | 10.526 | 7.3171 | 1.4091 | -0.19989 | 2.659% | -2.659%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.7801 | 0.99131 | -2.8573 | -10.526 | 10.526 | 7.21 | 1.3886 | -0.19698 | 2.659% | -2.659%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0157 | -0.77886 | 0.99136 | -2.8534 | -10.526 | 10.526 | 7.2013 | 1.3869 | -0.19674 | 2.659% | -2.659%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0155 | -0.80174 | 0.99057 | -2.9247 | -10.526 | 10.526 | 7.3619 | 1.4177 | -0.20111 | 2.659% | -2.659%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.86052 | 0.98855 | -3.1079 | -10.526 | 10.526 | 7.7737 | 1.4966 | -0.21231 | 2.658% | -2.658%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0142 | -0.94973 | 0.98545 | -3.3869 | -10.526 | 10.526 | 8.3968 | 1.616 | -0.22924 | 2.658% | -2.658%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0136 | -1.0105 | 0.98335 | -3.5769 | -10.5155 | 10.5155 | 8.8186 | 1.6968 | -0.24045 | 2.654% | -2.654%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0138 | -1.0301 | 0.98303 | -3.6319 | -10.4102 | 10.4102 | 8.9399 | 1.721 | -0.24114 | 2.627% | -2.627%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0144 | -1.04 | 0.98353 | -3.6469 | -10.1892 | 10.1892 | 8.9943 | 1.7341 | -0.23571 | 2.554% | -2.554%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.015 | -1.05 | 0.98399 | -3.6643 | -9.9576 | 9.9576 | 9.03 | 1.7431 | -0.23098 | 2.494% | -2.494%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0153 | -1.0574 | 0.98416 | -3.68 | -9.8313 | 9.8313 | 9.0633 | 1.7507 | -0.22873 | 2.462% | -2.462%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0149 | -1.0583 | 0.98366 | -3.6909 | -9.9681 | 9.9681 | 9.0893 | 1.7544 | -0.23274 | 2.497% | -2.497%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0147 | -1.059 | 0.98341 | -3.6969 | -10.0313 | 10.0313 | 9.1033 | 1.7565 | -0.23465 | 2.513% | -2.513%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0139 | -1.0618 | 0.98239 | -3.7217 | -10.2944 | 10.2944 | 9.1613 | 1.7651 | -0.24266 | 2.58% | -2.58%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0132 | -1.084 | 0.98098 | -3.8025 | -10.4734 | 10.4734 | 9.3421 | 1.7979 | -0.25194 | 2.626% | -2.626%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0125 | -1.126 | 0.97922 | -3.9408 | -10.526 | 10.526 | 9.6205 | 1.85 | -0.26249 | 2.656% | -2.656%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0124 | -1.1424 | 0.97863 | -3.9928 | -10.526 | 10.526 | 9.7344 | 1.8717 | -0.26558 | 2.656% | -2.656%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0124 | -1.1377 | 0.97881 | -3.9777 | -10.526 | 10.526 | 9.7013 | 1.8654 | -0.26468 | 2.656% | -2.656%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0126 | -1.1223 | 0.97935 | -3.9293 | -10.526 | 10.526 | 9.5952 | 1.8451 | -0.2618 | 2.656% | -2.656%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.0129 | -1.089 | 0.98054 | -3.8243 | -10.526 | 10.526 | 9.3645 | 1.801 | -0.25554 | 2.656% | -2.656%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0135 | -1.0215 | 0.98293 | -3.612 | -10.526 | 10.526 | 8.8962 | 1.7115 | -0.24281 | 2.657% | -2.657%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0143 | -0.9387 | 0.98583 | -3.3524 | -10.526 | 10.526 | 8.3198 | 1.6012 | -0.22715 | 2.658% | -2.658%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0149 | -0.86901 | 0.98825 | -3.1344 | -10.526 | 10.526 | 7.8331 | 1.508 | -0.21392 | 2.658% | -2.658%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0153 | -0.82298 | 0.98984 | -2.9909 | -10.526 | 10.526 | 7.5108 | 1.4463 | -0.20516 | 2.659% | -2.659%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.79536 | 0.99079 | -2.9048 | -10.526 | 10.526 | 7.3171 | 1.4091 | -0.19989 | 2.659% | -2.659%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.7801 | 0.99131 | -2.8573 | -10.526 | 10.526 | 7.21 | 1.3886 | -0.19698 | 2.659% | -2.659%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0157 | -0.77886 | 0.99136 | -2.8534 | -10.526 | 10.526 | 7.2013 | 1.3869 | -0.19674 | 2.659% | -2.659%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0155 | -0.80174 | 0.99057 | -2.9247 | -10.526 | 10.526 | 7.3619 | 1.4177 | -0.20111 | 2.659% | -2.659%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.86052 | 0.98855 | -3.1079 | -10.526 | 10.526 | 7.7737 | 1.4966 | -0.21231 | 2.658% | -2.658%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0142 | -0.94973 | 0.98545 | -3.3869 | -10.526 | 10.526 | 8.3968 | 1.616 | -0.22924 | 2.658% | -2.658%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0136 | -1.0103 | 0.98332 | -3.5768 | -10.526 | 10.526 | 8.8183 | 1.6966 | -0.24069 | 2.657% | -2.657%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0135 | -1.0274 | 0.98272 | -3.6305 | -10.526 | 10.526 | 8.9371 | 1.7193 | -0.24392 | 2.657% | -2.657%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0134 | -1.0345 | 0.98251 | -3.6522 | -10.5155 | 10.5155 | 8.985 | 1.7286 | -0.24497 | 2.654% | -2.654%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0135 | -1.0396 | 0.98244 | -3.6662 | -10.4839 | 10.4839 | 9.016 | 1.7348 | -0.24502 | 2.646% | -2.646%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0135 | -1.0447 | 0.98237 | -3.6803 | -10.4523 | 10.4523 | 9.0469 | 1.7411 | -0.24507 | 2.637% | -2.637%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0135 | -1.0489 | 0.98222 | -3.6935 | -10.4523 | 10.4523 | 9.0761 | 1.7466 | -0.24586 | 2.637% | -2.637%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0135 | -1.0482 | 0.98225 | -3.6897 | -10.4734 | 10.4734 | 9.0927 | 1.7502 | -0.24527 | 2.627% | -2.627%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0133 | -1.0566 | 0.98184 | -3.7183 | -10.5049 | 10.5049 | 9.1562 | 1.7621 | -0.24775 | 2.635% | -2.635%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0129 | -1.0856 | 0.9807 | -3.8129 | -10.5155 | 10.5155 | 9.3394 | 1.7964 | -0.25458 | 2.654% | -2.654%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0125 | -1.126 | 0.97922 | -3.9408 | -10.526 | 10.526 | 9.6205 | 1.85 | -0.26249 | 2.656% | -2.656%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0124 | -1.1424 | 0.97863 | -3.9928 | -10.526 | 10.526 | 9.7344 | 1.8717 | -0.26558 | 2.656% | -2.656%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0124 | -1.1377 | 0.97881 | -3.9777 | -10.526 | 10.526 | 9.7013 | 1.8654 | -0.26468 | 2.656% | -2.656%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0126 | -1.1223 | 0.97935 | -3.9293 | -10.526 | 10.526 | 9.5952 | 1.8451 | -0.2618 | 2.656% | -2.656%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.0129 | -1.089 | 0.98054 | -3.8243 | -10.526 | 10.526 | 9.3645 | 1.801 | -0.25554 | 2.656% | -2.656%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0135 | -1.0215 | 0.98293 | -3.612 | -10.526 | 10.526 | 8.8962 | 1.7115 | -0.24281 | 2.657% | -2.657%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0143 | -0.9387 | 0.98583 | -3.3524 | -10.526 | 10.526 | 8.3198 | 1.6012 | -0.22715 | 2.658% | -2.658%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0149 | -0.86901 | 0.98825 | -3.1344 | -10.526 | 10.526 | 7.8331 | 1.508 | -0.21392 | 2.658% | -2.658%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0296 | -2.1143 | 1.0168 | -3.1788 | 1.0019 | -1.6728 | 0.98929 | -2.7709 | -5.263 | 5.263 | 7.5067 | 1.4438 | -0.20931 | 2.713% | -2.713%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0025 | -1.6177 | 0.99024 | -2.6858 | -5.263 | 5.263 | 7.3131 | 1.4068 | -0.20391 | 2.713% | -2.713%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.0028 | -1.5873 | 0.99077 | -2.6388 | -5.263 | 5.263 | 7.2061 | 1.3863 | -0.20092 | 2.713% | -2.713%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0029 | -1.5848 | 0.99081 | -2.635 | -5.263 | 5.263 | 7.1973 | 1.3846 | -0.20068 | 2.713% | -2.713%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0023 | -1.6304 | 0.99002 | -2.7055 | -5.263 | 5.263 | 7.3578 | 1.4153 | -0.20516 | 2.713% | -2.713%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.001 | -1.7478 | 0.98799 | -2.8868 | -5.263 | 5.263 | 7.7694 | 1.4941 | -0.21665 | 2.713% | -2.713%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99924 | -1.9218 | 0.9851 | -3.1543 | -5.2525 | 5.2525 | 8.3939 | 1.6143 | -0.23213 | 2.691% | -2.691%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99861 | -2.0543 | 0.98371 | -3.3521 | -5.1156 | 5.1156 | 8.8218 | 1.6987 | -0.23724 | 2.619% | -2.619%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 1.0004 | -2.1236 | 0.98531 | -3.4367 | -4.7051 | 4.7051 | 8.9604 | 1.7331 | -0.22064 | 2.403% | -2.403%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.142 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 1.0033 | -2.1863 | 0.98802 | -3.5032 | -4.142 | 4.142 | 9.035 | 1.7582 | -0.19505 | 2.113% | -2.113%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 1.0061 | -2.2485 | 0.99073 | -3.5693 | -3.5736 | 3.5736 | 9.0914 | 1.7796 | -0.16957 | 1.831% | -1.831%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 1.0077 | -2.2824 | 0.99227 | -3.6045 | -3.2578 | 3.2578 | 9.1373 | 1.7947 | -0.15468 | 1.665% | -1.665%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 1.0072 | -2.2778 | 0.99178 | -3.6014 | -3.3525 | 3.3525 | 9.1637 | 1.7986 | -0.15827 | 1.698% | -1.698%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 1.0064 | -2.2694 | 0.9909 | -3.5967 | -3.5052 | 3.5052 | 9.1721 | 1.7973 | -0.16594 | 1.777% | -1.777%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.942 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 1.0038 | -2.2513 | 0.98825 | -3.5926 | -3.942 | 3.942 | 9.2154 | 1.7972 | -0.18862 | 2.006% | -2.006%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 1.0004 | -2.2604 | 0.98457 | -3.6352 | -4.4578 | 4.4578 | 9.3759 | 1.818 | -0.21812 | 2.273% | -2.273%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99688 | -2.3066 | 0.9805 | -3.734 | -4.9209 | 4.9209 | 9.6329 | 1.8573 | -0.25013 | 2.531% | -2.531%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99502 | -2.3178 | 0.97844 | -3.767 | -5.1893 | 5.1893 | 9.7325 | 1.8706 | -0.26748 | 2.675% | -2.675%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99475 | -2.3027 | 0.97824 | -3.7474 | -5.2577 | 5.2577 | 9.6958 | 1.8621 | -0.27022 | 2.711% | -2.711%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99508 | -2.2715 | 0.97876 | -3.6992 | -5.263 | 5.263 | 9.5895 | 1.8417 | -0.26753 | 2.714% | -2.714%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99585 | -2.2047 | 0.97995 | -3.5953 | -5.263 | 5.263 | 9.3589 | 1.7977 | -0.26108 | 2.714% | -2.714%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.9974 | -2.0696 | 0.98235 | -3.3853 | -5.263 | 5.263 | 8.891 | 1.7084 | -0.24799 | 2.714% | -2.714%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99929 | -1.904 | 0.98526 | -3.1285 | -5.263 | 5.263 | 8.3151 | 1.5984 | -0.23189 | 2.713% | -2.713%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0009 | -1.7647 | 0.9877 | -2.913 | -5.263 | 5.263 | 7.8287 | 1.5054 | -0.21831 | 2.713% | -2.713%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0019 | -1.6728 | 0.98929 | -2.7709 | -5.263 | 5.263 | 7.5067 | 1.4438 | -0.20932 | 2.713% | -2.713%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0025 | -1.6177 | 0.99024 | -2.6858 | -5.263 | 5.263 | 7.3131 | 1.4068 | -0.20391 | 2.713% | -2.713%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.0028 | -1.5873 | 0.99077 | -2.6388 | -5.263 | 5.263 | 7.2061 | 1.3863 | -0.20092 | 2.713% | -2.713%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0029 | -1.5848 | 0.99081 | -2.635 | -5.263 | 5.263 | 7.1973 | 1.3846 | -0.20068 | 2.713% | -2.713%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0023 | -1.6304 | 0.99002 | -2.7055 | -5.263 | 5.263 | 7.3578 | 1.4153 | -0.20516 | 2.713% | -2.713%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.001 | -1.7478 | 0.98799 | -2.8868 | -5.263 | 5.263 | 7.7694 | 1.4941 | -0.21665 | 2.713% | -2.713%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99904 | -1.926 | 0.98488 | -3.1627 | -5.263 | 5.263 | 8.392 | 1.6131 | -0.23404 | 2.713% | -2.713%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99769 | -2.0476 | 0.98277 | -3.3509 | -5.2577 | 5.2577 | 8.8134 | 1.6937 | -0.24556 | 2.711% | -2.711%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99759 | -2.0861 | 0.98246 | -3.4076 | -5.2051 | 5.2051 | 8.9347 | 1.7179 | -0.24629 | 2.683% | -2.683%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99818 | -2.1039 | 0.98298 | -3.4279 | -5.0946 | 5.0946 | 8.9893 | 1.7311 | -0.24069 | 2.608% | -2.608%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.9987 | -2.1225 | 0.98345 | -3.4503 | -4.9788 | 4.9788 | 9.0251 | 1.7402 | -0.23586 | 2.547% | -2.547%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99894 | -2.1366 | 0.98363 | -3.4687 | -4.9156 | 4.9156 | 9.0584 | 1.7479 | -0.23357 | 2.514% | -2.514%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99848 | -2.1392 | 0.98312 | -3.4764 | -4.9841 | 4.9841 | 9.0843 | 1.7515 | -0.23767 | 2.55% | -2.55%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99826 | -2.1409 | 0.98287 | -3.4809 | -5.0156 | 5.0156 | 9.0984 | 1.7536 | -0.23963 | 2.566% | -2.566%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99733 | -2.1481 | 0.98183 | -3.4995 | -5.1472 | 5.1472 | 9.1562 | 1.762 | -0.24783 | 2.635% | -2.635%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99623 | -2.1937 | 0.9804 | -3.5754 | -5.2367 | 5.2367 | 9.3367 | 1.7947 | -0.25735 | 2.682% | -2.682%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.995 | -2.2789 | 0.97863 | -3.7106 | -5.263 | 5.263 | 9.6148 | 1.8465 | -0.26824 | 2.714% | -2.714%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99461 | -2.3119 | 0.97804 | -3.762 | -5.263 | 5.263 | 9.7286 | 1.8682 | -0.27142 | 2.714% | -2.714%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99472 | -2.3023 | 0.97821 | -3.747 | -5.263 | 5.263 | 9.6955 | 1.8619 | -0.2705 | 2.714% | -2.714%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99508 | -2.2715 | 0.97876 | -3.6992 | -5.263 | 5.263 | 9.5895 | 1.8417 | -0.26753 | 2.714% | -2.714%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99585 | -2.2047 | 0.97995 | -3.5953 | -5.263 | 5.263 | 9.3589 | 1.7977 | -0.26108 | 2.714% | -2.714%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.9974 | -2.0696 | 0.98235 | -3.3853 | -5.263 | 5.263 | 8.891 | 1.7084 | -0.24799 | 2.714% | -2.714%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99929 | -1.904 | 0.98526 | -3.1285 | -5.263 | 5.263 | 8.3151 | 1.5984 | -0.23189 | 2.713% | -2.713%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0009 | -1.7647 | 0.9877 | -2.913 | -5.263 | 5.263 | 7.8287 | 1.5054 | -0.21831 | 2.713% | -2.713%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0019 | -1.6728 | 0.98929 | -2.7709 | -5.263 | 5.263 | 7.5067 | 1.4438 | -0.20932 | 2.713% | -2.713%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0025 | -1.6177 | 0.99024 | -2.6858 | -5.263 | 5.263 | 7.3131 | 1.4068 | -0.20391 | 2.713% | -2.713%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.0028 | -1.5873 | 0.99077 | -2.6388 | -5.263 | 5.263 | 7.2061 | 1.3863 | -0.20092 | 2.713% | -2.713%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0029 | -1.5848 | 0.99081 | -2.635 | -5.263 | 5.263 | 7.1973 | 1.3846 | -0.20068 | 2.713% | -2.713%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0023 | -1.6304 | 0.99002 | -2.7055 | -5.263 | 5.263 | 7.3578 | 1.4153 | -0.20516 | 2.713% | -2.713%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.001 | -1.7478 | 0.98799 | -2.8868 | -5.263 | 5.263 | 7.7694 | 1.4941 | -0.21665 | 2.713% | -2.713%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99904 | -1.926 | 0.98488 | -3.1627 | -5.263 | 5.263 | 8.392 | 1.6131 | -0.23404 | 2.713% | -2.713%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99766 | -2.0472 | 0.98275 | -3.3505 | -5.263 | 5.263 | 8.8132 | 1.6936 | -0.24581 | 2.713% | -2.713%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99727 | -2.0814 | 0.98214 | -3.4036 | -5.263 | 5.263 | 8.9319 | 1.7162 | -0.24913 | 2.714% | -2.714%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99714 | -2.0956 | 0.98193 | -3.4253 | -5.2577 | 5.2577 | 8.9798 | 1.7255 | -0.2502 | 2.711% | -2.711%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99713 | -2.1055 | 0.98186 | -3.4399 | -5.2419 | 5.2419 | 9.0107 | 1.7317 | -0.25027 | 2.702% | -2.702%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99712 | -2.1155 | 0.98179 | -3.4545 | -5.2262 | 5.2262 | 9.0417 | 1.7379 | -0.25032 | 2.694% | -2.694%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99702 | -2.1239 | 0.98164 | -3.4676 | -5.2262 | 5.2262 | 9.0709 | 1.7435 | -0.25113 | 2.694% | -2.694%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99706 | -2.122 | 0.98168 | -3.4639 | -5.2367 | 5.2367 | 9.0875 | 1.7471 | -0.25049 | 2.682% | -2.682%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99676 | -2.1391 | 0.98127 | -3.4914 | -5.2525 | 5.2525 | 9.151 | 1.7589 | -0.25304 | 2.691% | -2.691%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99597 | -2.1978 | 0.98011 | -3.5842 | -5.2577 | 5.2577 | 9.3339 | 1.7931 | -0.2601 | 2.711% | -2.711%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.995 | -2.2789 | 0.97863 | -3.7106 | -5.263 | 5.263 | 9.6148 | 1.8465 | -0.26824 | 2.714% | -2.714%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99461 | -2.3119 | 0.97804 | -3.762 | -5.263 | 5.263 | 9.7286 | 1.8682 | -0.27142 | 2.714% | -2.714%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99472 | -2.3023 | 0.97821 | -3.747 | -5.263 | 5.263 | 9.6955 | 1.8619 | -0.2705 | 2.714% | -2.714%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99508 | -2.2715 | 0.97876 | -3.6992 | -5.263 | 5.263 | 9.5895 | 1.8417 | -0.26753 | 2.714% | -2.714%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99585 | -2.2047 | 0.97995 | -3.5953 | -5.263 | 5.263 | 9.3589 | 1.7977 | -0.26108 | 2.714% | -2.714%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.9974 | -2.0696 | 0.98235 | -3.3853 | -5.263 | 5.263 | 8.891 | 1.7084 | -0.24799 | 2.714% | -2.714%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99929 | -1.904 | 0.98526 | -3.1285 | -5.263 | 5.263 | 8.3151 | 1.5984 | -0.23189 | 2.713% | -2.713%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0009 | -1.7647 | 0.9877 | -2.913 | -5.263 | 5.263 | 7.8287 | 1.5054 | -0.21831 | 2.713% | -2.713%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4815 | 0.97713 | -2.5966 | -7.4845 | 10.526 | 7.4155 | 1.3906 | -0.30053 | 3.895% | -3.895%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99024 | -1.4264 | 0.97809 | -2.511 | -7.4837 | 10.526 | 7.2242 | 1.355 | -0.29275 | 3.895% | -3.895%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3959 | 0.97861 | -2.4637 | -7.4836 | 10.526 | 7.1185 | 1.3353 | -0.28845 | 3.894% | -3.894%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3934 | 0.97865 | -2.4599 | -7.4836 | 10.526 | 7.1099 | 1.3337 | -0.2881 | 3.894% | -3.894%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4391 | 0.97787 | -2.5308 | -7.4839 | 10.526 | 7.2685 | 1.3632 | -0.29455 | 3.895% | -3.895%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5564 | 0.97584 | -2.7131 | -7.4846 | 10.526 | 7.6749 | 1.4389 | -0.31109 | 3.895% | -3.895%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7347 | 0.97273 | -2.9907 | -7.4854 | 10.5049 | 8.2899 | 1.5531 | -0.33613 | 3.897% | -3.897%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.8559 | 0.9706 | -3.1796 | -7.4858 | 10.2313 | 8.7059 | 1.6303 | -0.35309 | 3.898% | -3.898%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99501 | -2.048 | 0.9799 | -3.3749 | -5.6736 | 9.4102 | 8.9117 | 1.7043 | -0.26929 | 2.933% | -2.933%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.284 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99485 | -2.0617 | 0.97965 | -3.3962 | -5.6741 | 8.284 | 8.9593 | 1.7134 | -0.27073 | 2.933% | -2.933%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0704 | 0.9795 | -3.4098 | -5.6741 | 7.1472 | 8.9894 | 1.7191 | -0.27164 | 2.933% | -2.933%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.0791 | 0.97935 | -3.4233 | -5.6741 | 6.5156 | 9.0194 | 1.7248 | -0.27256 | 2.933% | -2.933%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0875 | 0.9792 | -3.4364 | -5.6742 | 6.7051 | 9.0486 | 1.7303 | -0.27344 | 2.933% | -2.933%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.092 | 0.97912 | -3.4434 | -5.6742 | 7.0103 | 9.0641 | 1.7333 | -0.27391 | 2.933% | -2.933%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.884 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1106 | 0.97879 | -3.4723 | -5.6742 | 7.884 | 9.1281 | 1.7454 | -0.27586 | 2.933% | -2.933%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1641 | 0.97784 | -3.5555 | -5.6744 | 8.9155 | 9.3125 | 1.7804 | -0.28146 | 2.934% | -2.934%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2455 | 0.97638 | -3.6824 | -5.6745 | 9.8418 | 9.593 | 1.8336 | -0.28999 | 2.934% | -2.934%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2786 | 0.97579 | -3.7339 | -5.6746 | 10.3786 | 9.7066 | 1.8551 | -0.29344 | 2.934% | -2.934%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.269 | 0.97596 | -3.7189 | -5.6746 | 10.5155 | 9.6736 | 1.8489 | -0.29244 | 2.934% | -2.934%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2382 | 0.97651 | -3.6709 | -5.6745 | 10.526 | 9.5678 | 1.8288 | -0.28922 | 2.934% | -2.934%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.1714 | 0.97771 | -3.5669 | -5.6744 | 10.526 | 9.3378 | 1.7852 | -0.28223 | 2.934% | -2.934%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8783 | 0.9702 | -3.2146 | -7.4862 | 10.526 | 8.7828 | 1.6446 | -0.35622 | 3.898% | -3.898%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7127 | 0.97311 | -2.9563 | -7.4851 | 10.526 | 8.214 | 1.539 | -0.33304 | 3.897% | -3.897%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5734 | 0.97554 | -2.7395 | -7.4845 | 10.526 | 7.7335 | 1.4498 | -0.31348 | 3.896% | -3.896%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4815 | 0.97714 | -2.5966 | -7.484 | 10.526 | 7.4155 | 1.3906 | -0.30053 | 3.895% | -3.895%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99024 | -1.4264 | 0.97809 | -2.511 | -7.4837 | 10.526 | 7.2242 | 1.355 | -0.29275 | 3.895% | -3.895%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3959 | 0.97861 | -2.4637 | -7.4836 | 10.526 | 7.1185 | 1.3353 | -0.28845 | 3.894% | -3.894%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3934 | 0.97865 | -2.4599 | -7.4836 | 10.526 | 7.1099 | 1.3337 | -0.2881 | 3.894% | -3.894%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4391 | 0.97787 | -2.5308 | -7.4839 | 10.526 | 7.2685 | 1.3632 | -0.29455 | 3.895% | -3.895%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5564 | 0.97584 | -2.7131 | -7.4846 | 10.526 | 7.6749 | 1.4389 | -0.31109 | 3.895% | -3.895%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7347 | 0.97273 | -2.9907 | -7.4854 | 10.526 | 8.2899 | 1.5531 | -0.33613 | 3.897% | -3.897%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.8559 | 0.9706 | -3.1796 | -7.4858 | 10.5155 | 8.7059 | 1.6303 | -0.35309 | 3.898% | -3.898%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99501 | -2.048 | 0.9799 | -3.3749 | -5.6736 | 10.4102 | 8.9117 | 1.7043 | -0.26929 | 2.933% | -2.933%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99485 | -2.0617 | 0.97965 | -3.3962 | -5.6741 | 10.1892 | 8.9593 | 1.7134 | -0.27073 | 2.933% | -2.933%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0704 | 0.9795 | -3.4098 | -5.6741 | 9.9576 | 8.9894 | 1.7191 | -0.27164 | 2.933% | -2.933%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.0791 | 0.97935 | -3.4233 | -5.6741 | 9.8313 | 9.0194 | 1.7248 | -0.27256 | 2.933% | -2.933%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0875 | 0.9792 | -3.4364 | -5.6742 | 9.9681 | 9.0486 | 1.7303 | -0.27344 | 2.933% | -2.933%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.092 | 0.97912 | -3.4434 | -5.6742 | 10.0313 | 9.0641 | 1.7333 | -0.27391 | 2.933% | -2.933%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1106 | 0.97879 | -3.4723 | -5.6742 | 10.2944 | 9.1281 | 1.7454 | -0.27586 | 2.933% | -2.933%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1641 | 0.97784 | -3.5555 | -5.6744 | 10.4734 | 9.3125 | 1.7804 | -0.28146 | 2.934% | -2.934%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2455 | 0.97638 | -3.6824 | -5.6745 | 10.526 | 9.593 | 1.8336 | -0.28999 | 2.934% | -2.934%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2786 | 0.97579 | -3.7339 | -5.6746 | 10.526 | 9.7066 | 1.8551 | -0.29344 | 2.934% | -2.934%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.269 | 0.97596 | -3.7189 | -5.6746 | 10.526 | 9.6736 | 1.8489 | -0.29244 | 2.934% | -2.934%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2382 | 0.97651 | -3.6709 | -5.6745 | 10.526 | 9.5678 | 1.8288 | -0.28922 | 2.934% | -2.934%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.1714 | 0.97771 | -3.5669 | -5.6744 | 10.526 | 9.3378 | 1.7852 | -0.28223 | 2.934% | -2.934%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8783 | 0.9702 | -3.2146 | -7.4862 | 10.526 | 8.7828 | 1.6446 | -0.35622 | 3.898% | -3.898%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7127 | 0.97311 | -2.9563 | -7.4851 | 10.526 | 8.214 | 1.539 | -0.33304 | 3.897% | -3.897%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5734 | 0.97554 | -2.7395 | -7.4845 | 10.526 | 7.7335 | 1.4498 | -0.31348 | 3.896% | -3.896%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4815 | 0.97714 | -2.5966 | -7.484 | 10.526 | 7.4155 | 1.3906 | -0.30053 | 3.895% | -3.895%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99024 | -1.4264 | 0.97809 | -2.511 | -7.4837 | 10.526 | 7.2242 | 1.355 | -0.29275 | 3.895% | -3.895%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3959 | 0.97861 | -2.4637 | -7.4836 | 10.526 | 7.1185 | 1.3353 | -0.28845 | 3.894% | -3.894%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3934 | 0.97865 | -2.4599 | -7.4836 | 10.526 | 7.1099 | 1.3337 | -0.2881 | 3.894% | -3.894%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4391 | 0.97787 | -2.5308 | -7.4839 | 10.526 | 7.2685 | 1.3632 | -0.29455 | 3.895% | -3.895%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5564 | 0.97584 | -2.7131 | -7.4846 | 10.526 | 7.6749 | 1.4389 | -0.31109 | 3.895% | -3.895%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7347 | 0.97273 | -2.9907 | -7.4854 | 10.526 | 8.2899 | 1.5531 | -0.33613 | 3.897% | -3.897%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.8559 | 0.9706 | -3.1796 | -7.4858 | 10.526 | 8.7059 | 1.6303 | -0.35309 | 3.898% | -3.898%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99501 | -2.048 | 0.9799 | -3.3749 | -5.6736 | 10.526 | 8.9117 | 1.7043 | -0.26929 | 2.933% | -2.933%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99485 | -2.0617 | 0.97965 | -3.3962 | -5.6741 | 10.5155 | 8.9593 | 1.7134 | -0.27073 | 2.933% | -2.933%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0704 | 0.9795 | -3.4098 | -5.6741 | 10.4839 | 8.9894 | 1.7191 | -0.27164 | 2.933% | -2.933%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.0791 | 0.97935 | -3.4233 | -5.6741 | 10.4523 | 9.0194 | 1.7248 | -0.27256 | 2.933% | -2.933%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0875 | 0.9792 | -3.4364 | -5.6742 | 10.4523 | 9.0486 | 1.7303 | -0.27344 | 2.933% | -2.933%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.092 | 0.97912 | -3.4434 | -5.6742 | 10.4734 | 9.0641 | 1.7333 | -0.27391 | 2.933% | -2.933%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1106 | 0.97879 | -3.4723 | -5.6742 | 10.5049 | 9.1281 | 1.7454 | -0.27586 | 2.933% | -2.933%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1641 | 0.97784 | -3.5555 | -5.6744 | 10.5155 | 9.3125 | 1.7804 | -0.28146 | 2.934% | -2.934%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2455 | 0.97638 | -3.6824 | -5.6745 | 10.526 | 9.593 | 1.8336 | -0.28999 | 2.934% | -2.934%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2786 | 0.97579 | -3.7339 | -5.6746 | 10.526 | 9.7066 | 1.8551 | -0.29344 | 2.934% | -2.934%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.269 | 0.97596 | -3.7189 | -5.6746 | 10.526 | 9.6736 | 1.8489 | -0.29244 | 2.934% | -2.934%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2382 | 0.97651 | -3.6709 | -5.6745 | 10.526 | 9.5678 | 1.8288 | -0.28922 | 2.934% | -2.934%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.1714 | 0.97771 | -3.5669 | -5.6744 | 10.526 | 9.3378 | 1.7852 | -0.28223 | 2.934% | -2.934%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8783 | 0.9702 | -3.2146 | -7.4862 | 10.526 | 8.7828 | 1.6446 | -0.35622 | 3.898% | -3.898%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7127 | 0.97311 | -2.9563 | -7.4851 | 10.526 | 8.214 | 1.539 | -0.33304 | 3.897% | -3.897%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5734 | 0.97554 | -2.7395 | -7.4845 | 10.526 | 7.7335 | 1.4498 | -0.31348 | 3.896% | -3.896%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0168 | -3.1788 | 1.0168 | -3.1788 | 0.97451 | -2.4059 | 0.97451 | -2.4059 | -5.263 | 5.263 | 7.3958 | 1.3792 | -0.32016 | 4.149% | -4.149%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97548 | -2.321 | 0.97548 | -2.321 | -5.263 | 5.263 | 7.2053 | 1.344 | -0.31174 | 4.147% | -4.147%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97601 | -2.2741 | 0.97601 | -2.2741 | -5.263 | 5.263 | 7.0999 | 1.3245 | -0.30708 | 4.146% | -4.146%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97606 | -2.2703 | 0.97606 | -2.2703 | -5.263 | 5.263 | 7.0913 | 1.3229 | -0.3067 | 4.146% | -4.146%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97525 | -2.3406 | 0.97525 | -2.3406 | -5.263 | 5.263 | 7.2493 | 1.3521 | -0.31369 | 4.148% | -4.148%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97318 | -2.5216 | 0.97318 | -2.5216 | -5.263 | 5.263 | 7.6544 | 1.4269 | -0.3316 | 4.152% | -4.152%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2525 | 5.2525 | 8.2671 | 1.5398 | -0.35892 | 4.161% | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 5.1156 | 8.7007 | 1.6272 | -0.35834 | 3.956% | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97199 | -3.1176 | 0.97199 | -3.1176 | -4.7051 | 4.7051 | 8.841 | 1.6626 | -0.34005 | 3.704% | -3.704%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.142 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97651 | -3.2173 | 0.97651 | -3.2173 | -4.142 | 4.142 | 8.9309 | 1.6966 | -0.29912 | 3.241% | -3.241%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.98115 | -3.3097 | 0.98115 | -3.3097 | -3.5736 | 3.5736 | 9.0043 | 1.7279 | -0.25669 | 2.772% | -2.772%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.98366 | -3.367 | 0.98366 | -3.367 | -3.2578 | 3.2578 | 9.0587 | 1.748 | -0.23332 | 2.511% | -2.511%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 5 | 1.0089 | -3.8658 | 1.0089 | -3.8658 | 0.9827 | -3.3669 | 0.9827 | -3.3669 | -3.3525 | 3.3525 | 9.0806 | 1.7493 | -0.24144 | 2.59% | -2.59%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 5 | 1.0088 | -3.8727 | 1.0088 | -3.8727 | 0.98133 | -3.3527 | 0.98133 | -3.3527 | -3.5052 | 3.5052 | 9.0843 | 1.7452 | -0.25367 | 2.716% | -2.716%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.942 | 5 | 1.0085 | -3.9012 | 1.0085 | -3.9012 | 0.97731 | -3.3209 | 0.97731 | -3.3209 | -3.942 | 3.942 | 9.1145 | 1.7374 | -0.28947 | 3.078% | -3.078%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97199 | -3.3328 | 0.97199 | -3.3328 | -4.4578 | 4.4578 | 9.2578 | 1.748 | -0.33623 | 3.505% | -3.505%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 4.9209 | 9.5314 | 1.797 | -0.35157 | 3.557% | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 5.1893 | 9.65 | 1.8215 | -0.35 | 3.5% | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 5.2577 | 9.6155 | 1.8144 | -0.35047 | 3.517% | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 5.263 | 9.5051 | 1.7916 | -0.3519 | 3.57% | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 5.263 | 9.2655 | 1.7424 | -0.35454 | 3.685% | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 5.263 | 8.781 | 1.6435 | -0.358 | 3.917% | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.263 | 5.263 | 8.1882 | 1.5239 | -0.35882 | 4.198% | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97288 | -2.5478 | 0.97288 | -2.5478 | -5.263 | 5.263 | 7.7128 | 1.4377 | -0.33419 | 4.153% | -4.153%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97451 | -2.4059 | 0.97451 | -2.4059 | -5.263 | 5.263 | 7.3958 | 1.3792 | -0.32017 | 4.149% | -4.149%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97548 | -2.321 | 0.97548 | -2.321 | -5.263 | 5.263 | 7.2053 | 1.344 | -0.31174 | 4.147% | -4.147%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97601 | -2.2741 | 0.97601 | -2.2741 | -5.263 | 5.263 | 7.0999 | 1.3245 | -0.30708 | 4.146% | -4.146%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97606 | -2.2703 | 0.97606 | -2.2703 | -5.263 | 5.263 | 7.0913 | 1.3229 | -0.3067 | 4.146% | -4.146%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97525 | -2.3406 | 0.97525 | -2.3406 | -5.263 | 5.263 | 7.2493 | 1.3521 | -0.31369 | 4.148% | -4.148%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97318 | -2.5216 | 0.97318 | -2.5216 | -5.263 | 5.263 | 7.6544 | 1.4269 | -0.3316 | 4.152% | -4.152%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.263 | 5.263 | 8.2671 | 1.5398 | -0.35892 | 4.161% | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 5.2577 | 8.7007 | 1.6272 | -0.35834 | 3.956% | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 5.2051 | 8.8232 | 1.6521 | -0.35781 | 3.897% | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 5.0946 | 8.8725 | 1.6621 | -0.35755 | 3.874% | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 4.9788 | 8.9036 | 1.6685 | -0.35737 | 3.859% | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 4.9156 | 8.9348 | 1.6748 | -0.35718 | 3.844% | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 4.9841 | 8.965 | 1.681 | -0.35699 | 3.83% | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 5.0156 | 8.9811 | 1.6842 | -0.35688 | 3.822% | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 5.1472 | 9.0476 | 1.6978 | -0.35641 | 3.79% | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 5.2367 | 9.2392 | 1.737 | -0.3548 | 3.698% | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 5.263 | 9.5314 | 1.797 | -0.35157 | 3.557% | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 5.263 | 9.65 | 1.8215 | -0.35 | 3.5% | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 5.263 | 9.6155 | 1.8144 | -0.35047 | 3.517% | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 5.263 | 9.5051 | 1.7916 | -0.3519 | 3.57% | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 5.263 | 9.2655 | 1.7424 | -0.35454 | 3.685% | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 5.263 | 8.781 | 1.6435 | -0.358 | 3.917% | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.263 | 5.263 | 8.1882 | 1.5239 | -0.35882 | 4.198% | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97288 | -2.5478 | 0.97288 | -2.5478 | -5.263 | 5.263 | 7.7128 | 1.4377 | -0.33419 | 4.153% | -4.153%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97451 | -2.4059 | 0.97451 | -2.4059 | -5.263 | 5.263 | 7.3958 | 1.3792 | -0.32017 | 4.149% | -4.149%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97548 | -2.321 | 0.97548 | -2.321 | -5.263 | 5.263 | 7.2053 | 1.344 | -0.31174 | 4.147% | -4.147%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97601 | -2.2741 | 0.97601 | -2.2741 | -5.263 | 5.263 | 7.0999 | 1.3245 | -0.30708 | 4.146% | -4.146%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97606 | -2.2703 | 0.97606 | -2.2703 | -5.263 | 5.263 | 7.0913 | 1.3229 | -0.3067 | 4.146% | -4.146%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97525 | -2.3406 | 0.97525 | -2.3406 | -5.263 | 5.263 | 7.2493 | 1.3521 | -0.31369 | 4.148% | -4.148%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97318 | -2.5216 | 0.97318 | -2.5216 | -5.263 | 5.263 | 7.6544 | 1.4269 | -0.3316 | 4.152% | -4.152%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.263 | 5.263 | 8.2671 | 1.5398 | -0.35892 | 4.161% | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 5.263 | 8.7007 | 1.6272 | -0.35834 | 3.956% | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 5.263 | 8.8232 | 1.6521 | -0.35781 | 3.897% | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 5.2577 | 8.8725 | 1.6621 | -0.35755 | 3.874% | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 5.2419 | 8.9036 | 1.6685 | -0.35737 | 3.859% | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 5.2262 | 8.9348 | 1.6748 | -0.35718 | 3.844% | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 5.2262 | 8.965 | 1.681 | -0.35699 | 3.83% | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 5.2367 | 8.9811 | 1.6842 | -0.35688 | 3.822% | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 5.2525 | 9.0476 | 1.6978 | -0.35641 | 3.79% | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 5.2577 | 9.2392 | 1.737 | -0.3548 | 3.698% | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 5.263 | 9.5314 | 1.797 | -0.35157 | 3.557% | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 5.263 | 9.65 | 1.8215 | -0.35 | 3.5% | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 5.263 | 9.6155 | 1.8144 | -0.35047 | 3.517% | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 5.263 | 9.5051 | 1.7916 | -0.3519 | 3.57% | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 5.263 | 9.2655 | 1.7424 | -0.35454 | 3.685% | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 5.263 | 8.781 | 1.6435 | -0.358 | 3.917% | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.263 | 5.263 | 8.1882 | 1.5239 | -0.35882 | 4.198% | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97288 | -2.5478 | 0.97288 | -2.5478 | -5.263 | 5.263 | 7.7128 | 1.4377 | -0.33419 | 4.153% | -4.153%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.331 | 0.97 | -2.331 | -5.7876 | 10.526 | 7.3623 | 1.3597 | -0.35373 | 4.584% | -4.584%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2297 | 0.97 | -2.2297 | -5.8994 | 10.526 | 7.1655 | 1.3209 | -0.35147 | 4.676% | -4.676%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1739 | 0.97 | -2.1739 | -5.9608 | 10.526 | 7.057 | 1.2996 | -0.35004 | 4.726% | -4.726%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1693 | 0.97 | -2.1693 | -5.9658 | 10.526 | 7.0481 | 1.2979 | -0.34992 | 4.73% | -4.73%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2531 | 0.97 | -2.2531 | -5.8736 | 10.526 | 7.211 | 1.3299 | -0.35203 | 4.655% | -4.655%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4688 | 0.97 | -2.4688 | -5.6347 | 10.526 | 7.6298 | 1.4126 | -0.35618 | 4.46% | -4.46%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2666 | 10.5049 | 8.2671 | 1.5398 | -0.35894 | 4.161% | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 10.2313 | 8.7007 | 1.6272 | -0.35834 | 3.956% | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 9.4102 | 8.8232 | 1.6521 | -0.35781 | 3.897% | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.284 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 8.284 | 8.8725 | 1.6621 | -0.35755 | 3.874% | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 7.1472 | 8.9036 | 1.6685 | -0.35737 | 3.859% | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 6.5156 | 8.9348 | 1.6748 | -0.35718 | 3.844% | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 6.7051 | 8.965 | 1.681 | -0.35699 | 3.83% | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 7.0103 | 8.9811 | 1.6842 | -0.35688 | 3.822% | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.884 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 7.884 | 9.0476 | 1.6978 | -0.35641 | 3.79% | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 8.9155 | 9.2392 | 1.737 | -0.3548 | 3.698% | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 9.8418 | 9.5314 | 1.797 | -0.35157 | 3.557% | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 10.3786 | 9.65 | 1.8215 | -0.35 | 3.5% | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 10.5155 | 9.6155 | 1.8144 | -0.35047 | 3.517% | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 10.526 | 9.5051 | 1.7916 | -0.3519 | 3.57% | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 10.526 | 9.2655 | 1.7424 | -0.35454 | 3.685% | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 10.526 | 8.781 | 1.6435 | -0.358 | 3.917% | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.3125 | 10.526 | 8.1882 | 1.5239 | -0.35882 | 4.198% | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.5 | 0.97 | -2.5 | -5.6 | 10.526 | 7.6904 | 1.4246 | -0.35662 | 4.432% | -4.432%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.331 | 0.97 | -2.331 | -5.7876 | 10.526 | 7.3623 | 1.3597 | -0.35374 | 4.584% | -4.584%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2297 | 0.97 | -2.2297 | -5.8994 | 10.526 | 7.1655 | 1.3209 | -0.35147 | 4.676% | -4.676%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1739 | 0.97 | -2.1739 | -5.9608 | 10.526 | 7.057 | 1.2996 | -0.35004 | 4.726% | -4.726%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1693 | 0.97 | -2.1693 | -5.9658 | 10.526 | 7.0481 | 1.2979 | -0.34992 | 4.73% | -4.73%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2531 | 0.97 | -2.2531 | -5.8736 | 10.526 | 7.211 | 1.3299 | -0.35203 | 4.655% | -4.655%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4688 | 0.97 | -2.4688 | -5.6347 | 10.526 | 7.6298 | 1.4126 | -0.35618 | 4.46% | -4.46%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2666 | 10.526 | 8.2671 | 1.5398 | -0.35894 | 4.161% | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 10.5155 | 8.7007 | 1.6272 | -0.35834 | 3.956% | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 10.4102 | 8.8232 | 1.6521 | -0.35781 | 3.897% | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 10.1892 | 8.8725 | 1.6621 | -0.35755 | 3.874% | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 9.9576 | 8.9036 | 1.6685 | -0.35737 | 3.859% | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 9.8313 | 8.9348 | 1.6748 | -0.35718 | 3.844% | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 9.9681 | 8.965 | 1.681 | -0.35699 | 3.83% | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 10.0313 | 8.9811 | 1.6842 | -0.35688 | 3.822% | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 10.2944 | 9.0476 | 1.6978 | -0.35641 | 3.79% | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 10.4734 | 9.2392 | 1.737 | -0.3548 | 3.698% | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 10.526 | 9.5314 | 1.797 | -0.35157 | 3.557% | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 10.526 | 9.65 | 1.8215 | -0.35 | 3.5% | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 10.526 | 9.6155 | 1.8144 | -0.35047 | 3.517% | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 10.526 | 9.5051 | 1.7916 | -0.3519 | 3.57% | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 10.526 | 9.2655 | 1.7424 | -0.35454 | 3.685% | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 10.526 | 8.781 | 1.6435 | -0.358 | 3.917% | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.3125 | 10.526 | 8.1882 | 1.5239 | -0.35882 | 4.198% | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.5 | 0.97 | -2.5 | -5.6 | 10.526 | 7.6904 | 1.4246 | -0.35662 | 4.432% | -4.432%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.331 | 0.97 | -2.331 | -5.7876 | 10.526 | 7.3623 | 1.3597 | -0.35374 | 4.584% | -4.584%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2297 | 0.97 | -2.2297 | -5.8994 | 10.526 | 7.1655 | 1.3209 | -0.35147 | 4.676% | -4.676%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1739 | 0.97 | -2.1739 | -5.9608 | 10.526 | 7.057 | 1.2996 | -0.35004 | 4.726% | -4.726%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1693 | 0.97 | -2.1693 | -5.9658 | 10.526 | 7.0481 | 1.2979 | -0.34992 | 4.73% | -4.73%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2531 | 0.97 | -2.2531 | -5.8736 | 10.526 | 7.211 | 1.3299 | -0.35203 | 4.655% | -4.655%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4688 | 0.97 | -2.4688 | -5.6347 | 10.526 | 7.6298 | 1.4126 | -0.35618 | 4.46% | -4.46%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2666 | 10.526 | 8.2671 | 1.5398 | -0.35894 | 4.161% | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 10.526 | 8.7007 | 1.6272 | -0.35834 | 3.956% | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 10.526 | 8.8232 | 1.6521 | -0.35781 | 3.897% | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 10.5155 | 8.8725 | 1.6621 | -0.35755 | 3.874% | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 10.4839 | 8.9036 | 1.6685 | -0.35737 | 3.859% | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 10.4523 | 8.9348 | 1.6748 | -0.35718 | 3.844% | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 10.4523 | 8.965 | 1.681 | -0.35699 | 3.83% | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 10.4734 | 8.9811 | 1.6842 | -0.35688 | 3.822% | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 10.5049 | 9.0476 | 1.6978 | -0.35641 | 3.79% | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 10.5155 | 9.2392 | 1.737 | -0.3548 | 3.698% | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 10.526 | 9.5314 | 1.797 | -0.35157 | 3.557% | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 10.526 | 9.65 | 1.8215 | -0.35 | 3.5% | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 10.526 | 9.6155 | 1.8144 | -0.35047 | 3.517% | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 10.526 | 9.5051 | 1.7916 | -0.3519 | 3.57% | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 10.526 | 9.2655 | 1.7424 | -0.35454 | 3.685% | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 10.526 | 8.781 | 1.6435 | -0.358 | 3.917% | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.3125 | 10.526 | 8.1882 | 1.5239 | -0.35882 | 4.198% | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.5 | 0.97 | -2.5 | -5.6 | 10.526 | 7.6904 | 1.4246 | -0.35662 | 4.432% | -4.432%

## ConstantZLoad(Consolidated data
Input Parameters | [8 empty] | NO CVR Voltages and Angles |  |  |  | WITH CVR Voltages and Angles |  |  |  | WITH CVR Q output and load |  |  |  | WITH VS WITHOUT CVR
hour | load |  | PF | load type | sun rating | PV_size | Q limit | PV bus # | PV bus V | % | Load bus (5) V | Load bus (5) angle | PV bus V pu | PV bus angle | Load bus (5) pu | Load bus (5) angle | PV bus Q output | PV bus Q limit | load |  | Reduction in P
hour | MW | MVAR | PF | load type | sun rating | MVA | MVAR | hour | PF | degrees | pu | degrees | pu | degrees | pu | degrees | MVAR | MVAR | MW | MVAR | MW reductoin | %
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.92 | 1.023 | -0.894 | 0.986 | -2.781 | -5.263 | 5.263 | 7.517 | 3.641 | -0.199 | 2.582%
2 | 7.517 | 3.641 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.868 | 0.987 | -2.703 | -5.263 | 5.263 | 7.323 | 3.547 | -0.194 | 2.579%
3 | 7.407 | 3.587 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.853 | 0.988 | -2.659 | -5.263 | 5.263 | 7.216 | 3.495 | -0.191 | 2.579%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.852 | 0.988 | -2.656 | -5.263 | 5.263 | 7.207 | 3.491 | -0.191 | 2.579%
5 | 7.563 | 3.663 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.874 | 0.987 | -2.721 | -5.263 | 5.263 | 7.368 | 3.568 | -0.195 | 2.579%
6 | 7.986 | 3.868 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.93 | 0.984 | -2.888 | -5.263 | 5.263 | 7.78 | 3.768 | -0.206 | 2.581%
7 | 8.626 | 4.178 | 0.9 | Z | very sunny | 5.263 | 5.252 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.022 | -1.016 | 0.979 | -3.143 | -5.252 | 5.252 | 8.404 | 4.07 | -0.222 | 2.578%
8 | 9.059 | 4.387 | 0.9 | Z | very sunny | 5.263 | 5.116 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.11 | 0.979 | -3.353 | -3.912 | 5.116 | 8.885 | 4.303 | -0.174 | 1.925%
9 | 9.181 | 4.447 | 0.9 | Z | very sunny | 5.263 | 4.705 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.126 | 0.978 | -3.403 | -3.913 | 4.705 | 9.004 | 4.361 | -0.177 | 1.925%
10 | 9.23 | 4.47 | 0.9 | Z | very sunny | 5.263 | 4.142 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.133 | 0.978 | -3.423 | -3.913 | 4.142 | 9.052 | 4.384 | -0.178 | 1.925%
11 | 9.261 | 4.485 | 0.9 | Z | very sunny | 5.263 | 3.574 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.025 | -1.146 | 0.978 | -3.444 | -3.574 | 3.574 | 9.098 | 4.406 | -0.163 | 1.758%
12 | 9.292 | 4.5 | 0.9 | Z | very sunny | 5.263 | 3.258 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.025 | -1.159 | 0.979 | -3.465 | -3.258 | 3.258 | 9.143 | 4.428 | -0.149 | 1.601%
13 | 9.322 | 4.515 | 0.9 | Z | very sunny | 5.263 | 3.353 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.025 | -1.16 | 0.979 | -3.475 | -3.353 | 3.353 | 9.168 | 4.44 | -0.154 | 1.648%
14 | 9.338 | 4.523 | 0.9 | Z | very sunny | 5.263 | 3.505 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.025 | -1.158 | 0.978 | -3.477 | -3.505 | 3.505 | 9.177 | 4.445 | -0.161 | 1.724%
15 | 9.404 | 4.555 | 0.9 | Z | very sunny | 5.263 | 3.942 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.156 | 0.977 | -3.493 | -3.913 | 3.942 | 9.223 | 4.467 | -0.181 | 1.926%
16 | 9.594 | 4.647 | 0.9 | Z | very sunny | 5.263 | 4.458 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.182 | 0.975 | -3.571 | -3.913 | 4.458 | 9.409 | 4.557 | -0.185 | 1.927%
17 | 9.883 | 4.787 | 0.9 | Z | very sunny | 5.263 | 4.921 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.221 | 0.973 | -3.689 | -3.914 | 4.921 | 9.692 | 4.694 | -0.191 | 1.928%
18 | 10 | 4.843 | 0.9 | Z | very sunny | 5.263 | 5.189 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.237 | 0.972 | -3.737 | -3.914 | 5.189 | 9.807 | 4.75 | -0.193 | 1.929%
19 | 9.966 | 4.827 | 0.9 | Z | very sunny | 5.263 | 5.258 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.232 | 0.972 | -3.723 | -3.914 | 5.258 | 9.774 | 4.734 | -0.192 | 1.928%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.218 | 0.973 | -3.678 | -3.914 | 5.263 | 9.667 | 4.682 | -0.19 | 1.928%
21 | 9.62 | 4.659 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.185 | 0.975 | -3.581 | -3.913 | 5.263 | 9.435 | 4.569 | -0.185 | 1.927%
22 | 9.139 | 4.426 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.12 | 0.979 | -3.386 | -3.913 | 5.263 | 8.963 | 4.341 | -0.176 | 1.925%
23 | 8.547 | 4.14 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.005 | 0.98 | -3.111 | -5.263 | 5.263 | 8.326 | 4.033 | -0.221 | 2.583%
24 | 8.047 | 3.897 | 0.9 | Z | very sunny | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.938 | 0.983 | -2.912 | -5.263 | 5.263 | 7.839 | 3.797 | -0.208 | 2.581%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.023 | -0.894 | 0.986 | -2.781 | -5.263 | 5.263 | 7.517 | 3.641 | -0.199 | 2.58%
2 | 7.517 | 3.641 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.868 | 0.987 | -2.703 | -5.263 | 5.263 | 7.323 | 3.547 | -0.194 | 2.579%
3 | 7.407 | 3.587 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.853 | 0.988 | -2.659 | -5.263 | 5.263 | 7.216 | 3.495 | -0.191 | 2.579%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.852 | 0.988 | -2.656 | -5.263 | 5.263 | 7.207 | 3.491 | -0.191 | 2.579%
5 | 7.563 | 3.663 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.874 | 0.987 | -2.721 | -5.263 | 5.263 | 7.368 | 3.568 | -0.195 | 2.579%
6 | 7.986 | 3.868 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.93 | 0.984 | -2.888 | -5.263 | 5.263 | 7.78 | 3.768 | -0.206 | 2.581%
7 | 8.626 | 4.178 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.022 | -1.015 | 0.979 | -3.143 | -5.263 | 5.263 | 8.403 | 4.07 | -0.223 | 2.584%
8 | 9.059 | 4.387 | 0.9 | Z | moderate sun | 5.263 | 5.258 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.11 | 0.979 | -3.353 | -3.912 | 5.258 | 8.885 | 4.303 | -0.174 | 1.925%
9 | 9.181 | 4.447 | 0.9 | Z | moderate sun | 5.263 | 5.205 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.126 | 0.978 | -3.403 | -3.913 | 5.205 | 9.004 | 4.361 | -0.177 | 1.925%
10 | 9.23 | 4.47 | 0.9 | Z | moderate sun | 5.263 | 5.095 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.133 | 0.978 | -3.423 | -3.913 | 5.095 | 9.052 | 4.384 | -0.178 | 1.925%
11 | 9.261 | 4.485 | 0.9 | Z | moderate sun | 5.263 | 4.979 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.137 | 0.978 | -3.435 | -3.913 | 4.979 | 9.083 | 4.399 | -0.178 | 1.926%
12 | 9.292 | 4.5 | 0.9 | Z | moderate sun | 5.263 | 4.916 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.141 | 0.977 | -3.448 | -3.913 | 4.916 | 9.113 | 4.414 | -0.179 | 1.926%
13 | 9.322 | 4.515 | 0.9 | Z | moderate sun | 5.263 | 4.984 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.145 | 0.977 | -3.46 | -3.913 | 4.984 | 9.142 | 4.428 | -0.18 | 1.926%
14 | 9.338 | 4.523 | 0.9 | Z | moderate sun | 5.263 | 5.016 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.147 | 0.977 | -3.466 | -3.913 | 5.016 | 9.158 | 4.436 | -0.18 | 1.926%
15 | 9.404 | 4.555 | 0.9 | Z | moderate sun | 5.263 | 5.147 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.156 | 0.977 | -3.493 | -3.913 | 5.147 | 9.223 | 4.467 | -0.181 | 1.926%
16 | 9.594 | 4.647 | 0.9 | Z | moderate sun | 5.263 | 5.237 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.182 | 0.975 | -3.571 | -3.913 | 5.237 | 9.409 | 4.557 | -0.185 | 1.927%
17 | 9.883 | 4.787 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.221 | 0.973 | -3.689 | -3.914 | 5.263 | 9.692 | 4.694 | -0.191 | 1.928%
18 | 10 | 4.843 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.237 | 0.972 | -3.737 | -3.914 | 5.263 | 9.807 | 4.75 | -0.193 | 1.929%
19 | 9.966 | 4.827 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.232 | 0.972 | -3.723 | -3.914 | 5.263 | 9.774 | 4.734 | -0.192 | 1.928%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.218 | 0.973 | -3.678 | -3.914 | 5.263 | 9.667 | 4.682 | -0.19 | 1.928%
21 | 9.62 | 4.659 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.185 | 0.975 | -3.581 | -3.913 | 5.263 | 9.435 | 4.569 | -0.185 | 1.927%
22 | 9.139 | 4.426 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.12 | 0.979 | -3.386 | -3.913 | 5.263 | 8.963 | 4.341 | -0.176 | 1.925%
23 | 8.547 | 4.14 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.005 | 0.98 | -3.111 | -5.263 | 5.263 | 8.326 | 4.033 | -0.221 | 2.583%
24 | 8.047 | 3.897 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.938 | 0.983 | -2.912 | -5.263 | 5.263 | 7.839 | 3.797 | -0.208 | 2.581%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.023 | -0.894 | 0.986 | -2.781 | -5.263 | 5.263 | 7.517 | 3.641 | -0.199 | 2.58%
2 | 7.517 | 3.641 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.868 | 0.987 | -2.703 | -5.263 | 5.263 | 7.323 | 3.547 | -0.194 | 2.579%
3 | 7.407 | 3.587 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.853 | 0.988 | -2.659 | -5.263 | 5.263 | 7.216 | 3.495 | -0.191 | 2.579%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.852 | 0.988 | -2.656 | -5.263 | 5.263 | 7.207 | 3.491 | -0.191 | 2.579%
5 | 7.563 | 3.663 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.874 | 0.987 | -2.721 | -5.263 | 5.263 | 7.368 | 3.568 | -0.195 | 2.579%
6 | 7.986 | 3.868 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.93 | 0.984 | -2.888 | -5.263 | 5.263 | 7.78 | 3.768 | -0.206 | 2.581%
7 | 8.626 | 4.178 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.022 | -1.015 | 0.979 | -3.143 | -5.263 | 5.263 | 8.403 | 4.07 | -0.223 | 2.584%
8 | 9.059 | 4.387 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.11 | 0.979 | -3.353 | -3.912 | 5.263 | 8.885 | 4.303 | -0.174 | 1.925%
9 | 9.181 | 4.447 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.126 | 0.978 | -3.403 | -3.913 | 5.263 | 9.004 | 4.361 | -0.177 | 1.925%
10 | 9.23 | 4.47 | 0.9 | Z | cloudy | 5.263 | 5.258 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.133 | 0.978 | -3.423 | -3.913 | 5.258 | 9.052 | 4.384 | -0.178 | 1.925%
11 | 9.261 | 4.485 | 0.9 | Z | cloudy | 5.263 | 5.242 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.137 | 0.978 | -3.435 | -3.913 | 5.242 | 9.083 | 4.399 | -0.178 | 1.926%
12 | 9.292 | 4.5 | 0.9 | Z | cloudy | 5.263 | 5.226 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.141 | 0.977 | -3.448 | -3.913 | 5.226 | 9.113 | 4.414 | -0.179 | 1.926%
13 | 9.322 | 4.515 | 0.9 | Z | cloudy | 5.263 | 5.226 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.145 | 0.977 | -3.46 | -3.913 | 5.226 | 9.142 | 4.428 | -0.18 | 1.926%
14 | 9.338 | 4.523 | 0.9 | Z | cloudy | 5.263 | 5.237 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.147 | 0.977 | -3.466 | -3.913 | 5.237 | 9.158 | 4.436 | -0.18 | 1.926%
15 | 9.404 | 4.555 | 0.9 | Z | cloudy | 5.263 | 5.252 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.156 | 0.977 | -3.493 | -3.913 | 5.252 | 9.223 | 4.467 | -0.181 | 1.926%
16 | 9.594 | 4.647 | 0.9 | Z | cloudy | 5.263 | 5.258 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.182 | 0.975 | -3.571 | -3.913 | 5.258 | 9.409 | 4.557 | -0.185 | 1.927%
17 | 9.883 | 4.787 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.221 | 0.973 | -3.689 | -3.914 | 5.263 | 9.692 | 4.694 | -0.191 | 1.928%
18 | 10 | 4.843 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.237 | 0.972 | -3.737 | -3.914 | 5.263 | 9.807 | 4.75 | -0.193 | 1.929%
19 | 9.966 | 4.827 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.232 | 0.972 | -3.723 | -3.914 | 5.263 | 9.774 | 4.734 | -0.192 | 1.928%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.218 | 0.973 | -3.678 | -3.914 | 5.263 | 9.667 | 4.682 | -0.19 | 1.928%
21 | 9.62 | 4.659 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.185 | 0.975 | -3.581 | -3.913 | 5.263 | 9.435 | 4.569 | -0.185 | 1.927%
22 | 9.139 | 4.426 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.12 | 0.979 | -3.386 | -3.913 | 5.263 | 8.963 | 4.341 | -0.176 | 1.925%
23 | 8.547 | 4.14 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.005 | 0.98 | -3.111 | -5.263 | 5.263 | 8.326 | 4.033 | -0.221 | 2.583%
24 | 8.047 | 3.897 | 0.9 | Z | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.938 | 0.983 | -2.912 | -5.263 | 5.263 | 7.839 | 3.797 | -0.208 | 2.581%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.827 | 0.979 | -2.714 | -7.743 | 10.526 | 7.421 | 3.594 | -0.295 | 3.82%
2 | 7.517 | 3.641 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.725 | 0.974 | -2.56 | -10.526 | 10.526 | 7.125 | 3.451 | -0.392 | 5.21%
3 | 7.407 | 3.587 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.711 | 0.975 | -2.517 | -10.526 | 10.526 | 7.021 | 3.4 | -0.386 | 5.21%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.71 | 0.975 | -2.514 | -10.526 | 10.526 | 7.013 | 3.396 | -0.385 | 5.209%
5 | 7.563 | 3.663 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.01 | -0.731 | 0.973 | -2.578 | -10.526 | 10.526 | 7.169 | 3.472 | -0.394 | 5.211%
6 | 7.986 | 3.868 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.863 | 0.978 | -2.82 | -7.744 | 10.526 | 7.681 | 3.72 | -0.305 | 3.822%
7 | 8.626 | 4.178 | 0.9 | Z | very sunny | 10.526 | 10.505 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.947 | 0.973 | -3.075 | -7.746 | 10.505 | 8.296 | 4.018 | -0.33 | 3.827%
8 | 9.059 | 4.387 | 0.9 | Z | very sunny | 10.526 | 10.231 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.11 | 0.979 | -3.353 | -3.912 | 10.231 | 8.885 | 4.303 | -0.174 | 1.925%
9 | 9.181 | 4.447 | 0.9 | Z | very sunny | 10.526 | 9.41 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.126 | 0.978 | -3.403 | -3.913 | 9.41 | 9.004 | 4.361 | -0.177 | 1.925%
10 | 9.23 | 4.47 | 0.9 | Z | very sunny | 10.526 | 8.284 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.133 | 0.978 | -3.423 | -3.913 | 8.284 | 9.052 | 4.384 | -0.178 | 1.925%
11 | 9.261 | 4.485 | 0.9 | Z | very sunny | 10.526 | 7.147 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.137 | 0.978 | -3.435 | -3.913 | 7.147 | 9.083 | 4.399 | -0.178 | 1.926%
12 | 9.292 | 4.5 | 0.9 | Z | very sunny | 10.526 | 6.516 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.141 | 0.977 | -3.448 | -3.913 | 6.516 | 9.113 | 4.414 | -0.179 | 1.926%
13 | 9.322 | 4.515 | 0.9 | Z | very sunny | 10.526 | 6.705 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.145 | 0.977 | -3.46 | -3.913 | 6.705 | 9.142 | 4.428 | -0.18 | 1.926%
14 | 9.338 | 4.523 | 0.9 | Z | very sunny | 10.526 | 7.01 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.147 | 0.977 | -3.466 | -3.913 | 7.01 | 9.158 | 4.436 | -0.18 | 1.926%
15 | 9.404 | 4.555 | 0.9 | Z | very sunny | 10.526 | 7.884 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.156 | 0.977 | -3.493 | -3.913 | 7.884 | 9.223 | 4.467 | -0.181 | 1.926%
16 | 9.594 | 4.647 | 0.9 | Z | very sunny | 10.526 | 8.916 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.182 | 0.975 | -3.571 | -3.913 | 8.916 | 9.409 | 4.557 | -0.185 | 1.927%
17 | 9.883 | 4.787 | 0.9 | Z | very sunny | 10.526 | 9.842 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.221 | 0.973 | -3.689 | -3.914 | 9.842 | 9.692 | 4.694 | -0.191 | 1.928%
18 | 10 | 4.843 | 0.9 | Z | very sunny | 10.526 | 10.379 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.237 | 0.972 | -3.737 | -3.914 | 10.379 | 9.807 | 4.75 | -0.193 | 1.929%
19 | 9.966 | 4.827 | 0.9 | Z | very sunny | 10.526 | 10.515 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.232 | 0.972 | -3.723 | -3.914 | 10.515 | 9.774 | 4.734 | -0.192 | 1.928%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.218 | 0.973 | -3.678 | -3.914 | 10.526 | 9.667 | 4.682 | -0.19 | 1.928%
21 | 9.62 | 4.659 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.185 | 0.975 | -3.581 | -3.913 | 10.526 | 9.435 | 4.569 | -0.185 | 1.927%
22 | 9.139 | 4.426 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.12 | 0.979 | -3.386 | -3.913 | 10.526 | 8.963 | 4.341 | -0.176 | 1.925%
23 | 8.547 | 4.14 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.937 | 0.973 | -3.043 | -7.746 | 10.526 | 8.22 | 3.981 | -0.327 | 3.827%
24 | 8.047 | 3.897 | 0.9 | Z | very sunny | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.871 | 0.977 | -2.845 | -7.744 | 10.526 | 7.739 | 3.748 | -0.308 | 3.823%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.827 | 0.979 | -2.714 | -7.743 | 10.526 | 7.421 | 3.594 | -0.295 | 3.82%
2 | 7.517 | 3.641 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.725 | 0.974 | -2.56 | -10.526 | 10.526 | 7.125 | 3.451 | -0.392 | 5.21%
3 | 7.407 | 3.587 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.711 | 0.975 | -2.517 | -10.526 | 10.526 | 7.021 | 3.4 | -0.386 | 5.21%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.71 | 0.975 | -2.514 | -10.526 | 10.526 | 7.013 | 3.396 | -0.385 | 5.209%
5 | 7.563 | 3.663 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.01 | -0.731 | 0.973 | -2.578 | -10.526 | 10.526 | 7.169 | 3.472 | -0.394 | 5.211%
6 | 7.986 | 3.868 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.863 | 0.978 | -2.82 | -7.744 | 10.526 | 7.681 | 3.72 | -0.305 | 3.822%
7 | 8.626 | 4.178 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.947 | 0.973 | -3.075 | -7.746 | 10.526 | 8.296 | 4.018 | -0.33 | 3.827%
8 | 9.059 | 4.387 | 0.9 | Z | moderate sun | 10.526 | 10.515 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.11 | 0.979 | -3.353 | -3.912 | 10.515 | 8.885 | 4.303 | -0.174 | 1.925%
9 | 9.181 | 4.447 | 0.9 | Z | moderate sun | 10.526 | 10.41 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.126 | 0.978 | -3.403 | -3.913 | 10.41 | 9.004 | 4.361 | -0.177 | 1.925%
10 | 9.23 | 4.47 | 0.9 | Z | moderate sun | 10.526 | 10.189 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.133 | 0.978 | -3.423 | -3.913 | 10.189 | 9.052 | 4.384 | -0.178 | 1.925%
11 | 9.261 | 4.485 | 0.9 | Z | moderate sun | 10.526 | 9.958 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.137 | 0.978 | -3.435 | -3.913 | 9.958 | 9.083 | 4.399 | -0.178 | 1.926%
12 | 9.292 | 4.5 | 0.9 | Z | moderate sun | 10.526 | 9.831 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.141 | 0.977 | -3.448 | -3.913 | 9.831 | 9.113 | 4.414 | -0.179 | 1.926%
13 | 9.322 | 4.515 | 0.9 | Z | moderate sun | 10.526 | 9.968 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.145 | 0.977 | -3.46 | -3.913 | 9.968 | 9.142 | 4.428 | -0.18 | 1.926%
14 | 9.338 | 4.523 | 0.9 | Z | moderate sun | 10.526 | 10.031 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.147 | 0.977 | -3.466 | -3.913 | 10.031 | 9.158 | 4.436 | -0.18 | 1.926%
15 | 9.404 | 4.555 | 0.9 | Z | moderate sun | 10.526 | 10.294 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.156 | 0.977 | -3.493 | -3.913 | 10.294 | 9.223 | 4.467 | -0.181 | 1.926%
16 | 9.594 | 4.647 | 0.9 | Z | moderate sun | 10.526 | 10.473 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.182 | 0.975 | -3.571 | -3.913 | 10.473 | 9.409 | 4.557 | -0.185 | 1.927%
17 | 9.883 | 4.787 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.221 | 0.973 | -3.689 | -3.914 | 10.526 | 9.692 | 4.694 | -0.191 | 1.928%
18 | 10 | 4.843 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.237 | 0.972 | -3.737 | -3.914 | 10.526 | 9.807 | 4.75 | -0.193 | 1.929%
19 | 9.966 | 4.827 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.232 | 0.972 | -3.723 | -3.914 | 10.526 | 9.774 | 4.734 | -0.192 | 1.928%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.218 | 0.973 | -3.678 | -3.914 | 10.526 | 9.667 | 4.682 | -0.19 | 1.928%
21 | 9.62 | 4.659 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.185 | 0.975 | -3.581 | -3.913 | 10.526 | 9.435 | 4.569 | -0.185 | 1.927%
22 | 9.139 | 4.426 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.12 | 0.979 | -3.386 | -3.913 | 10.526 | 8.963 | 4.341 | -0.176 | 1.925%
23 | 8.547 | 4.14 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.937 | 0.973 | -3.043 | -7.746 | 10.526 | 8.22 | 3.981 | -0.327 | 3.827%
24 | 8.047 | 3.897 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.871 | 0.977 | -2.845 | -7.744 | 10.526 | 7.739 | 3.748 | -0.308 | 3.823%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.827 | 0.979 | -2.714 | -7.743 | 10.526 | 7.421 | 3.594 | -0.295 | 3.82%
2 | 7.517 | 3.641 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.725 | 0.974 | -2.56 | -10.526 | 10.526 | 7.125 | 3.451 | -0.392 | 5.21%
3 | 7.407 | 3.587 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.711 | 0.975 | -2.517 | -10.526 | 10.526 | 7.021 | 3.4 | -0.386 | 5.21%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.71 | 0.975 | -2.514 | -10.526 | 10.526 | 7.013 | 3.396 | -0.385 | 5.209%
5 | 7.563 | 3.663 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.01 | -0.731 | 0.973 | -2.578 | -10.526 | 10.526 | 7.169 | 3.472 | -0.394 | 5.211%
6 | 7.986 | 3.868 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.863 | 0.978 | -2.82 | -7.744 | 10.526 | 7.681 | 3.72 | -0.305 | 3.822%
7 | 8.626 | 4.178 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.947 | 0.973 | -3.075 | -7.746 | 10.526 | 8.296 | 4.018 | -0.33 | 3.827%
8 | 9.059 | 4.387 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.11 | 0.979 | -3.353 | -3.912 | 10.526 | 8.885 | 4.303 | -0.174 | 1.925%
9 | 9.181 | 4.447 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.126 | 0.978 | -3.403 | -3.913 | 10.526 | 9.004 | 4.361 | -0.177 | 1.925%
10 | 9.23 | 4.47 | 0.9 | Z | cloudy | 10.526 | 10.515 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.133 | 0.978 | -3.423 | -3.913 | 10.515 | 9.052 | 4.384 | -0.178 | 1.925%
11 | 9.261 | 4.485 | 0.9 | Z | cloudy | 10.526 | 10.484 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.137 | 0.978 | -3.435 | -3.913 | 10.484 | 9.083 | 4.399 | -0.178 | 1.926%
12 | 9.292 | 4.5 | 0.9 | Z | cloudy | 10.526 | 10.452 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.141 | 0.977 | -3.448 | -3.913 | 10.452 | 9.113 | 4.414 | -0.179 | 1.926%
13 | 9.322 | 4.515 | 0.9 | Z | cloudy | 10.526 | 10.452 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.145 | 0.977 | -3.46 | -3.913 | 10.452 | 9.142 | 4.428 | -0.18 | 1.926%
14 | 9.338 | 4.523 | 0.9 | Z | cloudy | 10.526 | 10.473 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.147 | 0.977 | -3.466 | -3.913 | 10.473 | 9.158 | 4.436 | -0.18 | 1.926%
15 | 9.404 | 4.555 | 0.9 | Z | cloudy | 10.526 | 10.505 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.156 | 0.977 | -3.493 | -3.913 | 10.505 | 9.223 | 4.467 | -0.181 | 1.926%
16 | 9.594 | 4.647 | 0.9 | Z | cloudy | 10.526 | 10.515 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.182 | 0.975 | -3.571 | -3.913 | 10.515 | 9.409 | 4.557 | -0.185 | 1.927%
17 | 9.883 | 4.787 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.221 | 0.973 | -3.689 | -3.914 | 10.526 | 9.692 | 4.694 | -0.191 | 1.928%
18 | 10 | 4.843 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.237 | 0.972 | -3.737 | -3.914 | 10.526 | 9.807 | 4.75 | -0.193 | 1.929%
19 | 9.966 | 4.827 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.232 | 0.972 | -3.723 | -3.914 | 10.526 | 9.774 | 4.734 | -0.192 | 1.928%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.218 | 0.973 | -3.678 | -3.914 | 10.526 | 9.667 | 4.682 | -0.19 | 1.928%
21 | 9.62 | 4.659 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.185 | 0.975 | -3.581 | -3.913 | 10.526 | 9.435 | 4.569 | -0.185 | 1.927%
22 | 9.139 | 4.426 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.12 | 0.979 | -3.386 | -3.913 | 10.526 | 8.963 | 4.341 | -0.176 | 1.925%
23 | 8.547 | 4.14 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.937 | 0.973 | -3.043 | -7.746 | 10.526 | 8.22 | 3.981 | -0.327 | 3.827%
24 | 8.047 | 3.897 | 0.9 | Z | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.871 | 0.977 | -2.845 | -7.744 | 10.526 | 7.739 | 3.748 | -0.308 | 3.823%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.594 | 0.979 | -2.554 | -3.841 | 5.263 | 7.416 | 3.592 | -0.3 | 3.892%
2 | 7.517 | 3.641 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.991 | -1.405 | 0.973 | -2.338 | -5.263 | 5.263 | 7.115 | 3.446 | -0.402 | 5.35%
3 | 7.407 | 3.587 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.992 | -1.377 | 0.974 | -2.296 | -5.263 | 5.263 | 7.011 | 3.396 | -0.396 | 5.348%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.992 | -1.375 | 0.974 | -2.293 | -5.263 | 5.263 | 7.002 | 3.391 | -0.396 | 5.348%
5 | 7.563 | 3.663 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.991 | -1.416 | 0.973 | -2.356 | -5.263 | 5.263 | 7.158 | 3.467 | -0.405 | 5.351%
6 | 7.986 | 3.868 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.662 | 0.977 | -2.66 | -3.843 | 5.263 | 7.675 | 3.717 | -0.311 | 3.897%
7 | 8.626 | 4.178 | 0.9 | Z | very sunny | 5.263 | 5.252 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.825 | 0.972 | -2.911 | -3.846 | 5.252 | 8.289 | 4.014 | -0.337 | 3.908%
8 | 9.059 | 4.387 | 0.9 | Z | very sunny | 5.263 | 5.116 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.124 | 0.979 | -3.27 | -1.945 | 5.116 | 8.881 | 4.301 | -0.178 | 1.968%
9 | 9.181 | 4.447 | 0.9 | Z | very sunny | 5.263 | 4.705 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.156 | 0.978 | -3.32 | -1.945 | 4.705 | 9 | 4.359 | -0.181 | 1.969%
10 | 9.23 | 4.47 | 0.9 | Z | very sunny | 5.263 | 4.142 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.169 | 0.978 | -3.339 | -1.945 | 4.142 | 9.048 | 4.382 | -0.182 | 1.97%
11 | 9.261 | 4.485 | 0.9 | Z | very sunny | 5.263 | 3.574 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.177 | 0.977 | -3.352 | -1.945 | 3.574 | 9.079 | 4.397 | -0.182 | 1.97%
12 | 9.292 | 4.5 | 0.9 | Z | very sunny | 5.263 | 3.258 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.185 | 0.977 | -3.364 | -1.945 | 3.258 | 9.109 | 4.412 | -0.183 | 1.97%
13 | 9.322 | 4.515 | 0.9 | Z | very sunny | 5.263 | 3.353 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.193 | 0.977 | -3.376 | -1.945 | 3.353 | 9.138 | 4.426 | -0.184 | 1.971%
14 | 9.338 | 4.523 | 0.9 | Z | very sunny | 5.263 | 3.505 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.197 | 0.977 | -3.383 | -1.946 | 3.505 | 9.154 | 4.433 | -0.184 | 1.971%
15 | 9.404 | 4.555 | 0.9 | Z | very sunny | 5.263 | 3.942 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.214 | 0.976 | -3.41 | -1.946 | 3.942 | 9.219 | 4.465 | -0.185 | 1.971%
16 | 9.594 | 4.647 | 0.9 | Z | very sunny | 5.263 | 4.458 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.264 | 0.975 | -3.487 | -1.946 | 4.458 | 9.405 | 4.555 | -0.189 | 1.973%
17 | 9.883 | 4.787 | 0.9 | Z | very sunny | 5.263 | 4.921 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.34 | 0.973 | -3.604 | -1.947 | 4.921 | 9.688 | 4.692 | -0.195 | 1.976%
18 | 10 | 4.843 | 0.9 | Z | very sunny | 5.263 | 5.189 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.371 | 0.972 | -3.652 | -1.947 | 5.189 | 9.802 | 4.747 | -0.198 | 1.977%
19 | 9.966 | 4.827 | 0.9 | Z | very sunny | 5.263 | 5.258 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.362 | 0.972 | -3.638 | -1.947 | 5.258 | 9.769 | 4.731 | -0.197 | 1.977%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.333 | 0.973 | -3.593 | -1.947 | 5.263 | 9.662 | 4.68 | -0.195 | 1.976%
21 | 9.62 | 4.659 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.271 | 0.975 | -3.497 | -1.946 | 5.263 | 9.43 | 4.567 | -0.19 | 1.973%
22 | 9.139 | 4.426 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.145 | 0.978 | -3.303 | -1.945 | 5.263 | 8.959 | 4.339 | -0.18 | 1.969%
23 | 8.547 | 4.14 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.805 | 0.973 | -2.88 | -3.846 | 5.263 | 8.213 | 3.978 | -0.334 | 3.907%
24 | 8.047 | 3.897 | 0.9 | Z | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.678 | 0.977 | -2.683 | -3.843 | 5.263 | 7.733 | 3.745 | -0.314 | 3.898%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.594 | 0.979 | -2.554 | -3.841 | 5.263 | 7.416 | 3.592 | -0.3 | 3.892%
2 | 7.517 | 3.641 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.991 | -1.405 | 0.973 | -2.338 | -5.263 | 5.263 | 7.115 | 3.446 | -0.402 | 5.35%
3 | 7.407 | 3.587 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.992 | -1.377 | 0.974 | -2.296 | -5.263 | 5.263 | 7.011 | 3.396 | -0.396 | 5.348%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.992 | -1.375 | 0.974 | -2.293 | -5.263 | 5.263 | 7.002 | 3.391 | -0.396 | 5.348%
5 | 7.563 | 3.663 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.991 | -1.416 | 0.973 | -2.356 | -5.263 | 5.263 | 7.158 | 3.467 | -0.405 | 5.351%
6 | 7.986 | 3.868 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.662 | 0.977 | -2.66 | -3.843 | 5.263 | 7.675 | 3.717 | -0.311 | 3.897%
7 | 8.626 | 4.178 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.825 | 0.972 | -2.911 | -3.846 | 5.263 | 8.289 | 4.014 | -0.337 | 3.908%
8 | 9.059 | 4.387 | 0.9 | Z | moderate sun | 5.263 | 5.258 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.124 | 0.979 | -3.27 | -1.945 | 5.258 | 8.881 | 4.301 | -0.178 | 1.968%
9 | 9.181 | 4.447 | 0.9 | Z | moderate sun | 5.263 | 5.205 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.156 | 0.978 | -3.32 | -1.945 | 5.205 | 9 | 4.359 | -0.181 | 1.969%
10 | 9.23 | 4.47 | 0.9 | Z | moderate sun | 5.263 | 5.095 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.169 | 0.978 | -3.339 | -1.945 | 5.095 | 9.048 | 4.382 | -0.182 | 1.97%
11 | 9.261 | 4.485 | 0.9 | Z | moderate sun | 5.263 | 4.979 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.177 | 0.977 | -3.352 | -1.945 | 4.979 | 9.079 | 4.397 | -0.182 | 1.97%
12 | 9.292 | 4.5 | 0.9 | Z | moderate sun | 5.263 | 4.916 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.185 | 0.977 | -3.364 | -1.945 | 4.916 | 9.109 | 4.412 | -0.183 | 1.97%
13 | 9.322 | 4.515 | 0.9 | Z | moderate sun | 5.263 | 4.984 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.193 | 0.977 | -3.376 | -1.945 | 4.984 | 9.138 | 4.426 | -0.184 | 1.971%
14 | 9.338 | 4.523 | 0.9 | Z | moderate sun | 5.263 | 5.016 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.197 | 0.977 | -3.383 | -1.946 | 5.016 | 9.154 | 4.433 | -0.184 | 1.971%
15 | 9.404 | 4.555 | 0.9 | Z | moderate sun | 5.263 | 5.147 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.214 | 0.976 | -3.41 | -1.946 | 5.147 | 9.219 | 4.465 | -0.185 | 1.971%
16 | 9.594 | 4.647 | 0.9 | Z | moderate sun | 5.263 | 5.237 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.264 | 0.975 | -3.487 | -1.946 | 5.237 | 9.405 | 4.555 | -0.189 | 1.973%
17 | 9.883 | 4.787 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.34 | 0.973 | -3.604 | -1.947 | 5.263 | 9.688 | 4.692 | -0.195 | 1.976%
18 | 10 | 4.843 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.371 | 0.972 | -3.652 | -1.947 | 5.263 | 9.802 | 4.747 | -0.198 | 1.977%
19 | 9.966 | 4.827 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.362 | 0.972 | -3.638 | -1.947 | 5.263 | 9.769 | 4.731 | -0.197 | 1.977%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.333 | 0.973 | -3.593 | -1.947 | 5.263 | 9.662 | 4.68 | -0.195 | 1.976%
21 | 9.62 | 4.659 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.271 | 0.975 | -3.497 | -1.946 | 5.263 | 9.43 | 4.567 | -0.19 | 1.973%
22 | 9.139 | 4.426 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.145 | 0.978 | -3.303 | -1.945 | 5.263 | 8.959 | 4.339 | -0.18 | 1.969%
23 | 8.547 | 4.14 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.805 | 0.973 | -2.88 | -3.846 | 5.263 | 8.213 | 3.978 | -0.334 | 3.907%
24 | 8.047 | 3.897 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.678 | 0.977 | -2.683 | -3.843 | 5.263 | 7.733 | 3.745 | -0.314 | 3.898%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.594 | 0.979 | -2.554 | -3.841 | 5.263 | 7.416 | 3.592 | -0.3 | 3.892%
2 | 7.517 | 3.641 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.991 | -1.405 | 0.973 | -2.338 | -5.263 | 5.263 | 7.115 | 3.446 | -0.402 | 5.35%
3 | 7.407 | 3.587 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.992 | -1.377 | 0.974 | -2.296 | -5.263 | 5.263 | 7.011 | 3.396 | -0.396 | 5.348%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.992 | -1.375 | 0.974 | -2.293 | -5.263 | 5.263 | 7.002 | 3.391 | -0.396 | 5.348%
5 | 7.563 | 3.663 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.991 | -1.416 | 0.973 | -2.356 | -5.263 | 5.263 | 7.158 | 3.467 | -0.405 | 5.351%
6 | 7.986 | 3.868 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.662 | 0.977 | -2.66 | -3.843 | 5.263 | 7.675 | 3.717 | -0.311 | 3.897%
7 | 8.626 | 4.178 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.825 | 0.972 | -2.911 | -3.846 | 5.263 | 8.289 | 4.014 | -0.337 | 3.908%
8 | 9.059 | 4.387 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.124 | 0.979 | -3.27 | -1.945 | 5.263 | 8.881 | 4.301 | -0.178 | 1.968%
9 | 9.181 | 4.447 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.156 | 0.978 | -3.32 | -1.945 | 5.263 | 9 | 4.359 | -0.181 | 1.969%
10 | 9.23 | 4.47 | 0.9 | Z | cloudy | 5.263 | 5.258 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.169 | 0.978 | -3.339 | -1.945 | 5.258 | 9.048 | 4.382 | -0.182 | 1.97%
11 | 9.261 | 4.485 | 0.9 | Z | cloudy | 5.263 | 5.242 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.177 | 0.977 | -3.352 | -1.945 | 5.242 | 9.079 | 4.397 | -0.182 | 1.97%
12 | 9.292 | 4.5 | 0.9 | Z | cloudy | 5.263 | 5.226 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.185 | 0.977 | -3.364 | -1.945 | 5.226 | 9.109 | 4.412 | -0.183 | 1.97%
13 | 9.322 | 4.515 | 0.9 | Z | cloudy | 5.263 | 5.226 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.193 | 0.977 | -3.376 | -1.945 | 5.226 | 9.138 | 4.426 | -0.184 | 1.971%
14 | 9.338 | 4.523 | 0.9 | Z | cloudy | 5.263 | 5.237 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.197 | 0.977 | -3.383 | -1.946 | 5.237 | 9.154 | 4.433 | -0.184 | 1.971%
15 | 9.404 | 4.555 | 0.9 | Z | cloudy | 5.263 | 5.252 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.214 | 0.976 | -3.41 | -1.946 | 5.252 | 9.219 | 4.465 | -0.185 | 1.971%
16 | 9.594 | 4.647 | 0.9 | Z | cloudy | 5.263 | 5.258 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.264 | 0.975 | -3.487 | -1.946 | 5.258 | 9.405 | 4.555 | -0.189 | 1.973%
17 | 9.883 | 4.787 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.34 | 0.973 | -3.604 | -1.947 | 5.263 | 9.688 | 4.692 | -0.195 | 1.976%
18 | 10 | 4.843 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.371 | 0.972 | -3.652 | -1.947 | 5.263 | 9.802 | 4.747 | -0.198 | 1.977%
19 | 9.966 | 4.827 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.362 | 0.972 | -3.638 | -1.947 | 5.263 | 9.769 | 4.731 | -0.197 | 1.977%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.333 | 0.973 | -3.593 | -1.947 | 5.263 | 9.662 | 4.68 | -0.195 | 1.976%
21 | 9.62 | 4.659 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.271 | 0.975 | -3.497 | -1.946 | 5.263 | 9.43 | 4.567 | -0.19 | 1.973%
22 | 9.139 | 4.426 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.145 | 0.978 | -3.303 | -1.945 | 5.263 | 8.959 | 4.339 | -0.18 | 1.969%
23 | 8.547 | 4.14 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.805 | 0.973 | -2.88 | -3.846 | 5.263 | 8.213 | 3.978 | -0.334 | 3.907%
24 | 8.047 | 3.897 | 0.9 | Z | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.678 | 0.977 | -2.683 | -3.843 | 5.263 | 7.733 | 3.745 | -0.314 | 3.898%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.594 | 0.979 | -2.554 | -3.841 | 10.526 | 7.416 | 3.592 | -0.3 | 3.892%
2 | 7.517 | 3.641 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.362 | 0.971 | -2.295 | -5.7 | 10.526 | 7.081 | 3.429 | -0.436 | 5.803%
3 | 7.407 | 3.587 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.334 | 0.972 | -2.253 | -5.699 | 10.526 | 6.977 | 3.379 | -0.43 | 5.8%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.332 | 0.972 | -2.25 | -5.699 | 10.526 | 6.969 | 3.375 | -0.429 | 5.8%
5 | 7.563 | 3.663 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.988 | -1.373 | 0.97 | -2.313 | -5.7 | 10.526 | 7.124 | 3.45 | -0.439 | 5.805%
6 | 7.986 | 3.868 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.662 | 0.977 | -2.66 | -3.843 | 10.526 | 7.675 | 3.717 | -0.311 | 3.897%
7 | 8.626 | 4.178 | 0.9 | Z | very sunny | 10.526 | 10.505 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.825 | 0.972 | -2.911 | -3.846 | 10.505 | 8.289 | 4.014 | -0.337 | 3.908%
8 | 9.059 | 4.387 | 0.9 | Z | very sunny | 10.526 | 10.231 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.124 | 0.979 | -3.27 | -1.945 | 10.231 | 8.881 | 4.301 | -0.178 | 1.968%
9 | 9.181 | 4.447 | 0.9 | Z | very sunny | 10.526 | 9.41 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.156 | 0.978 | -3.32 | -1.945 | 9.41 | 9 | 4.359 | -0.181 | 1.969%
10 | 9.23 | 4.47 | 0.9 | Z | very sunny | 10.526 | 8.284 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.169 | 0.978 | -3.339 | -1.945 | 8.284 | 9.048 | 4.382 | -0.182 | 1.97%
11 | 9.261 | 4.485 | 0.9 | Z | very sunny | 10.526 | 7.147 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.177 | 0.977 | -3.352 | -1.945 | 7.147 | 9.079 | 4.397 | -0.182 | 1.97%
12 | 9.292 | 4.5 | 0.9 | Z | very sunny | 10.526 | 6.516 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.185 | 0.977 | -3.364 | -1.945 | 6.516 | 9.109 | 4.412 | -0.183 | 1.97%
13 | 9.322 | 4.515 | 0.9 | Z | very sunny | 10.526 | 6.705 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.193 | 0.977 | -3.376 | -1.945 | 6.705 | 9.138 | 4.426 | -0.184 | 1.971%
14 | 9.338 | 4.523 | 0.9 | Z | very sunny | 10.526 | 7.01 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.197 | 0.977 | -3.383 | -1.946 | 7.01 | 9.154 | 4.433 | -0.184 | 1.971%
15 | 9.404 | 4.555 | 0.9 | Z | very sunny | 10.526 | 7.884 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.214 | 0.976 | -3.41 | -1.946 | 7.884 | 9.219 | 4.465 | -0.185 | 1.971%
16 | 9.594 | 4.647 | 0.9 | Z | very sunny | 10.526 | 8.916 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.264 | 0.975 | -3.487 | -1.946 | 8.916 | 9.405 | 4.555 | -0.189 | 1.973%
17 | 9.883 | 4.787 | 0.9 | Z | very sunny | 10.526 | 9.842 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.34 | 0.973 | -3.604 | -1.947 | 9.842 | 9.688 | 4.692 | -0.195 | 1.976%
18 | 10 | 4.843 | 0.9 | Z | very sunny | 10.526 | 10.379 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.371 | 0.972 | -3.652 | -1.947 | 10.379 | 9.802 | 4.747 | -0.198 | 1.977%
19 | 9.966 | 4.827 | 0.9 | Z | very sunny | 10.526 | 10.515 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.362 | 0.972 | -3.638 | -1.947 | 10.515 | 9.769 | 4.731 | -0.197 | 1.977%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.333 | 0.973 | -3.593 | -1.947 | 10.526 | 9.662 | 4.68 | -0.195 | 1.976%
21 | 9.62 | 4.659 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.271 | 0.975 | -3.497 | -1.946 | 10.526 | 9.43 | 4.567 | -0.19 | 1.973%
22 | 9.139 | 4.426 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.145 | 0.978 | -3.303 | -1.945 | 10.526 | 8.959 | 4.339 | -0.18 | 1.969%
23 | 8.547 | 4.14 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.805 | 0.973 | -2.88 | -3.846 | 10.526 | 8.213 | 3.978 | -0.334 | 3.907%
24 | 8.047 | 3.897 | 0.9 | Z | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.678 | 0.977 | -2.683 | -3.843 | 10.526 | 7.733 | 3.745 | -0.314 | 3.898%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.594 | 0.979 | -2.554 | -3.841 | 10.526 | 7.416 | 3.592 | -0.3 | 3.892%
2 | 7.517 | 3.641 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.362 | 0.971 | -2.295 | -5.7 | 10.526 | 7.081 | 3.429 | -0.436 | 5.803%
3 | 7.407 | 3.587 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.334 | 0.972 | -2.253 | -5.699 | 10.526 | 6.977 | 3.379 | -0.43 | 5.8%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.332 | 0.972 | -2.25 | -5.699 | 10.526 | 6.969 | 3.375 | -0.429 | 5.8%
5 | 7.563 | 3.663 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.988 | -1.373 | 0.97 | -2.313 | -5.7 | 10.526 | 7.124 | 3.45 | -0.439 | 5.805%
6 | 7.986 | 3.868 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.662 | 0.977 | -2.66 | -3.843 | 10.526 | 7.675 | 3.717 | -0.311 | 3.897%
7 | 8.626 | 4.178 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.825 | 0.972 | -2.911 | -3.846 | 10.526 | 8.289 | 4.014 | -0.337 | 3.908%
8 | 9.059 | 4.387 | 0.9 | Z | moderate sun | 10.526 | 10.515 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.124 | 0.979 | -3.27 | -1.945 | 10.515 | 8.881 | 4.301 | -0.178 | 1.968%
9 | 9.181 | 4.447 | 0.9 | Z | moderate sun | 10.526 | 10.41 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.156 | 0.978 | -3.32 | -1.945 | 10.41 | 9 | 4.359 | -0.181 | 1.969%
10 | 9.23 | 4.47 | 0.9 | Z | moderate sun | 10.526 | 10.189 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.169 | 0.978 | -3.339 | -1.945 | 10.189 | 9.048 | 4.382 | -0.182 | 1.97%
11 | 9.261 | 4.485 | 0.9 | Z | moderate sun | 10.526 | 9.958 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.177 | 0.977 | -3.352 | -1.945 | 9.958 | 9.079 | 4.397 | -0.182 | 1.97%
12 | 9.292 | 4.5 | 0.9 | Z | moderate sun | 10.526 | 9.831 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.185 | 0.977 | -3.364 | -1.945 | 9.831 | 9.109 | 4.412 | -0.183 | 1.97%
13 | 9.322 | 4.515 | 0.9 | Z | moderate sun | 10.526 | 9.968 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.193 | 0.977 | -3.376 | -1.945 | 9.968 | 9.138 | 4.426 | -0.184 | 1.971%
14 | 9.338 | 4.523 | 0.9 | Z | moderate sun | 10.526 | 10.031 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.197 | 0.977 | -3.383 | -1.946 | 10.031 | 9.154 | 4.433 | -0.184 | 1.971%
15 | 9.404 | 4.555 | 0.9 | Z | moderate sun | 10.526 | 10.294 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.214 | 0.976 | -3.41 | -1.946 | 10.294 | 9.219 | 4.465 | -0.185 | 1.971%
16 | 9.594 | 4.647 | 0.9 | Z | moderate sun | 10.526 | 10.473 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.264 | 0.975 | -3.487 | -1.946 | 10.473 | 9.405 | 4.555 | -0.189 | 1.973%
17 | 9.883 | 4.787 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.34 | 0.973 | -3.604 | -1.947 | 10.526 | 9.688 | 4.692 | -0.195 | 1.976%
18 | 10 | 4.843 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.371 | 0.972 | -3.652 | -1.947 | 10.526 | 9.802 | 4.747 | -0.198 | 1.977%
19 | 9.966 | 4.827 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.362 | 0.972 | -3.638 | -1.947 | 10.526 | 9.769 | 4.731 | -0.197 | 1.977%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.333 | 0.973 | -3.593 | -1.947 | 10.526 | 9.662 | 4.68 | -0.195 | 1.976%
21 | 9.62 | 4.659 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.271 | 0.975 | -3.497 | -1.946 | 10.526 | 9.43 | 4.567 | -0.19 | 1.973%
22 | 9.139 | 4.426 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.145 | 0.978 | -3.303 | -1.945 | 10.526 | 8.959 | 4.339 | -0.18 | 1.969%
23 | 8.547 | 4.14 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.805 | 0.973 | -2.88 | -3.846 | 10.526 | 8.213 | 3.978 | -0.334 | 3.907%
24 | 8.047 | 3.897 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.678 | 0.977 | -2.683 | -3.843 | 10.526 | 7.733 | 3.745 | -0.314 | 3.898%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.594 | 0.979 | -2.554 | -3.841 | 10.526 | 7.416 | 3.592 | -0.3 | 3.892%
2 | 7.517 | 3.641 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.362 | 0.971 | -2.295 | -5.7 | 10.526 | 7.081 | 3.429 | -0.436 | 5.803%
3 | 7.407 | 3.587 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.334 | 0.972 | -2.253 | -5.699 | 10.526 | 6.977 | 3.379 | -0.43 | 5.8%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.332 | 0.972 | -2.25 | -5.699 | 10.526 | 6.969 | 3.375 | -0.429 | 5.8%
5 | 7.563 | 3.663 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.988 | -1.373 | 0.97 | -2.313 | -5.7 | 10.526 | 7.124 | 3.45 | -0.439 | 5.805%
6 | 7.986 | 3.868 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.662 | 0.977 | -2.66 | -3.843 | 10.526 | 7.675 | 3.717 | -0.311 | 3.897%
7 | 8.626 | 4.178 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.825 | 0.972 | -2.911 | -3.846 | 10.526 | 8.289 | 4.014 | -0.337 | 3.908%
8 | 9.059 | 4.387 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.124 | 0.979 | -3.27 | -1.945 | 10.526 | 8.881 | 4.301 | -0.178 | 1.968%
9 | 9.181 | 4.447 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.156 | 0.978 | -3.32 | -1.945 | 10.526 | 9 | 4.359 | -0.181 | 1.969%
10 | 9.23 | 4.47 | 0.9 | Z | cloudy | 10.526 | 10.515 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.169 | 0.978 | -3.339 | -1.945 | 10.515 | 9.048 | 4.382 | -0.182 | 1.97%
11 | 9.261 | 4.485 | 0.9 | Z | cloudy | 10.526 | 10.484 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.177 | 0.977 | -3.352 | -1.945 | 10.484 | 9.079 | 4.397 | -0.182 | 1.97%
12 | 9.292 | 4.5 | 0.9 | Z | cloudy | 10.526 | 10.452 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.185 | 0.977 | -3.364 | -1.945 | 10.452 | 9.109 | 4.412 | -0.183 | 1.97%
13 | 9.322 | 4.515 | 0.9 | Z | cloudy | 10.526 | 10.452 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.193 | 0.977 | -3.376 | -1.945 | 10.452 | 9.138 | 4.426 | -0.184 | 1.971%
14 | 9.338 | 4.523 | 0.9 | Z | cloudy | 10.526 | 10.473 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.197 | 0.977 | -3.383 | -1.946 | 10.473 | 9.154 | 4.433 | -0.184 | 1.971%
15 | 9.404 | 4.555 | 0.9 | Z | cloudy | 10.526 | 10.505 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.214 | 0.976 | -3.41 | -1.946 | 10.505 | 9.219 | 4.465 | -0.185 | 1.971%
16 | 9.594 | 4.647 | 0.9 | Z | cloudy | 10.526 | 10.515 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.264 | 0.975 | -3.487 | -1.946 | 10.515 | 9.405 | 4.555 | -0.189 | 1.973%
17 | 9.883 | 4.787 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.34 | 0.973 | -3.604 | -1.947 | 10.526 | 9.688 | 4.692 | -0.195 | 1.976%
18 | 10 | 4.843 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.371 | 0.972 | -3.652 | -1.947 | 10.526 | 9.802 | 4.747 | -0.198 | 1.977%
19 | 9.966 | 4.827 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.362 | 0.972 | -3.638 | -1.947 | 10.526 | 9.769 | 4.731 | -0.197 | 1.977%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.333 | 0.973 | -3.593 | -1.947 | 10.526 | 9.662 | 4.68 | -0.195 | 1.976%
21 | 9.62 | 4.659 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.271 | 0.975 | -3.497 | -1.946 | 10.526 | 9.43 | 4.567 | -0.19 | 1.973%
22 | 9.139 | 4.426 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.145 | 0.978 | -3.303 | -1.945 | 10.526 | 8.959 | 4.339 | -0.18 | 1.969%
23 | 8.547 | 4.14 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.805 | 0.973 | -2.88 | -3.846 | 10.526 | 8.213 | 3.978 | -0.334 | 3.907%
24 | 8.047 | 3.897 | 0.9 | Z | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.678 | 0.977 | -2.683 | -3.843 | 10.526 | 7.733 | 3.745 | -0.314 | 3.898%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.288 | 0.97 | -2.288 | -3.654 | 5.263 | 7.278 | 3.525 | -0.438 | 5.673%
2 | 7.517 | 3.641 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.18 | 0.97 | -2.18 | -3.832 | 5.263 | 7.07 | 3.424 | -0.447 | 5.95%
3 | 7.407 | 3.587 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.122 | 0.97 | -2.122 | -3.93 | 5.263 | 6.955 | 3.369 | -0.452 | 6.101%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.117 | 0.97 | -2.117 | -3.938 | 5.263 | 6.946 | 3.364 | -0.452 | 6.113%
5 | 7.563 | 3.663 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.205 | 0.97 | -2.205 | -3.791 | 5.263 | 7.118 | 3.447 | -0.445 | 5.886%
6 | 7.986 | 3.868 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.434 | 0.97 | -2.434 | -3.409 | 5.263 | 7.563 | 3.663 | -0.423 | 5.295%
7 | 8.626 | 4.178 | 0.9 | Z | very sunny | 5.263 | 5.252 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.788 | 0.97 | -2.788 | -2.819 | 5.252 | 8.248 | 3.995 | -0.378 | 4.379%
8 | 9.059 | 4.387 | 0.9 | Z | very sunny | 5.263 | 5.116 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.031 | 0.97 | -3.031 | -2.41 | 5.116 | 8.72 | 4.223 | -0.339 | 3.744%
9 | 9.181 | 4.447 | 0.9 | Z | very sunny | 5.263 | 4.705 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.101 | 0.97 | -3.101 | -2.293 | 4.705 | 8.854 | 4.288 | -0.327 | 3.563%
10 | 9.23 | 4.47 | 0.9 | Z | very sunny | 5.263 | 4.142 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.129 | 0.97 | -3.129 | -2.246 | 4.142 | 8.908 | 4.314 | -0.322 | 3.49%
11 | 9.261 | 4.485 | 0.9 | Z | very sunny | 5.263 | 3.574 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.146 | 0.97 | -3.146 | -2.216 | 3.574 | 8.942 | 4.331 | -0.319 | 3.443%
12 | 9.292 | 4.5 | 0.9 | Z | very sunny | 5.263 | 3.258 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.164 | 0.97 | -3.164 | -2.186 | 3.258 | 8.976 | 4.347 | -0.316 | 3.397%
13 | 9.322 | 4.515 | 0.9 | Z | very sunny | 5.263 | 3.353 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.181 | 0.97 | -3.181 | -2.157 | 3.353 | 9.01 | 4.364 | -0.312 | 3.352%
14 | 9.338 | 4.523 | 0.9 | Z | very sunny | 5.263 | 3.505 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.19 | 0.97 | -3.19 | -2.141 | 3.505 | 9.027 | 4.372 | -0.311 | 3.328%
15 | 9.404 | 4.555 | 0.9 | Z | very sunny | 5.263 | 3.942 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 3.942 | 9.1 | 4.408 | -0.304 | 3.229%
16 | 9.594 | 4.647 | 0.9 | Z | very sunny | 5.263 | 4.458 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.338 | 0.97 | -3.338 | -1.892 | 4.458 | 9.312 | 4.51 | -0.282 | 2.941%
17 | 9.883 | 4.787 | 0.9 | Z | very sunny | 5.263 | 4.921 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.608 | 4.921 | 9.636 | 4.667 | -0.247 | 2.499%
18 | 10 | 4.843 | 0.9 | Z | very sunny | 5.263 | 5.189 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.575 | 0.97 | -3.575 | -1.491 | 5.189 | 9.768 | 4.731 | -0.232 | 2.318%
19 | 9.966 | 4.827 | 0.9 | Z | very sunny | 5.263 | 5.258 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.555 | 0.97 | -3.555 | -1.525 | 5.258 | 9.73 | 4.712 | -0.236 | 2.371%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.491 | 0.97 | -3.491 | -1.633 | 5.263 | 9.607 | 4.653 | -0.25 | 2.539%
21 | 9.62 | 4.659 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.353 | 0.97 | -3.353 | -1.867 | 5.263 | 9.341 | 4.524 | -0.279 | 2.902%
22 | 9.139 | 4.426 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.077 | 0.97 | -3.077 | -2.333 | 5.263 | 8.808 | 4.266 | -0.331 | 3.625%
23 | 8.547 | 4.14 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.744 | 0.97 | -2.744 | -2.893 | 5.263 | 8.163 | 3.953 | -0.384 | 4.494%
24 | 8.047 | 3.897 | 0.9 | Z | very sunny | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.468 | 0.97 | -2.468 | -3.354 | 5.263 | 7.628 | 3.694 | -0.419 | 5.209%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.288 | 0.97 | -2.288 | -3.654 | 5.263 | 7.278 | 3.525 | -0.438 | 5.674%
2 | 7.517 | 3.641 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.18 | 0.97 | -2.18 | -3.832 | 5.263 | 7.07 | 3.424 | -0.447 | 5.95%
3 | 7.407 | 3.587 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.122 | 0.97 | -2.122 | -3.93 | 5.263 | 6.955 | 3.369 | -0.452 | 6.101%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.117 | 0.97 | -2.117 | -3.938 | 5.263 | 6.946 | 3.364 | -0.452 | 6.113%
5 | 7.563 | 3.663 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.205 | 0.97 | -2.205 | -3.791 | 5.263 | 7.118 | 3.447 | -0.445 | 5.886%
6 | 7.986 | 3.868 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.434 | 0.97 | -2.434 | -3.409 | 5.263 | 7.563 | 3.663 | -0.423 | 5.295%
7 | 8.626 | 4.178 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.788 | 0.97 | -2.788 | -2.819 | 5.263 | 8.248 | 3.995 | -0.378 | 4.379%
8 | 9.059 | 4.387 | 0.9 | Z | moderate sun | 5.263 | 5.258 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.031 | 0.97 | -3.031 | -2.41 | 5.258 | 8.72 | 4.223 | -0.339 | 3.744%
9 | 9.181 | 4.447 | 0.9 | Z | moderate sun | 5.263 | 5.205 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.101 | 0.97 | -3.101 | -2.293 | 5.205 | 8.854 | 4.288 | -0.327 | 3.563%
10 | 9.23 | 4.47 | 0.9 | Z | moderate sun | 5.263 | 5.095 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.129 | 0.97 | -3.129 | -2.246 | 5.095 | 8.908 | 4.314 | -0.322 | 3.49%
11 | 9.261 | 4.485 | 0.9 | Z | moderate sun | 5.263 | 4.979 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.146 | 0.97 | -3.146 | -2.216 | 4.979 | 8.942 | 4.331 | -0.319 | 3.443%
12 | 9.292 | 4.5 | 0.9 | Z | moderate sun | 5.263 | 4.916 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.164 | 0.97 | -3.164 | -2.186 | 4.916 | 8.976 | 4.347 | -0.316 | 3.397%
13 | 9.322 | 4.515 | 0.9 | Z | moderate sun | 5.263 | 4.984 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.181 | 0.97 | -3.181 | -2.157 | 4.984 | 9.01 | 4.364 | -0.312 | 3.352%
14 | 9.338 | 4.523 | 0.9 | Z | moderate sun | 5.263 | 5.016 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.19 | 0.97 | -3.19 | -2.141 | 5.016 | 9.027 | 4.372 | -0.311 | 3.328%
15 | 9.404 | 4.555 | 0.9 | Z | moderate sun | 5.263 | 5.147 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 5.147 | 9.1 | 4.408 | -0.304 | 3.229%
16 | 9.594 | 4.647 | 0.9 | Z | moderate sun | 5.263 | 5.237 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.338 | 0.97 | -3.338 | -1.892 | 5.237 | 9.312 | 4.51 | -0.282 | 2.941%
17 | 9.883 | 4.787 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.608 | 5.263 | 9.636 | 4.667 | -0.247 | 2.499%
18 | 10 | 4.843 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.575 | 0.97 | -3.575 | -1.491 | 5.263 | 9.768 | 4.731 | -0.232 | 2.318%
19 | 9.966 | 4.827 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.555 | 0.97 | -3.555 | -1.525 | 5.263 | 9.73 | 4.712 | -0.236 | 2.371%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.491 | 0.97 | -3.491 | -1.633 | 5.263 | 9.607 | 4.653 | -0.25 | 2.539%
21 | 9.62 | 4.659 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.353 | 0.97 | -3.353 | -1.867 | 5.263 | 9.341 | 4.524 | -0.279 | 2.902%
22 | 9.139 | 4.426 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.077 | 0.97 | -3.077 | -2.333 | 5.263 | 8.808 | 4.266 | -0.331 | 3.625%
23 | 8.547 | 4.14 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.744 | 0.97 | -2.744 | -2.893 | 5.263 | 8.163 | 3.953 | -0.384 | 4.494%
24 | 8.047 | 3.897 | 0.9 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.468 | 0.97 | -2.468 | -3.354 | 5.263 | 7.628 | 3.694 | -0.419 | 5.209%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.288 | 0.97 | -2.288 | -3.654 | 5.263 | 7.278 | 3.525 | -0.438 | 5.674%
2 | 7.517 | 3.641 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.18 | 0.97 | -2.18 | -3.832 | 5.263 | 7.07 | 3.424 | -0.447 | 5.95%
3 | 7.407 | 3.587 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.122 | 0.97 | -2.122 | -3.93 | 5.263 | 6.955 | 3.369 | -0.452 | 6.101%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.117 | 0.97 | -2.117 | -3.938 | 5.263 | 6.946 | 3.364 | -0.452 | 6.113%
5 | 7.563 | 3.663 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.205 | 0.97 | -2.205 | -3.791 | 5.263 | 7.118 | 3.447 | -0.445 | 5.886%
6 | 7.986 | 3.868 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.434 | 0.97 | -2.434 | -3.409 | 5.263 | 7.563 | 3.663 | -0.423 | 5.295%
7 | 8.626 | 4.178 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.788 | 0.97 | -2.788 | -2.819 | 5.263 | 8.248 | 3.995 | -0.378 | 4.379%
8 | 9.059 | 4.387 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.031 | 0.97 | -3.031 | -2.41 | 5.263 | 8.72 | 4.223 | -0.339 | 3.744%
9 | 9.181 | 4.447 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.101 | 0.97 | -3.101 | -2.293 | 5.263 | 8.854 | 4.288 | -0.327 | 3.563%
10 | 9.23 | 4.47 | 0.9 | Z | cloudy | 5.263 | 5.258 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.129 | 0.97 | -3.129 | -2.246 | 5.258 | 8.908 | 4.314 | -0.322 | 3.49%
11 | 9.261 | 4.485 | 0.9 | Z | cloudy | 5.263 | 5.242 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.146 | 0.97 | -3.146 | -2.216 | 5.242 | 8.942 | 4.331 | -0.319 | 3.443%
12 | 9.292 | 4.5 | 0.9 | Z | cloudy | 5.263 | 5.226 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.164 | 0.97 | -3.164 | -2.186 | 5.226 | 8.976 | 4.347 | -0.316 | 3.397%
13 | 9.322 | 4.515 | 0.9 | Z | cloudy | 5.263 | 5.226 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.181 | 0.97 | -3.181 | -2.157 | 5.226 | 9.01 | 4.364 | -0.312 | 3.352%
14 | 9.338 | 4.523 | 0.9 | Z | cloudy | 5.263 | 5.237 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.19 | 0.97 | -3.19 | -2.141 | 5.237 | 9.027 | 4.372 | -0.311 | 3.328%
15 | 9.404 | 4.555 | 0.9 | Z | cloudy | 5.263 | 5.252 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 5.252 | 9.1 | 4.408 | -0.304 | 3.229%
16 | 9.594 | 4.647 | 0.9 | Z | cloudy | 5.263 | 5.258 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.338 | 0.97 | -3.338 | -1.892 | 5.258 | 9.312 | 4.51 | -0.282 | 2.941%
17 | 9.883 | 4.787 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.608 | 5.263 | 9.636 | 4.667 | -0.247 | 2.499%
18 | 10 | 4.843 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.575 | 0.97 | -3.575 | -1.491 | 5.263 | 9.768 | 4.731 | -0.232 | 2.318%
19 | 9.966 | 4.827 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.555 | 0.97 | -3.555 | -1.525 | 5.263 | 9.73 | 4.712 | -0.236 | 2.371%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.491 | 0.97 | -3.491 | -1.633 | 5.263 | 9.607 | 4.653 | -0.25 | 2.539%
21 | 9.62 | 4.659 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.353 | 0.97 | -3.353 | -1.867 | 5.263 | 9.341 | 4.524 | -0.279 | 2.902%
22 | 9.139 | 4.426 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.077 | 0.97 | -3.077 | -2.333 | 5.263 | 8.808 | 4.266 | -0.331 | 3.625%
23 | 8.547 | 4.14 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.744 | 0.97 | -2.744 | -2.893 | 5.263 | 8.163 | 3.953 | -0.384 | 4.494%
24 | 8.047 | 3.897 | 0.9 | Z | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.468 | 0.97 | -2.468 | -3.354 | 5.263 | 7.628 | 3.694 | -0.419 | 5.209%
1 | 7.716 | 3.737 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.288 | 0.97 | -2.288 | -3.654 | 10.526 | 7.278 | 3.525 | -0.438 | 5.674%
2 | 7.517 | 3.641 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.18 | 0.97 | -2.18 | -3.832 | 10.526 | 7.07 | 3.424 | -0.447 | 5.95%
3 | 7.407 | 3.587 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.122 | 0.97 | -2.122 | -3.93 | 10.526 | 6.955 | 3.369 | -0.452 | 6.101%
4 | 7.398 | 3.583 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.117 | 0.97 | -2.117 | -3.938 | 10.526 | 6.946 | 3.364 | -0.452 | 6.113%
5 | 7.563 | 3.663 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.205 | 0.97 | -2.205 | -3.791 | 10.526 | 7.118 | 3.447 | -0.445 | 5.886%
6 | 7.986 | 3.868 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.434 | 0.97 | -2.434 | -3.409 | 10.526 | 7.563 | 3.663 | -0.423 | 5.295%
7 | 8.626 | 4.178 | 0.9 | Z | very sunny | 10.526 | 10.505 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.788 | 0.97 | -2.788 | -2.819 | 10.505 | 8.248 | 3.995 | -0.378 | 4.379%
8 | 9.059 | 4.387 | 0.9 | Z | very sunny | 10.526 | 10.231 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.031 | 0.97 | -3.031 | -2.41 | 10.231 | 8.72 | 4.223 | -0.339 | 3.744%
9 | 9.181 | 4.447 | 0.9 | Z | very sunny | 10.526 | 9.41 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.101 | 0.97 | -3.101 | -2.293 | 9.41 | 8.854 | 4.288 | -0.327 | 3.563%
10 | 9.23 | 4.47 | 0.9 | Z | very sunny | 10.526 | 8.284 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.129 | 0.97 | -3.129 | -2.246 | 8.284 | 8.908 | 4.314 | -0.322 | 3.49%
11 | 9.261 | 4.485 | 0.9 | Z | very sunny | 10.526 | 7.147 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.146 | 0.97 | -3.146 | -2.216 | 7.147 | 8.942 | 4.331 | -0.319 | 3.443%
12 | 9.292 | 4.5 | 0.9 | Z | very sunny | 10.526 | 6.516 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.164 | 0.97 | -3.164 | -2.186 | 6.516 | 8.976 | 4.347 | -0.316 | 3.397%
13 | 9.322 | 4.515 | 0.9 | Z | very sunny | 10.526 | 6.705 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.181 | 0.97 | -3.181 | -2.157 | 6.705 | 9.01 | 4.364 | -0.312 | 3.352%
14 | 9.338 | 4.523 | 0.9 | Z | very sunny | 10.526 | 7.01 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.19 | 0.97 | -3.19 | -2.141 | 7.01 | 9.027 | 4.372 | -0.311 | 3.328%
15 | 9.404 | 4.555 | 0.9 | Z | very sunny | 10.526 | 7.884 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 7.884 | 9.1 | 4.408 | -0.304 | 3.229%
16 | 9.594 | 4.647 | 0.9 | Z | very sunny | 10.526 | 8.916 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.338 | 0.97 | -3.338 | -1.892 | 8.916 | 9.312 | 4.51 | -0.282 | 2.941%
17 | 9.883 | 4.787 | 0.9 | Z | very sunny | 10.526 | 9.842 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.608 | 9.842 | 9.636 | 4.667 | -0.247 | 2.499%
18 | 10 | 4.843 | 0.9 | Z | very sunny | 10.526 | 10.379 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.575 | 0.97 | -3.575 | -1.491 | 10.379 | 9.768 | 4.731 | -0.232 | 2.318%
19 | 9.966 | 4.827 | 0.9 | Z | very sunny | 10.526 | 10.515 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.555 | 0.97 | -3.555 | -1.525 | 10.515 | 9.73 | 4.712 | -0.236 | 2.371%
20 | 9.857 | 4.774 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.491 | 0.97 | -3.491 | -1.633 | 10.526 | 9.607 | 4.653 | -0.25 | 2.539%
21 | 9.62 | 4.659 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.353 | 0.97 | -3.353 | -1.867 | 10.526 | 9.341 | 4.524 | -0.279 | 2.902%
22 | 9.139 | 4.426 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.077 | 0.97 | -3.077 | -2.333 | 10.526 | 8.808 | 4.266 | -0.331 | 3.625%
23 | 8.547 | 4.14 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.744 | 0.97 | -2.744 | -2.893 | 10.526 | 8.163 | 3.953 | -0.384 | 4.494%
24 | 8.047 | 3.897 | 0.9 | Z | very sunny | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.468 | 0.97 | -2.468 | -3.354 | 10.526 | 7.628 | 3.694 | -0.419 | 5.209%
1 | 7.716 | 3.737 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.288 | 0.97 | -2.288 | -3.654 | 10.526 | 7.278 | 3.525 | -0.438 | 5.674%
2 | 7.517 | 3.641 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.18 | 0.97 | -2.18 | -3.832 | 10.526 | 7.07 | 3.424 | -0.447 | 5.95%
3 | 7.407 | 3.587 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.122 | 0.97 | -2.122 | -3.93 | 10.526 | 6.955 | 3.369 | -0.452 | 6.101%
4 | 7.398 | 3.583 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.117 | 0.97 | -2.117 | -3.938 | 10.526 | 6.946 | 3.364 | -0.452 | 6.113%
5 | 7.563 | 3.663 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.205 | 0.97 | -2.205 | -3.791 | 10.526 | 7.118 | 3.447 | -0.445 | 5.886%
6 | 7.986 | 3.868 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.434 | 0.97 | -2.434 | -3.409 | 10.526 | 7.563 | 3.663 | -0.423 | 5.295%
7 | 8.626 | 4.178 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.788 | 0.97 | -2.788 | -2.819 | 10.526 | 8.248 | 3.995 | -0.378 | 4.379%
8 | 9.059 | 4.387 | 0.9 | Z | moderate sun | 10.526 | 10.515 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.031 | 0.97 | -3.031 | -2.41 | 10.515 | 8.72 | 4.223 | -0.339 | 3.744%
9 | 9.181 | 4.447 | 0.9 | Z | moderate sun | 10.526 | 10.41 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.101 | 0.97 | -3.101 | -2.293 | 10.41 | 8.854 | 4.288 | -0.327 | 3.563%
10 | 9.23 | 4.47 | 0.9 | Z | moderate sun | 10.526 | 10.189 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.129 | 0.97 | -3.129 | -2.246 | 10.189 | 8.908 | 4.314 | -0.322 | 3.49%
11 | 9.261 | 4.485 | 0.9 | Z | moderate sun | 10.526 | 9.958 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.146 | 0.97 | -3.146 | -2.216 | 9.958 | 8.942 | 4.331 | -0.319 | 3.443%
12 | 9.292 | 4.5 | 0.9 | Z | moderate sun | 10.526 | 9.831 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.164 | 0.97 | -3.164 | -2.186 | 9.831 | 8.976 | 4.347 | -0.316 | 3.397%
13 | 9.322 | 4.515 | 0.9 | Z | moderate sun | 10.526 | 9.968 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.181 | 0.97 | -3.181 | -2.157 | 9.968 | 9.01 | 4.364 | -0.312 | 3.352%
14 | 9.338 | 4.523 | 0.9 | Z | moderate sun | 10.526 | 10.031 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.19 | 0.97 | -3.19 | -2.141 | 10.031 | 9.027 | 4.372 | -0.311 | 3.328%
15 | 9.404 | 4.555 | 0.9 | Z | moderate sun | 10.526 | 10.294 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 10.294 | 9.1 | 4.408 | -0.304 | 3.229%
16 | 9.594 | 4.647 | 0.9 | Z | moderate sun | 10.526 | 10.473 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.338 | 0.97 | -3.338 | -1.892 | 10.473 | 9.312 | 4.51 | -0.282 | 2.941%
17 | 9.883 | 4.787 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.608 | 10.526 | 9.636 | 4.667 | -0.247 | 2.499%
18 | 10 | 4.843 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.575 | 0.97 | -3.575 | -1.491 | 10.526 | 9.768 | 4.731 | -0.232 | 2.318%
19 | 9.966 | 4.827 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.555 | 0.97 | -3.555 | -1.525 | 10.526 | 9.73 | 4.712 | -0.236 | 2.371%
20 | 9.857 | 4.774 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.491 | 0.97 | -3.491 | -1.633 | 10.526 | 9.607 | 4.653 | -0.25 | 2.539%
21 | 9.62 | 4.659 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.353 | 0.97 | -3.353 | -1.867 | 10.526 | 9.341 | 4.524 | -0.279 | 2.902%
22 | 9.139 | 4.426 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.077 | 0.97 | -3.077 | -2.333 | 10.526 | 8.808 | 4.266 | -0.331 | 3.625%
23 | 8.547 | 4.14 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.744 | 0.97 | -2.744 | -2.893 | 10.526 | 8.163 | 3.953 | -0.384 | 4.494%
24 | 8.047 | 3.897 | 0.9 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.468 | 0.97 | -2.468 | -3.354 | 10.526 | 7.628 | 3.694 | -0.419 | 5.209%
1 | 7.716 | 3.737 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.288 | 0.97 | -2.288 | -3.654 | 10.526 | 7.278 | 3.525 | -0.438 | 5.674%
2 | 7.517 | 3.641 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.18 | 0.97 | -2.18 | -3.832 | 10.526 | 7.07 | 3.424 | -0.447 | 5.95%
3 | 7.407 | 3.587 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.122 | 0.97 | -2.122 | -3.93 | 10.526 | 6.955 | 3.369 | -0.452 | 6.101%
4 | 7.398 | 3.583 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.117 | 0.97 | -2.117 | -3.938 | 10.526 | 6.946 | 3.364 | -0.452 | 6.113%
5 | 7.563 | 3.663 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.205 | 0.97 | -2.205 | -3.791 | 10.526 | 7.118 | 3.447 | -0.445 | 5.886%
6 | 7.986 | 3.868 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.434 | 0.97 | -2.434 | -3.409 | 10.526 | 7.563 | 3.663 | -0.423 | 5.295%
7 | 8.626 | 4.178 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.788 | 0.97 | -2.788 | -2.819 | 10.526 | 8.248 | 3.995 | -0.378 | 4.379%
8 | 9.059 | 4.387 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.031 | 0.97 | -3.031 | -2.41 | 10.526 | 8.72 | 4.223 | -0.339 | 3.744%
9 | 9.181 | 4.447 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.101 | 0.97 | -3.101 | -2.293 | 10.526 | 8.854 | 4.288 | -0.327 | 3.563%
10 | 9.23 | 4.47 | 0.9 | Z | cloudy | 10.526 | 10.515 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.129 | 0.97 | -3.129 | -2.246 | 10.515 | 8.908 | 4.314 | -0.322 | 3.49%
11 | 9.261 | 4.485 | 0.9 | Z | cloudy | 10.526 | 10.484 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.146 | 0.97 | -3.146 | -2.216 | 10.484 | 8.942 | 4.331 | -0.319 | 3.443%
12 | 9.292 | 4.5 | 0.9 | Z | cloudy | 10.526 | 10.452 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.164 | 0.97 | -3.164 | -2.186 | 10.452 | 8.976 | 4.347 | -0.316 | 3.397%
13 | 9.322 | 4.515 | 0.9 | Z | cloudy | 10.526 | 10.452 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.181 | 0.97 | -3.181 | -2.157 | 10.452 | 9.01 | 4.364 | -0.312 | 3.352%
14 | 9.338 | 4.523 | 0.9 | Z | cloudy | 10.526 | 10.473 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.19 | 0.97 | -3.19 | -2.141 | 10.473 | 9.027 | 4.372 | -0.311 | 3.328%
15 | 9.404 | 4.555 | 0.9 | Z | cloudy | 10.526 | 10.505 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 10.505 | 9.1 | 4.408 | -0.304 | 3.229%
16 | 9.594 | 4.647 | 0.9 | Z | cloudy | 10.526 | 10.515 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.338 | 0.97 | -3.338 | -1.892 | 10.515 | 9.312 | 4.51 | -0.282 | 2.941%
17 | 9.883 | 4.787 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.506 | 0.97 | -3.506 | -1.608 | 10.526 | 9.636 | 4.667 | -0.247 | 2.499%
18 | 10 | 4.843 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.575 | 0.97 | -3.575 | -1.491 | 10.526 | 9.768 | 4.731 | -0.232 | 2.318%
19 | 9.966 | 4.827 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.555 | 0.97 | -3.555 | -1.525 | 10.526 | 9.73 | 4.712 | -0.236 | 2.371%
20 | 9.857 | 4.774 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.491 | 0.97 | -3.491 | -1.633 | 10.526 | 9.607 | 4.653 | -0.25 | 2.539%
21 | 9.62 | 4.659 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.353 | 0.97 | -3.353 | -1.867 | 10.526 | 9.341 | 4.524 | -0.279 | 2.902%
22 | 9.139 | 4.426 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.077 | 0.97 | -3.077 | -2.333 | 10.526 | 8.808 | 4.266 | -0.331 | 3.625%
23 | 8.547 | 4.14 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.744 | 0.97 | -2.744 | -2.893 | 10.526 | 8.163 | 3.953 | -0.384 | 4.494%
24 | 8.047 | 3.897 | 0.9 | Z | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.468 | 0.97 | -2.468 | -3.354 | 10.526 | 7.628 | 3.694 | -0.419 | 5.209%
1 | 7.716 | 2.536 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.918 | 0.996 | -2.926 | -5.263 | 5.263 | 7.517 | 2.471 | -0.199 | 2.573%
2 | 7.517 | 2.471 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.891 | 0.997 | -2.844 | -5.263 | 5.263 | 7.324 | 2.407 | -0.193 | 2.571%
3 | 7.407 | 2.435 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.876 | 0.998 | -2.799 | -5.263 | 5.263 | 7.217 | 2.372 | -0.19 | 2.571%
4 | 7.398 | 2.432 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.875 | 0.998 | -2.796 | -5.263 | 5.263 | 7.208 | 2.369 | -0.19 | 2.571%
5 | 7.563 | 2.486 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.897 | 0.997 | -2.863 | -5.263 | 5.263 | 7.369 | 2.422 | -0.194 | 2.571%
6 | 7.986 | 2.625 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.954 | 0.994 | -3.037 | -5.263 | 5.263 | 7.781 | 2.557 | -0.205 | 2.572%
7 | 8.626 | 2.835 | 0.95 | Z | very sunny | 5.263 | 5.252 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.042 | 0.99 | -3.302 | -5.252 | 5.252 | 8.405 | 2.763 | -0.221 | 2.558%
8 | 9.059 | 2.978 | 0.95 | Z | very sunny | 5.263 | 5.116 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.025 | -1.105 | 0.988 | -3.486 | -5.116 | 5.116 | 8.833 | 2.903 | -0.226 | 2.492%
9 | 9.181 | 3.018 | 0.95 | Z | very sunny | 5.263 | 4.705 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.026 | -1.132 | 0.988 | -3.548 | -4.705 | 4.705 | 8.971 | 2.949 | -0.21 | 2.289%
10 | 9.23 | 3.034 | 0.95 | Z | very sunny | 5.263 | 4.142 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.027 | -1.154 | 0.99 | -3.584 | -4.142 | 4.142 | 9.044 | 2.973 | -0.186 | 2.014%
11 | 9.261 | 3.044 | 0.95 | Z | very sunny | 5.263 | 3.574 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.029 | -1.173 | 0.991 | -3.611 | -3.574 | 3.574 | 9.099 | 2.991 | -0.162 | 1.751%
12 | 9.292 | 3.054 | 0.95 | Z | very sunny | 5.263 | 3.258 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.029 | -1.186 | 0.991 | -3.633 | -3.258 | 3.258 | 9.144 | 3.005 | -0.148 | 1.595%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 5.263 | 3.353 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.029 | -1.188 | 0.991 | -3.644 | -3.353 | 3.353 | 9.171 | 3.014 | -0.151 | 1.623%
14 | 9.338 | 3.069 | 0.95 | Z | very sunny | 5.263 | 3.505 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.029 | -1.187 | 0.99 | -3.646 | -3.505 | 3.505 | 9.179 | 3.017 | -0.159 | 1.698%
15 | 9.404 | 3.091 | 0.95 | Z | very sunny | 5.263 | 3.942 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.027 | -1.184 | 0.989 | -3.662 | -3.942 | 3.942 | 9.224 | 3.032 | -0.18 | 1.913%
16 | 9.594 | 3.153 | 0.95 | Z | very sunny | 5.263 | 4.458 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.026 | -1.196 | 0.987 | -3.728 | -4.458 | 4.458 | 9.386 | 3.085 | -0.208 | 2.168%
17 | 9.883 | 3.248 | 0.95 | Z | very sunny | 5.263 | 4.921 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.024 | -1.222 | 0.984 | -3.837 | -4.921 | 4.921 | 9.645 | 3.17 | -0.238 | 2.406%
18 | 10 | 3.287 | 0.95 | Z | very sunny | 5.263 | 5.189 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.231 | 0.982 | -3.879 | -5.189 | 5.189 | 9.746 | 3.203 | -0.254 | 2.541%
19 | 9.966 | 3.276 | 0.95 | Z | very sunny | 5.263 | 5.258 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.224 | 0.982 | -3.862 | -5.258 | 5.258 | 9.709 | 3.191 | -0.257 | 2.576%
20 | 9.857 | 3.24 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.209 | 0.983 | -3.816 | -5.263 | 5.263 | 9.603 | 3.156 | -0.254 | 2.578%
21 | 9.62 | 3.162 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.024 | -1.177 | 0.984 | -3.716 | -5.263 | 5.263 | 9.372 | 3.08 | -0.248 | 2.577%
22 | 9.139 | 3.004 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.111 | 0.987 | -3.515 | -5.263 | 5.263 | 8.904 | 2.926 | -0.235 | 2.576%
23 | 8.547 | 2.809 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.03 | 0.991 | -3.268 | -5.263 | 5.263 | 8.327 | 2.737 | -0.22 | 2.574%
24 | 8.047 | 2.645 | 0.95 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.963 | 0.994 | -3.062 | -5.263 | 5.263 | 7.84 | 2.577 | -0.207 | 2.573%
1 | 7.716 | 2.536 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.918 | 0.996 | -2.926 | -5.263 | 5.263 | 7.518 | 2.471 | -0.198 | 2.572%
2 | 7.517 | 2.471 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.891 | 0.997 | -2.844 | -5.263 | 5.263 | 7.324 | 2.407 | -0.193 | 2.571%
3 | 7.407 | 2.435 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.876 | 0.998 | -2.799 | -5.263 | 5.263 | 7.217 | 2.372 | -0.19 | 2.571%
4 | 7.398 | 2.432 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.875 | 0.998 | -2.796 | -5.263 | 5.263 | 7.208 | 2.369 | -0.19 | 2.571%
5 | 7.563 | 2.486 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.897 | 0.997 | -2.863 | -5.263 | 5.263 | 7.369 | 2.422 | -0.194 | 2.571%
6 | 7.986 | 2.625 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.954 | 0.994 | -3.037 | -5.263 | 5.263 | 7.781 | 2.557 | -0.205 | 2.572%
7 | 8.626 | 2.835 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.041 | 0.99 | -3.301 | -5.263 | 5.263 | 8.404 | 2.762 | -0.222 | 2.574%
8 | 9.059 | 2.978 | 0.95 | Z | moderate sun | 5.263 | 5.258 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.025 | -1.1 | 0.988 | -3.481 | -5.258 | 5.258 | 8.826 | 2.901 | -0.233 | 2.573%
9 | 9.181 | 3.018 | 0.95 | Z | moderate sun | 5.263 | 5.205 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.024 | -1.118 | 0.987 | -3.534 | -5.205 | 5.205 | 8.947 | 2.941 | -0.234 | 2.547%
10 | 9.23 | 3.034 | 0.95 | Z | moderate sun | 5.263 | 5.095 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.025 | -1.129 | 0.987 | -3.558 | -5.095 | 5.095 | 9.001 | 2.958 | -0.229 | 2.482%
11 | 9.261 | 3.044 | 0.95 | Z | moderate sun | 5.263 | 4.979 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.025 | -1.136 | 0.987 | -3.574 | -4.979 | 4.979 | 9.036 | 2.97 | -0.225 | 2.425%
12 | 9.292 | 3.054 | 0.95 | Z | moderate sun | 5.263 | 4.916 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.025 | -1.142 | 0.987 | -3.589 | -4.916 | 4.916 | 9.07 | 2.981 | -0.222 | 2.394%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 5.263 | 4.984 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.025 | -1.144 | 0.987 | -3.599 | -4.984 | 4.984 | 9.096 | 2.99 | -0.226 | 2.428%
14 | 9.338 | 3.069 | 0.95 | Z | moderate sun | 5.263 | 5.016 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.025 | -1.145 | 0.987 | -3.605 | -5.016 | 5.016 | 9.11 | 2.994 | -0.228 | 2.443%
15 | 9.404 | 3.091 | 0.95 | Z | moderate sun | 5.263 | 5.147 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.024 | -1.151 | 0.986 | -3.629 | -5.147 | 5.147 | 9.168 | 3.013 | -0.236 | 2.508%
16 | 9.594 | 3.153 | 0.95 | Z | moderate sun | 5.263 | 5.237 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.024 | -1.174 | 0.985 | -3.707 | -5.237 | 5.237 | 9.349 | 3.073 | -0.245 | 2.553%
17 | 9.883 | 3.248 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.023 | -1.213 | 0.983 | -3.827 | -5.263 | 5.263 | 9.628 | 3.165 | -0.255 | 2.578%
18 | 10 | 3.287 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.229 | 0.982 | -3.877 | -5.263 | 5.263 | 9.742 | 3.202 | -0.258 | 2.578%
19 | 9.966 | 3.276 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.224 | 0.982 | -3.862 | -5.263 | 5.263 | 9.709 | 3.191 | -0.257 | 2.578%
20 | 9.857 | 3.24 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.209 | 0.983 | -3.816 | -5.263 | 5.263 | 9.603 | 3.156 | -0.254 | 2.578%
21 | 9.62 | 3.162 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.024 | -1.177 | 0.984 | -3.716 | -5.263 | 5.263 | 9.372 | 3.08 | -0.248 | 2.577%
22 | 9.139 | 3.004 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.111 | 0.987 | -3.515 | -5.263 | 5.263 | 8.904 | 2.926 | -0.235 | 2.576%
23 | 8.547 | 2.809 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.03 | 0.991 | -3.268 | -5.263 | 5.263 | 8.327 | 2.737 | -0.22 | 2.574%
24 | 8.047 | 2.645 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.963 | 0.994 | -3.062 | -5.263 | 5.263 | 7.84 | 2.577 | -0.207 | 2.573%
1 | 7.716 | 2.536 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.918 | 0.996 | -2.926 | -5.263 | 5.263 | 7.518 | 2.471 | -0.198 | 2.572%
2 | 7.517 | 2.471 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.891 | 0.997 | -2.844 | -5.263 | 5.263 | 7.324 | 2.407 | -0.193 | 2.571%
3 | 7.407 | 2.435 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.876 | 0.998 | -2.799 | -5.263 | 5.263 | 7.217 | 2.372 | -0.19 | 2.571%
4 | 7.398 | 2.432 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.875 | 0.998 | -2.796 | -5.263 | 5.263 | 7.208 | 2.369 | -0.19 | 2.571%
5 | 7.563 | 2.486 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.897 | 0.997 | -2.863 | -5.263 | 5.263 | 7.369 | 2.422 | -0.194 | 2.571%
6 | 7.986 | 2.625 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.954 | 0.994 | -3.037 | -5.263 | 5.263 | 7.781 | 2.557 | -0.205 | 2.572%
7 | 8.626 | 2.835 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.041 | 0.99 | -3.301 | -5.263 | 5.263 | 8.404 | 2.762 | -0.222 | 2.574%
8 | 9.059 | 2.978 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.025 | -1.1 | 0.988 | -3.481 | -5.263 | 5.263 | 8.826 | 2.901 | -0.233 | 2.576%
9 | 9.181 | 3.018 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.024 | -1.117 | 0.987 | -3.532 | -5.263 | 5.263 | 8.945 | 2.94 | -0.236 | 2.576%
10 | 9.23 | 3.034 | 0.95 | Z | cloudy | 5.263 | 5.258 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.024 | -1.124 | 0.987 | -3.553 | -5.258 | 5.258 | 8.992 | 2.956 | -0.238 | 2.573%
11 | 9.261 | 3.044 | 0.95 | Z | cloudy | 5.263 | 5.242 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.024 | -1.128 | 0.987 | -3.566 | -5.242 | 5.242 | 9.023 | 2.966 | -0.238 | 2.566%
12 | 9.292 | 3.054 | 0.95 | Z | cloudy | 5.263 | 5.226 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.024 | -1.133 | 0.986 | -3.58 | -5.226 | 5.226 | 9.054 | 2.976 | -0.238 | 2.558%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 5.263 | 5.226 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.024 | -1.137 | 0.986 | -3.592 | -5.226 | 5.226 | 9.084 | 2.986 | -0.238 | 2.558%
14 | 9.338 | 3.069 | 0.95 | Z | cloudy | 5.263 | 5.237 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.024 | -1.139 | 0.986 | -3.599 | -5.237 | 5.237 | 9.1 | 2.991 | -0.238 | 2.552%
15 | 9.404 | 3.091 | 0.95 | Z | cloudy | 5.263 | 5.252 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.024 | -1.148 | 0.986 | -3.626 | -5.252 | 5.252 | 9.163 | 3.012 | -0.241 | 2.56%
16 | 9.594 | 3.153 | 0.95 | Z | cloudy | 5.263 | 5.258 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.024 | -1.173 | 0.985 | -3.706 | -5.258 | 5.258 | 9.347 | 3.072 | -0.247 | 2.574%
17 | 9.883 | 3.248 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.023 | -1.213 | 0.983 | -3.827 | -5.263 | 5.263 | 9.628 | 3.165 | -0.255 | 2.578%
18 | 10 | 3.287 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.229 | 0.982 | -3.877 | -5.263 | 5.263 | 9.742 | 3.202 | -0.258 | 2.578%
19 | 9.966 | 3.276 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.224 | 0.982 | -3.862 | -5.263 | 5.263 | 9.709 | 3.191 | -0.257 | 2.578%
20 | 9.857 | 3.24 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.209 | 0.983 | -3.816 | -5.263 | 5.263 | 9.603 | 3.156 | -0.254 | 2.578%
21 | 9.62 | 3.162 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.024 | -1.177 | 0.984 | -3.716 | -5.263 | 5.263 | 9.372 | 3.08 | -0.248 | 2.577%
22 | 9.139 | 3.004 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.111 | 0.987 | -3.515 | -5.263 | 5.263 | 8.904 | 2.926 | -0.235 | 2.576%
23 | 8.547 | 2.809 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.03 | 0.991 | -3.268 | -5.263 | 5.263 | 8.327 | 2.737 | -0.22 | 2.574%
24 | 8.047 | 2.645 | 0.95 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.963 | 0.994 | -3.062 | -5.263 | 5.263 | 7.84 | 2.577 | -0.207 | 2.573%
1 | 7.716 | 2.536 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.775 | 0.982 | -2.783 | -10.526 | 10.526 | 7.315 | 2.404 | -0.401 | 5.195%
2 | 7.517 | 2.471 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.749 | 0.983 | -2.702 | -10.526 | 10.526 | 7.127 | 2.342 | -0.39 | 5.194%
3 | 7.407 | 2.435 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.734 | 0.984 | -2.657 | -10.526 | 10.526 | 7.022 | 2.308 | -0.385 | 5.193%
4 | 7.398 | 2.432 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.733 | 0.984 | -2.653 | -10.526 | 10.526 | 7.014 | 2.305 | -0.384 | 5.193%
5 | 7.563 | 2.486 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.755 | 0.983 | -2.72 | -10.526 | 10.526 | 7.17 | 2.357 | -0.393 | 5.194%
6 | 7.986 | 2.625 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.811 | 0.981 | -2.893 | -10.526 | 10.526 | 7.571 | 2.488 | -0.415 | 5.197%
7 | 8.626 | 2.835 | 0.95 | Z | very sunny | 10.526 | 10.505 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.897 | 0.977 | -3.157 | -10.505 | 10.505 | 8.178 | 2.688 | -0.448 | 5.19%
8 | 9.059 | 2.978 | 0.95 | Z | very sunny | 10.526 | 10.231 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.011 | -0.963 | 0.975 | -3.344 | -10.231 | 10.231 | 8.601 | 2.827 | -0.458 | 5.054%
9 | 9.181 | 3.018 | 0.95 | Z | very sunny | 10.526 | 9.41 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.013 | -1.002 | 0.977 | -3.418 | -9.41 | 9.41 | 8.755 | 2.878 | -0.426 | 4.64%
10 | 9.23 | 3.034 | 0.95 | Z | very sunny | 10.526 | 8.284 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.016 | -1.041 | 0.979 | -3.47 | -8.284 | 8.284 | 8.854 | 2.91 | -0.376 | 4.07%
11 | 9.261 | 3.044 | 0.95 | Z | very sunny | 10.526 | 7.147 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.019 | -1.076 | 0.982 | -3.514 | -7.147 | 7.147 | 8.935 | 2.937 | -0.326 | 3.518%
12 | 9.292 | 3.054 | 0.95 | Z | very sunny | 10.526 | 6.516 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.021 | -1.097 | 0.983 | -3.544 | -6.516 | 6.516 | 8.994 | 2.956 | -0.298 | 3.203%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 10.526 | 6.705 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.02 | -1.097 | 0.983 | -3.552 | -6.705 | 6.705 | 9.016 | 2.964 | -0.306 | 3.28%
14 | 9.338 | 3.069 | 0.95 | Z | very sunny | 10.526 | 7.01 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.02 | -1.091 | 0.982 | -3.551 | -7.01 | 7.01 | 9.018 | 2.964 | -0.32 | 3.431%
15 | 9.404 | 3.091 | 0.95 | Z | very sunny | 10.526 | 7.884 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.078 | 0.979 | -3.557 | -7.75 | 7.884 | 9.045 | 2.973 | -0.359 | 3.819%
16 | 9.594 | 3.153 | 0.95 | Z | very sunny | 10.526 | 8.916 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.104 | 0.978 | -3.636 | -7.75 | 8.916 | 9.228 | 3.033 | -0.366 | 3.82%
17 | 9.883 | 3.248 | 0.95 | Z | very sunny | 10.526 | 9.842 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.143 | 0.976 | -3.758 | -7.751 | 9.842 | 9.505 | 3.124 | -0.378 | 3.822%
18 | 10 | 3.287 | 0.95 | Z | very sunny | 10.526 | 10.379 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.159 | 0.976 | -3.807 | -7.751 | 10.379 | 9.618 | 3.161 | -0.382 | 3.822%
19 | 9.966 | 3.276 | 0.95 | Z | very sunny | 10.526 | 10.515 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.155 | 0.976 | -3.793 | -7.751 | 10.515 | 9.585 | 3.15 | -0.381 | 3.822%
20 | 9.857 | 3.24 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.14 | 0.977 | -3.747 | -7.751 | 10.526 | 9.48 | 3.116 | -0.377 | 3.821%
21 | 9.62 | 3.162 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.108 | 0.978 | -3.647 | -7.75 | 10.526 | 9.253 | 3.041 | -0.367 | 3.82%
22 | 9.139 | 3.004 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.965 | 0.974 | -3.369 | -10.526 | 10.526 | 8.663 | 2.848 | -0.476 | 5.204%
23 | 8.547 | 2.809 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.886 | 0.977 | -3.124 | -10.526 | 10.526 | 8.103 | 2.663 | -0.444 | 5.2%
24 | 8.047 | 2.645 | 0.95 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.012 | -0.819 | 0.98 | -2.918 | -10.526 | 10.526 | 7.629 | 2.507 | -0.418 | 5.197%
1 | 7.716 | 2.536 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.775 | 0.982 | -2.783 | -10.526 | 10.526 | 7.315 | 2.404 | -0.401 | 5.195%
2 | 7.517 | 2.471 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.749 | 0.983 | -2.702 | -10.526 | 10.526 | 7.127 | 2.342 | -0.39 | 5.194%
3 | 7.407 | 2.435 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.734 | 0.984 | -2.657 | -10.526 | 10.526 | 7.022 | 2.308 | -0.385 | 5.193%
4 | 7.398 | 2.432 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.733 | 0.984 | -2.653 | -10.526 | 10.526 | 7.014 | 2.305 | -0.384 | 5.193%
5 | 7.563 | 2.486 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.755 | 0.983 | -2.72 | -10.526 | 10.526 | 7.17 | 2.357 | -0.393 | 5.194%
6 | 7.986 | 2.625 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.811 | 0.981 | -2.893 | -10.526 | 10.526 | 7.571 | 2.488 | -0.415 | 5.197%
7 | 8.626 | 2.835 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.896 | 0.977 | -3.156 | -10.526 | 10.526 | 8.177 | 2.688 | -0.449 | 5.201%
8 | 9.059 | 2.978 | 0.95 | Z | moderate sun | 10.526 | 10.515 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.011 | -0.955 | 0.974 | -3.336 | -10.515 | 10.515 | 8.588 | 2.823 | -0.471 | 5.198%
9 | 9.181 | 3.018 | 0.95 | Z | moderate sun | 10.526 | 10.41 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.011 | -0.974 | 0.974 | -3.39 | -10.41 | 10.41 | 8.709 | 2.862 | -0.472 | 5.145%
10 | 9.23 | 3.034 | 0.95 | Z | moderate sun | 10.526 | 10.189 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.011 | -0.987 | 0.974 | -3.416 | -10.189 | 10.189 | 8.765 | 2.881 | -0.465 | 5.034%
11 | 9.261 | 3.044 | 0.95 | Z | moderate sun | 10.526 | 9.958 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.012 | -0.998 | 0.975 | -3.436 | -9.958 | 9.958 | 8.806 | 2.894 | -0.455 | 4.917%
12 | 9.292 | 3.054 | 0.95 | Z | moderate sun | 10.526 | 9.831 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.012 | -1.005 | 0.975 | -3.452 | -9.831 | 9.831 | 8.841 | 2.906 | -0.451 | 4.854%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 10.526 | 9.968 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.018 | -1.067 | 0.98 | -3.522 | -7.749 | 9.968 | 8.966 | 2.947 | -0.356 | 3.818%
14 | 9.338 | 3.069 | 0.95 | Z | moderate sun | 10.526 | 10.031 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.018 | -1.069 | 0.98 | -3.529 | -7.749 | 10.031 | 8.981 | 2.952 | -0.357 | 3.818%
15 | 9.404 | 3.091 | 0.95 | Z | moderate sun | 10.526 | 10.294 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.078 | 0.979 | -3.557 | -7.75 | 10.294 | 9.045 | 2.973 | -0.359 | 3.819%
16 | 9.594 | 3.153 | 0.95 | Z | moderate sun | 10.526 | 10.473 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.104 | 0.978 | -3.636 | -7.75 | 10.473 | 9.228 | 3.033 | -0.366 | 3.82%
17 | 9.883 | 3.248 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.143 | 0.976 | -3.758 | -7.751 | 10.526 | 9.505 | 3.124 | -0.378 | 3.822%
18 | 10 | 3.287 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.159 | 0.976 | -3.807 | -7.751 | 10.526 | 9.618 | 3.161 | -0.382 | 3.822%
19 | 9.966 | 3.276 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.155 | 0.976 | -3.793 | -7.751 | 10.526 | 9.585 | 3.15 | -0.381 | 3.822%
20 | 9.857 | 3.24 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.14 | 0.977 | -3.747 | -7.751 | 10.526 | 9.48 | 3.116 | -0.377 | 3.821%
21 | 9.62 | 3.162 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.108 | 0.978 | -3.647 | -7.75 | 10.526 | 9.253 | 3.041 | -0.367 | 3.82%
22 | 9.139 | 3.004 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.965 | 0.974 | -3.369 | -10.526 | 10.526 | 8.663 | 2.848 | -0.476 | 5.204%
23 | 8.547 | 2.809 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.886 | 0.977 | -3.124 | -10.526 | 10.526 | 8.103 | 2.663 | -0.444 | 5.2%
24 | 8.047 | 2.645 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.012 | -0.819 | 0.98 | -2.918 | -10.526 | 10.526 | 7.629 | 2.507 | -0.418 | 5.197%
1 | 7.716 | 2.536 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.775 | 0.982 | -2.783 | -10.526 | 10.526 | 7.315 | 2.404 | -0.401 | 5.195%
2 | 7.517 | 2.471 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.749 | 0.983 | -2.702 | -10.526 | 10.526 | 7.127 | 2.342 | -0.39 | 5.194%
3 | 7.407 | 2.435 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.734 | 0.984 | -2.657 | -10.526 | 10.526 | 7.022 | 2.308 | -0.385 | 5.193%
4 | 7.398 | 2.432 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.733 | 0.984 | -2.653 | -10.526 | 10.526 | 7.014 | 2.305 | -0.384 | 5.193%
5 | 7.563 | 2.486 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.755 | 0.983 | -2.72 | -10.526 | 10.526 | 7.17 | 2.357 | -0.393 | 5.194%
6 | 7.986 | 2.625 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.811 | 0.981 | -2.893 | -10.526 | 10.526 | 7.571 | 2.488 | -0.415 | 5.197%
7 | 8.626 | 2.835 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.896 | 0.977 | -3.156 | -10.526 | 10.526 | 8.177 | 2.688 | -0.449 | 5.201%
8 | 9.059 | 2.978 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.011 | -0.954 | 0.974 | -3.336 | -10.526 | 10.526 | 8.588 | 2.823 | -0.471 | 5.203%
9 | 9.181 | 3.018 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.01 | -0.971 | 0.974 | -3.386 | -10.526 | 10.526 | 8.703 | 2.861 | -0.478 | 5.204%
10 | 9.23 | 3.034 | 0.95 | Z | cloudy | 10.526 | 10.515 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.01 | -0.978 | 0.973 | -3.407 | -10.515 | 10.515 | 8.75 | 2.876 | -0.48 | 5.199%
11 | 9.261 | 3.044 | 0.95 | Z | cloudy | 10.526 | 10.484 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.01 | -0.983 | 0.973 | -3.421 | -10.484 | 10.484 | 8.781 | 2.886 | -0.48 | 5.183%
12 | 9.292 | 3.054 | 0.95 | Z | cloudy | 10.526 | 10.452 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.01 | -0.988 | 0.973 | -3.435 | -10.452 | 10.452 | 8.812 | 2.896 | -0.48 | 5.167%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 10.526 | 10.452 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.018 | -1.067 | 0.98 | -3.522 | -7.749 | 10.452 | 8.966 | 2.947 | -0.356 | 3.818%
14 | 9.338 | 3.069 | 0.95 | Z | cloudy | 10.526 | 10.473 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.018 | -1.069 | 0.98 | -3.529 | -7.749 | 10.473 | 8.981 | 2.952 | -0.357 | 3.818%
15 | 9.404 | 3.091 | 0.95 | Z | cloudy | 10.526 | 10.505 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.078 | 0.979 | -3.557 | -7.75 | 10.505 | 9.045 | 2.973 | -0.359 | 3.819%
16 | 9.594 | 3.153 | 0.95 | Z | cloudy | 10.526 | 10.515 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.104 | 0.978 | -3.636 | -7.75 | 10.515 | 9.228 | 3.033 | -0.366 | 3.82%
17 | 9.883 | 3.248 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.143 | 0.976 | -3.758 | -7.751 | 10.526 | 9.505 | 3.124 | -0.378 | 3.822%
18 | 10 | 3.287 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.159 | 0.976 | -3.807 | -7.751 | 10.526 | 9.618 | 3.161 | -0.382 | 3.822%
19 | 9.966 | 3.276 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.155 | 0.976 | -3.793 | -7.751 | 10.526 | 9.585 | 3.15 | -0.381 | 3.822%
20 | 9.857 | 3.24 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.14 | 0.977 | -3.747 | -7.751 | 10.526 | 9.48 | 3.116 | -0.377 | 3.821%
21 | 9.62 | 3.162 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.108 | 0.978 | -3.647 | -7.75 | 10.526 | 9.253 | 3.041 | -0.367 | 3.82%
22 | 9.139 | 3.004 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.965 | 0.974 | -3.369 | -10.526 | 10.526 | 8.663 | 2.848 | -0.476 | 5.204%
23 | 8.547 | 2.809 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.886 | 0.977 | -3.124 | -10.526 | 10.526 | 8.103 | 2.663 | -0.444 | 5.2%
24 | 8.047 | 2.645 | 0.95 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.012 | -0.819 | 0.98 | -2.918 | -10.526 | 10.526 | 7.629 | 2.507 | -0.418 | 5.197%
1 | 7.716 | 2.536 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.997 | -1.542 | 0.982 | -2.561 | -5.263 | 5.263 | 7.306 | 2.401 | -0.41 | 5.316%
2 | 7.517 | 2.471 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.998 | -1.49 | 0.983 | -2.481 | -5.263 | 5.263 | 7.118 | 2.339 | -0.399 | 5.313%
3 | 7.407 | 2.435 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.998 | -1.462 | 0.983 | -2.437 | -5.263 | 5.263 | 7.014 | 2.305 | -0.393 | 5.312%
4 | 7.398 | 2.432 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.998 | -1.459 | 0.984 | -2.433 | -5.263 | 5.263 | 7.005 | 2.302 | -0.393 | 5.312%
5 | 7.563 | 2.486 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.502 | 0.983 | -2.499 | -5.263 | 5.263 | 7.161 | 2.354 | -0.402 | 5.314%
6 | 7.986 | 2.625 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.996 | -1.613 | 0.98 | -2.67 | -5.263 | 5.263 | 7.561 | 2.485 | -0.425 | 5.319%
7 | 8.626 | 2.835 | 0.95 | Z | very sunny | 5.263 | 5.252 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.993 | -1.782 | 0.976 | -2.931 | -5.252 | 5.252 | 8.167 | 2.685 | -0.459 | 5.316%
8 | 9.059 | 2.978 | 0.95 | Z | very sunny | 5.263 | 5.116 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.992 | -1.91 | 0.974 | -3.122 | -5.116 | 5.116 | 8.59 | 2.823 | -0.469 | 5.18%
9 | 9.181 | 3.018 | 0.95 | Z | very sunny | 5.263 | 4.705 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.994 | -1.984 | 0.976 | -3.213 | -4.705 | 4.705 | 8.744 | 2.874 | -0.437 | 4.755%
10 | 9.23 | 3.034 | 0.95 | Z | very sunny | 5.263 | 4.142 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.997 | -2.054 | 0.979 | -3.291 | -4.142 | 4.142 | 8.845 | 2.907 | -0.385 | 4.17%
11 | 9.261 | 3.044 | 0.95 | Z | very sunny | 5.263 | 3.574 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 1 | -2.117 | 0.981 | -3.359 | -3.574 | 3.574 | 8.927 | 2.934 | -0.334 | 3.604%
12 | 9.292 | 3.054 | 0.95 | Z | very sunny | 5.263 | 3.258 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 1.001 | -2.157 | 0.983 | -3.403 | -3.258 | 3.258 | 8.987 | 2.954 | -0.305 | 3.281%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 5.263 | 3.353 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 1.001 | -2.158 | 0.982 | -3.408 | -3.353 | 3.353 | 9.009 | 2.961 | -0.313 | 3.359%
14 | 9.338 | 3.069 | 0.95 | Z | very sunny | 5.263 | 3.505 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 1 | -2.147 | 0.981 | -3.399 | -3.505 | 3.505 | 9.01 | 2.961 | -0.328 | 3.515%
15 | 9.404 | 3.091 | 0.95 | Z | very sunny | 5.263 | 3.942 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.128 | 0.979 | -3.39 | -3.853 | 3.942 | 9.038 | 2.971 | -0.366 | 3.891%
16 | 9.594 | 3.153 | 0.95 | Z | very sunny | 5.263 | 4.458 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.179 | 0.978 | -3.469 | -3.854 | 4.458 | 9.22 | 3.031 | -0.374 | 3.894%
17 | 9.883 | 3.248 | 0.95 | Z | very sunny | 5.263 | 4.921 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.256 | 0.976 | -3.589 | -3.856 | 4.921 | 9.498 | 3.122 | -0.385 | 3.899%
18 | 10 | 3.287 | 0.95 | Z | very sunny | 5.263 | 5.189 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.287 | 0.975 | -3.638 | -3.857 | 5.189 | 9.61 | 3.159 | -0.39 | 3.901%
19 | 9.966 | 3.276 | 0.95 | Z | very sunny | 5.263 | 5.258 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.278 | 0.976 | -3.624 | -3.857 | 5.258 | 9.577 | 3.148 | -0.389 | 3.9%
20 | 9.857 | 3.24 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.249 | 0.976 | -3.578 | -3.856 | 5.263 | 9.473 | 3.114 | -0.384 | 3.898%
21 | 9.62 | 3.162 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.186 | 0.978 | -3.48 | -3.855 | 5.263 | 9.245 | 3.039 | -0.375 | 3.895%
22 | 9.139 | 3.004 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.991 | -1.916 | 0.973 | -3.139 | -5.263 | 5.263 | 8.652 | 2.844 | -0.487 | 5.333%
23 | 8.547 | 2.809 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.994 | -1.76 | 0.977 | -2.897 | -5.263 | 5.263 | 8.092 | 2.66 | -0.455 | 5.326%
24 | 8.047 | 2.645 | 0.95 | Z | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.996 | -1.629 | 0.98 | -2.694 | -5.263 | 5.263 | 7.619 | 2.504 | -0.428 | 5.32%
1 | 7.716 | 2.536 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.997 | -1.542 | 0.982 | -2.561 | -5.263 | 5.263 | 7.306 | 2.401 | -0.41 | 5.316%
2 | 7.517 | 2.471 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.998 | -1.49 | 0.983 | -2.481 | -5.263 | 5.263 | 7.118 | 2.339 | -0.399 | 5.313%
3 | 7.407 | 2.435 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.998 | -1.462 | 0.983 | -2.437 | -5.263 | 5.263 | 7.014 | 2.305 | -0.393 | 5.312%
4 | 7.398 | 2.432 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.998 | -1.459 | 0.984 | -2.433 | -5.263 | 5.263 | 7.005 | 2.302 | -0.393 | 5.312%
5 | 7.563 | 2.486 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.502 | 0.983 | -2.499 | -5.263 | 5.263 | 7.161 | 2.354 | -0.402 | 5.314%
6 | 7.986 | 2.625 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.996 | -1.613 | 0.98 | -2.67 | -5.263 | 5.263 | 7.561 | 2.485 | -0.425 | 5.319%
7 | 8.626 | 2.835 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.993 | -1.781 | 0.976 | -2.93 | -5.263 | 5.263 | 8.167 | 2.684 | -0.459 | 5.327%
8 | 9.059 | 2.978 | 0.95 | Z | moderate sun | 5.263 | 5.258 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.992 | -1.895 | 0.974 | -3.107 | -5.258 | 5.258 | 8.576 | 2.819 | -0.483 | 5.327%
9 | 9.181 | 3.018 | 0.95 | Z | moderate sun | 5.263 | 5.205 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.991 | -1.933 | 0.973 | -3.163 | -5.205 | 5.205 | 8.697 | 2.859 | -0.484 | 5.274%
10 | 9.23 | 3.034 | 0.95 | Z | moderate sun | 5.263 | 5.095 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.992 | -1.957 | 0.974 | -3.194 | -5.095 | 5.095 | 8.754 | 2.877 | -0.476 | 5.16%
11 | 9.261 | 3.044 | 0.95 | Z | moderate sun | 5.263 | 4.979 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.09 | 0.98 | -3.331 | -3.852 | 4.979 | 8.901 | 2.926 | -0.36 | 3.889%
12 | 9.292 | 3.054 | 0.95 | Z | moderate sun | 5.263 | 4.916 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.098 | 0.98 | -3.344 | -3.853 | 4.916 | 8.931 | 2.935 | -0.361 | 3.89%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 5.263 | 4.984 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.106 | 0.979 | -3.356 | -3.853 | 4.984 | 8.959 | 2.945 | -0.363 | 3.89%
14 | 9.338 | 3.069 | 0.95 | Z | moderate sun | 5.263 | 5.016 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.11 | 0.979 | -3.363 | -3.853 | 5.016 | 8.975 | 2.95 | -0.363 | 3.891%
15 | 9.404 | 3.091 | 0.95 | Z | moderate sun | 5.263 | 5.147 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.128 | 0.979 | -3.39 | -3.853 | 5.147 | 9.038 | 2.971 | -0.366 | 3.892%
16 | 9.594 | 3.153 | 0.95 | Z | moderate sun | 5.263 | 5.237 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.179 | 0.978 | -3.469 | -3.854 | 5.237 | 9.22 | 3.031 | -0.374 | 3.894%
17 | 9.883 | 3.248 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.256 | 0.976 | -3.589 | -3.856 | 5.263 | 9.498 | 3.122 | -0.385 | 3.899%
18 | 10 | 3.287 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.287 | 0.975 | -3.638 | -3.857 | 5.263 | 9.61 | 3.159 | -0.39 | 3.901%
19 | 9.966 | 3.276 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.278 | 0.976 | -3.624 | -3.857 | 5.263 | 9.577 | 3.148 | -0.389 | 3.9%
20 | 9.857 | 3.24 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.249 | 0.976 | -3.578 | -3.856 | 5.263 | 9.473 | 3.114 | -0.384 | 3.898%
21 | 9.62 | 3.162 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.186 | 0.978 | -3.48 | -3.855 | 5.263 | 9.245 | 3.039 | -0.375 | 3.895%
22 | 9.139 | 3.004 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.991 | -1.916 | 0.973 | -3.139 | -5.263 | 5.263 | 8.652 | 2.844 | -0.487 | 5.333%
23 | 8.547 | 2.809 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.994 | -1.76 | 0.977 | -2.897 | -5.263 | 5.263 | 8.092 | 2.66 | -0.455 | 5.326%
24 | 8.047 | 2.645 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.996 | -1.629 | 0.98 | -2.694 | -5.263 | 5.263 | 7.619 | 2.504 | -0.428 | 5.32%
1 | 7.716 | 2.536 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.997 | -1.542 | 0.982 | -2.561 | -5.263 | 5.263 | 7.306 | 2.401 | -0.41 | 5.316%
2 | 7.517 | 2.471 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.998 | -1.49 | 0.983 | -2.481 | -5.263 | 5.263 | 7.118 | 2.339 | -0.399 | 5.313%
3 | 7.407 | 2.435 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.998 | -1.462 | 0.983 | -2.437 | -5.263 | 5.263 | 7.014 | 2.305 | -0.393 | 5.312%
4 | 7.398 | 2.432 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.998 | -1.459 | 0.984 | -2.433 | -5.263 | 5.263 | 7.005 | 2.302 | -0.393 | 5.312%
5 | 7.563 | 2.486 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.502 | 0.983 | -2.499 | -5.263 | 5.263 | 7.161 | 2.354 | -0.402 | 5.314%
6 | 7.986 | 2.625 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.996 | -1.613 | 0.98 | -2.67 | -5.263 | 5.263 | 7.561 | 2.485 | -0.425 | 5.319%
7 | 8.626 | 2.835 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.993 | -1.781 | 0.976 | -2.93 | -5.263 | 5.263 | 8.167 | 2.684 | -0.459 | 5.327%
8 | 9.059 | 2.978 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.992 | -1.895 | 0.974 | -3.107 | -5.263 | 5.263 | 8.576 | 2.819 | -0.483 | 5.332%
9 | 9.181 | 3.018 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.991 | -1.927 | 0.973 | -3.157 | -5.263 | 5.263 | 8.691 | 2.857 | -0.49 | 5.334%
10 | 9.23 | 3.034 | 0.95 | Z | cloudy | 5.263 | 5.258 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.991 | -1.941 | 0.973 | -3.177 | -5.258 | 5.258 | 8.738 | 2.872 | -0.492 | 5.329%
11 | 9.261 | 3.044 | 0.95 | Z | cloudy | 5.263 | 5.242 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.09 | 0.98 | -3.331 | -3.852 | 5.242 | 8.901 | 2.926 | -0.36 | 3.889%
12 | 9.292 | 3.054 | 0.95 | Z | cloudy | 5.263 | 5.226 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.098 | 0.98 | -3.344 | -3.853 | 5.226 | 8.931 | 2.935 | -0.361 | 3.89%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 5.263 | 5.226 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.106 | 0.979 | -3.356 | -3.853 | 5.226 | 8.959 | 2.945 | -0.363 | 3.89%
14 | 9.338 | 3.069 | 0.95 | Z | cloudy | 5.263 | 5.237 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.11 | 0.979 | -3.363 | -3.853 | 5.237 | 8.975 | 2.95 | -0.363 | 3.891%
15 | 9.404 | 3.091 | 0.95 | Z | cloudy | 5.263 | 5.252 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.128 | 0.979 | -3.39 | -3.853 | 5.252 | 9.038 | 2.971 | -0.366 | 3.892%
16 | 9.594 | 3.153 | 0.95 | Z | cloudy | 5.263 | 5.258 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.179 | 0.978 | -3.469 | -3.854 | 5.258 | 9.22 | 3.031 | -0.374 | 3.894%
17 | 9.883 | 3.248 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.256 | 0.976 | -3.589 | -3.856 | 5.263 | 9.498 | 3.122 | -0.385 | 3.899%
18 | 10 | 3.287 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.287 | 0.975 | -3.638 | -3.857 | 5.263 | 9.61 | 3.159 | -0.39 | 3.901%
19 | 9.966 | 3.276 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.278 | 0.976 | -3.624 | -3.857 | 5.263 | 9.577 | 3.148 | -0.389 | 3.9%
20 | 9.857 | 3.24 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.249 | 0.976 | -3.578 | -3.856 | 5.263 | 9.473 | 3.114 | -0.384 | 3.898%
21 | 9.62 | 3.162 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.186 | 0.978 | -3.48 | -3.855 | 5.263 | 9.245 | 3.039 | -0.375 | 3.895%
22 | 9.139 | 3.004 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.991 | -1.916 | 0.973 | -3.139 | -5.263 | 5.263 | 8.652 | 2.844 | -0.487 | 5.333%
23 | 8.547 | 2.809 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.994 | -1.76 | 0.977 | -2.897 | -5.263 | 5.263 | 8.092 | 2.66 | -0.455 | 5.326%
24 | 8.047 | 2.645 | 0.95 | Z | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.996 | -1.629 | 0.98 | -2.694 | -5.263 | 5.263 | 7.619 | 2.504 | -0.428 | 5.32%
1 | 7.716 | 2.536 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.498 | 0.979 | -2.517 | -5.705 | 10.526 | 7.271 | 2.39 | -0.445 | 5.772%
2 | 7.517 | 2.471 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.266 | 0.971 | -2.256 | -7.525 | 10.526 | 6.942 | 2.282 | -0.575 | 7.652%
3 | 7.407 | 2.435 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.238 | 0.971 | -2.213 | -7.523 | 10.526 | 6.84 | 2.248 | -0.567 | 7.649%
4 | 7.398 | 2.432 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.235 | 0.971 | -2.209 | -7.523 | 10.526 | 6.832 | 2.246 | -0.566 | 7.648%
5 | 7.563 | 2.486 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.985 | -1.277 | 0.97 | -2.274 | -7.525 | 10.526 | 6.984 | 2.296 | -0.579 | 7.653%
6 | 7.986 | 2.625 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.569 | 0.978 | -2.626 | -5.707 | 10.526 | 7.525 | 2.473 | -0.461 | 5.777%
7 | 8.626 | 2.835 | 0.95 | Z | very sunny | 10.526 | 10.505 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.735 | 0.974 | -2.884 | -5.712 | 10.505 | 8.126 | 2.671 | -0.5 | 5.791%
8 | 9.059 | 2.978 | 0.95 | Z | very sunny | 10.526 | 10.231 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.849 | 0.971 | -3.061 | -5.716 | 10.231 | 8.534 | 2.805 | -0.525 | 5.801%
9 | 9.181 | 3.018 | 0.95 | Z | very sunny | 10.526 | 9.41 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.989 | -1.881 | 0.971 | -3.111 | -5.717 | 9.41 | 8.648 | 2.843 | -0.533 | 5.803%
10 | 9.23 | 3.034 | 0.95 | Z | very sunny | 10.526 | 8.284 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.988 | -1.894 | 0.97 | -3.131 | -5.717 | 8.284 | 8.694 | 2.858 | -0.536 | 5.804%
11 | 9.261 | 3.044 | 0.95 | Z | very sunny | 10.526 | 7.147 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.09 | 0.98 | -3.331 | -3.852 | 7.147 | 8.901 | 2.926 | -0.36 | 3.889%
12 | 9.292 | 3.054 | 0.95 | Z | very sunny | 10.526 | 6.516 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.098 | 0.98 | -3.344 | -3.853 | 6.516 | 8.931 | 2.935 | -0.361 | 3.89%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 10.526 | 6.705 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.106 | 0.979 | -3.356 | -3.853 | 6.705 | 8.959 | 2.945 | -0.363 | 3.89%
14 | 9.338 | 3.069 | 0.95 | Z | very sunny | 10.526 | 7.01 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.11 | 0.979 | -3.363 | -3.853 | 7.01 | 8.975 | 2.95 | -0.363 | 3.891%
15 | 9.404 | 3.091 | 0.95 | Z | very sunny | 10.526 | 7.884 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.128 | 0.979 | -3.39 | -3.853 | 7.884 | 9.038 | 2.971 | -0.366 | 3.892%
16 | 9.594 | 3.153 | 0.95 | Z | very sunny | 10.526 | 8.916 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.179 | 0.978 | -3.469 | -3.854 | 8.916 | 9.22 | 3.031 | -0.374 | 3.894%
17 | 9.883 | 3.248 | 0.95 | Z | very sunny | 10.526 | 9.842 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.256 | 0.976 | -3.589 | -3.856 | 9.842 | 9.498 | 3.122 | -0.385 | 3.899%
18 | 10 | 3.287 | 0.95 | Z | very sunny | 10.526 | 10.379 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.287 | 0.975 | -3.638 | -3.857 | 10.379 | 9.61 | 3.159 | -0.39 | 3.901%
19 | 9.966 | 3.276 | 0.95 | Z | very sunny | 10.526 | 10.515 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.278 | 0.976 | -3.624 | -3.857 | 10.515 | 9.577 | 3.148 | -0.389 | 3.9%
20 | 9.857 | 3.24 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.249 | 0.976 | -3.578 | -3.856 | 10.526 | 9.473 | 3.114 | -0.384 | 3.898%
21 | 9.62 | 3.162 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.186 | 0.978 | -3.48 | -3.855 | 10.526 | 9.245 | 3.039 | -0.375 | 3.895%
22 | 9.139 | 3.004 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.87 | 0.971 | -3.093 | -5.717 | 10.526 | 8.609 | 2.83 | -0.53 | 5.802%
23 | 8.547 | 2.809 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.715 | 0.974 | -2.852 | -5.712 | 10.526 | 8.052 | 2.647 | -0.495 | 5.789%
24 | 8.047 | 2.645 | 0.95 | Z | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.584 | 0.977 | -2.65 | -5.708 | 10.526 | 7.582 | 2.492 | -0.465 | 5.779%
1 | 7.716 | 2.536 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.498 | 0.979 | -2.517 | -5.705 | 10.526 | 7.271 | 2.39 | -0.445 | 5.772%
2 | 7.517 | 2.471 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.266 | 0.971 | -2.256 | -7.525 | 10.526 | 6.942 | 2.282 | -0.575 | 7.652%
3 | 7.407 | 2.435 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.238 | 0.971 | -2.213 | -7.523 | 10.526 | 6.84 | 2.248 | -0.567 | 7.649%
4 | 7.398 | 2.432 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.235 | 0.971 | -2.209 | -7.523 | 10.526 | 6.832 | 2.246 | -0.566 | 7.648%
5 | 7.563 | 2.486 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.985 | -1.277 | 0.97 | -2.274 | -7.525 | 10.526 | 6.984 | 2.296 | -0.579 | 7.653%
6 | 7.986 | 2.625 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.569 | 0.978 | -2.626 | -5.707 | 10.526 | 7.525 | 2.473 | -0.461 | 5.777%
7 | 8.626 | 2.835 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.735 | 0.974 | -2.884 | -5.712 | 10.526 | 8.126 | 2.671 | -0.5 | 5.791%
8 | 9.059 | 2.978 | 0.95 | Z | moderate sun | 10.526 | 10.515 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.849 | 0.971 | -3.061 | -5.716 | 10.515 | 8.534 | 2.805 | -0.525 | 5.801%
9 | 9.181 | 3.018 | 0.95 | Z | moderate sun | 10.526 | 10.41 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.989 | -1.881 | 0.971 | -3.111 | -5.717 | 10.41 | 8.648 | 2.843 | -0.533 | 5.803%
10 | 9.23 | 3.034 | 0.95 | Z | moderate sun | 10.526 | 10.189 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.988 | -1.894 | 0.97 | -3.131 | -5.717 | 10.189 | 8.694 | 2.858 | -0.536 | 5.804%
11 | 9.261 | 3.044 | 0.95 | Z | moderate sun | 10.526 | 9.958 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.09 | 0.98 | -3.331 | -3.852 | 9.958 | 8.901 | 2.926 | -0.36 | 3.889%
12 | 9.292 | 3.054 | 0.95 | Z | moderate sun | 10.526 | 9.831 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.098 | 0.98 | -3.344 | -3.853 | 9.831 | 8.931 | 2.935 | -0.361 | 3.89%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 10.526 | 9.968 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.106 | 0.979 | -3.356 | -3.853 | 9.968 | 8.959 | 2.945 | -0.363 | 3.89%
14 | 9.338 | 3.069 | 0.95 | Z | moderate sun | 10.526 | 10.031 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.11 | 0.979 | -3.363 | -3.853 | 10.031 | 8.975 | 2.95 | -0.363 | 3.891%
15 | 9.404 | 3.091 | 0.95 | Z | moderate sun | 10.526 | 10.294 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.128 | 0.979 | -3.39 | -3.853 | 10.294 | 9.038 | 2.971 | -0.366 | 3.892%
16 | 9.594 | 3.153 | 0.95 | Z | moderate sun | 10.526 | 10.473 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.179 | 0.978 | -3.469 | -3.854 | 10.473 | 9.22 | 3.031 | -0.374 | 3.894%
17 | 9.883 | 3.248 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.256 | 0.976 | -3.589 | -3.856 | 10.526 | 9.498 | 3.122 | -0.385 | 3.899%
18 | 10 | 3.287 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.287 | 0.975 | -3.638 | -3.857 | 10.526 | 9.61 | 3.159 | -0.39 | 3.901%
19 | 9.966 | 3.276 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.278 | 0.976 | -3.624 | -3.857 | 10.526 | 9.577 | 3.148 | -0.389 | 3.9%
20 | 9.857 | 3.24 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.249 | 0.976 | -3.578 | -3.856 | 10.526 | 9.473 | 3.114 | -0.384 | 3.898%
21 | 9.62 | 3.162 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.186 | 0.978 | -3.48 | -3.855 | 10.526 | 9.245 | 3.039 | -0.375 | 3.895%
22 | 9.139 | 3.004 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.87 | 0.971 | -3.093 | -5.717 | 10.526 | 8.609 | 2.83 | -0.53 | 5.802%
23 | 8.547 | 2.809 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.715 | 0.974 | -2.852 | -5.712 | 10.526 | 8.052 | 2.647 | -0.495 | 5.789%
24 | 8.047 | 2.645 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.584 | 0.977 | -2.65 | -5.708 | 10.526 | 7.582 | 2.492 | -0.465 | 5.779%
1 | 7.716 | 2.536 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.498 | 0.979 | -2.517 | -5.705 | 10.526 | 7.271 | 2.39 | -0.445 | 5.772%
2 | 7.517 | 2.471 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.266 | 0.971 | -2.256 | -7.525 | 10.526 | 6.942 | 2.282 | -0.575 | 7.652%
3 | 7.407 | 2.435 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.238 | 0.971 | -2.213 | -7.523 | 10.526 | 6.84 | 2.248 | -0.567 | 7.649%
4 | 7.398 | 2.432 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.235 | 0.971 | -2.209 | -7.523 | 10.526 | 6.832 | 2.246 | -0.566 | 7.648%
5 | 7.563 | 2.486 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.985 | -1.277 | 0.97 | -2.274 | -7.525 | 10.526 | 6.984 | 2.296 | -0.579 | 7.653%
6 | 7.986 | 2.625 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.569 | 0.978 | -2.626 | -5.707 | 10.526 | 7.525 | 2.473 | -0.461 | 5.777%
7 | 8.626 | 2.835 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.735 | 0.974 | -2.884 | -5.712 | 10.526 | 8.126 | 2.671 | -0.5 | 5.791%
8 | 9.059 | 2.978 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.849 | 0.971 | -3.061 | -5.716 | 10.526 | 8.534 | 2.805 | -0.525 | 5.801%
9 | 9.181 | 3.018 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.989 | -1.881 | 0.971 | -3.111 | -5.717 | 10.526 | 8.648 | 2.843 | -0.533 | 5.803%
10 | 9.23 | 3.034 | 0.95 | Z | cloudy | 10.526 | 10.515 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.988 | -1.894 | 0.97 | -3.131 | -5.717 | 10.515 | 8.694 | 2.858 | -0.536 | 5.804%
11 | 9.261 | 3.044 | 0.95 | Z | cloudy | 10.526 | 10.484 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.09 | 0.98 | -3.331 | -3.852 | 10.484 | 8.901 | 2.926 | -0.36 | 3.889%
12 | 9.292 | 3.054 | 0.95 | Z | cloudy | 10.526 | 10.452 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.098 | 0.98 | -3.344 | -3.853 | 10.452 | 8.931 | 2.935 | -0.361 | 3.89%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 10.526 | 10.452 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.106 | 0.979 | -3.356 | -3.853 | 10.452 | 8.959 | 2.945 | -0.363 | 3.89%
14 | 9.338 | 3.069 | 0.95 | Z | cloudy | 10.526 | 10.473 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.11 | 0.979 | -3.363 | -3.853 | 10.473 | 8.975 | 2.95 | -0.363 | 3.891%
15 | 9.404 | 3.091 | 0.95 | Z | cloudy | 10.526 | 10.505 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.128 | 0.979 | -3.39 | -3.853 | 10.505 | 9.038 | 2.971 | -0.366 | 3.892%
16 | 9.594 | 3.153 | 0.95 | Z | cloudy | 10.526 | 10.515 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.179 | 0.978 | -3.469 | -3.854 | 10.515 | 9.22 | 3.031 | -0.374 | 3.894%
17 | 9.883 | 3.248 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.256 | 0.976 | -3.589 | -3.856 | 10.526 | 9.498 | 3.122 | -0.385 | 3.899%
18 | 10 | 3.287 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.287 | 0.975 | -3.638 | -3.857 | 10.526 | 9.61 | 3.159 | -0.39 | 3.901%
19 | 9.966 | 3.276 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.278 | 0.976 | -3.624 | -3.857 | 10.526 | 9.577 | 3.148 | -0.389 | 3.9%
20 | 9.857 | 3.24 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.249 | 0.976 | -3.578 | -3.856 | 10.526 | 9.473 | 3.114 | -0.384 | 3.898%
21 | 9.62 | 3.162 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.186 | 0.978 | -3.48 | -3.855 | 10.526 | 9.245 | 3.039 | -0.375 | 3.895%
22 | 9.139 | 3.004 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.87 | 0.971 | -3.093 | -5.717 | 10.526 | 8.609 | 2.83 | -0.53 | 5.802%
23 | 8.547 | 2.809 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.715 | 0.974 | -2.852 | -5.712 | 10.526 | 8.052 | 2.647 | -0.495 | 5.789%
24 | 8.047 | 2.645 | 0.95 | Z | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.584 | 0.977 | -2.65 | -5.708 | 10.526 | 7.582 | 2.492 | -0.465 | 5.779%
1 | 7.716 | 2.536 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.213 | 0.97 | -2.213 | -4.888 | 5.263 | 7.133 | 2.345 | -0.583 | 7.551%
2 | 7.517 | 2.471 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.11 | 0.97 | -2.11 | -5.027 | 5.263 | 6.933 | 2.279 | -0.584 | 7.767%
3 | 7.407 | 2.435 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.054 | 0.97 | -2.054 | -5.104 | 5.263 | 6.823 | 2.243 | -0.584 | 7.886%
4 | 7.398 | 2.432 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.049 | 0.97 | -2.049 | -5.11 | 5.263 | 6.814 | 2.24 | -0.584 | 7.896%
5 | 7.563 | 2.486 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.995 | 5.263 | 6.979 | 2.294 | -0.584 | 7.718%
6 | 7.986 | 2.625 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.354 | 0.97 | -2.354 | -4.696 | 5.263 | 7.407 | 2.434 | -0.579 | 7.255%
7 | 8.626 | 2.835 | 0.95 | Z | very sunny | 5.263 | 5.252 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.691 | 0.97 | -2.691 | -4.235 | 5.252 | 8.062 | 2.65 | -0.564 | 6.541%
8 | 9.059 | 2.978 | 0.95 | Z | very sunny | 5.263 | 5.116 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -2.924 | 0.97 | -2.924 | -3.916 | 5.116 | 8.511 | 2.797 | -0.548 | 6.047%
9 | 9.181 | 3.018 | 0.95 | Z | very sunny | 5.263 | 4.705 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -2.989 | 0.97 | -2.989 | -3.825 | 4.705 | 8.639 | 2.839 | -0.542 | 5.907%
10 | 9.23 | 3.034 | 0.95 | Z | very sunny | 5.263 | 4.142 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.788 | 4.142 | 8.69 | 2.856 | -0.54 | 5.85%
11 | 9.261 | 3.044 | 0.95 | Z | very sunny | 5.263 | 3.574 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.972 | -3.068 | 0.972 | -3.068 | -3.574 | 3.574 | 8.75 | 2.876 | -0.511 | 5.513%
12 | 9.292 | 3.054 | 0.95 | Z | very sunny | 5.263 | 3.258 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.974 | -3.139 | 0.974 | -3.139 | -3.258 | 3.258 | 8.826 | 2.901 | -0.466 | 5.016%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 5.263 | 3.353 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.973 | -3.134 | 0.973 | -3.134 | -3.353 | 3.353 | 8.84 | 2.906 | -0.482 | 5.166%
14 | 9.338 | 3.069 | 0.95 | Z | very sunny | 5.263 | 3.505 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.972 | -3.112 | 0.972 | -3.112 | -3.505 | 3.505 | 8.833 | 2.903 | -0.505 | 5.407%
15 | 9.404 | 3.091 | 0.95 | Z | very sunny | 5.263 | 3.942 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.111 | 0.97 | -3.111 | -3.657 | 3.942 | 8.873 | 2.916 | -0.531 | 5.647%
16 | 9.594 | 3.153 | 0.95 | Z | very sunny | 5.263 | 4.458 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.214 | 0.97 | -3.214 | -3.513 | 4.458 | 9.074 | 2.982 | -0.52 | 5.425%
17 | 9.883 | 3.248 | 0.95 | Z | very sunny | 5.263 | 4.921 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.374 | 0.97 | -3.374 | -3.292 | 4.921 | 9.381 | 3.083 | -0.502 | 5.083%
18 | 10 | 3.287 | 0.95 | Z | very sunny | 5.263 | 5.189 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.438 | 0.97 | -3.438 | -3.202 | 5.189 | 9.506 | 3.124 | -0.494 | 4.943%
19 | 9.966 | 3.276 | 0.95 | Z | very sunny | 5.263 | 5.258 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.42 | 0.97 | -3.42 | -3.228 | 5.258 | 9.469 | 3.112 | -0.497 | 4.984%
20 | 9.857 | 3.24 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.359 | 0.97 | -3.359 | -3.312 | 5.263 | 9.353 | 3.074 | -0.504 | 5.114%
21 | 9.62 | 3.162 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.229 | 0.97 | -3.229 | -3.493 | 5.263 | 9.101 | 2.991 | -0.519 | 5.394%
22 | 9.139 | 3.004 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -2.967 | 0.97 | -2.967 | -3.856 | 5.263 | 8.595 | 2.825 | -0.544 | 5.955%
23 | 8.547 | 2.809 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.649 | 0.97 | -2.649 | -4.292 | 5.263 | 7.98 | 2.623 | -0.567 | 6.63%
24 | 8.047 | 2.645 | 0.95 | Z | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.386 | 0.97 | -2.386 | -4.653 | 5.263 | 7.469 | 2.455 | -0.578 | 7.188%
1 | 7.716 | 2.536 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.213 | 0.97 | -2.213 | -4.888 | 5.263 | 7.133 | 2.345 | -0.583 | 7.551%
2 | 7.517 | 2.471 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.11 | 0.97 | -2.11 | -5.027 | 5.263 | 6.933 | 2.279 | -0.584 | 7.767%
3 | 7.407 | 2.435 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.054 | 0.97 | -2.054 | -5.104 | 5.263 | 6.823 | 2.243 | -0.584 | 7.886%
4 | 7.398 | 2.432 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.049 | 0.97 | -2.049 | -5.11 | 5.263 | 6.814 | 2.24 | -0.584 | 7.896%
5 | 7.563 | 2.486 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.995 | 5.263 | 6.979 | 2.294 | -0.584 | 7.718%
6 | 7.986 | 2.625 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.354 | 0.97 | -2.354 | -4.696 | 5.263 | 7.407 | 2.434 | -0.579 | 7.255%
7 | 8.626 | 2.835 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.691 | 0.97 | -2.691 | -4.235 | 5.263 | 8.062 | 2.65 | -0.564 | 6.541%
8 | 9.059 | 2.978 | 0.95 | Z | moderate sun | 5.263 | 5.258 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -2.924 | 0.97 | -2.924 | -3.916 | 5.258 | 8.511 | 2.797 | -0.548 | 6.047%
9 | 9.181 | 3.018 | 0.95 | Z | moderate sun | 5.263 | 5.205 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -2.989 | 0.97 | -2.989 | -3.825 | 5.205 | 8.639 | 2.839 | -0.542 | 5.907%
10 | 9.23 | 3.034 | 0.95 | Z | moderate sun | 5.263 | 5.095 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.788 | 5.095 | 8.69 | 2.856 | -0.54 | 5.85%
11 | 9.261 | 3.044 | 0.95 | Z | moderate sun | 5.263 | 4.979 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.033 | 0.97 | -3.033 | -3.765 | 4.979 | 8.723 | 2.867 | -0.538 | 5.814%
12 | 9.292 | 3.054 | 0.95 | Z | moderate sun | 5.263 | 4.916 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.05 | 0.97 | -3.05 | -3.741 | 4.916 | 8.755 | 2.878 | -0.537 | 5.778%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 5.263 | 4.984 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.066 | 0.97 | -3.066 | -3.719 | 4.984 | 8.787 | 2.888 | -0.535 | 5.743%
14 | 9.338 | 3.069 | 0.95 | Z | moderate sun | 5.263 | 5.016 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.075 | 0.97 | -3.075 | -3.707 | 5.016 | 8.803 | 2.894 | -0.535 | 5.724%
15 | 9.404 | 3.091 | 0.95 | Z | moderate sun | 5.263 | 5.147 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.111 | 0.97 | -3.111 | -3.657 | 5.147 | 8.873 | 2.916 | -0.531 | 5.647%
16 | 9.594 | 3.153 | 0.95 | Z | moderate sun | 5.263 | 5.237 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.214 | 0.97 | -3.214 | -3.513 | 5.237 | 9.074 | 2.982 | -0.52 | 5.425%
17 | 9.883 | 3.248 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.374 | 0.97 | -3.374 | -3.292 | 5.263 | 9.381 | 3.083 | -0.502 | 5.083%
18 | 10 | 3.287 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.438 | 0.97 | -3.438 | -3.202 | 5.263 | 9.506 | 3.124 | -0.494 | 4.943%
19 | 9.966 | 3.276 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.42 | 0.97 | -3.42 | -3.228 | 5.263 | 9.469 | 3.112 | -0.497 | 4.984%
20 | 9.857 | 3.24 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.359 | 0.97 | -3.359 | -3.312 | 5.263 | 9.353 | 3.074 | -0.504 | 5.114%
21 | 9.62 | 3.162 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.229 | 0.97 | -3.229 | -3.493 | 5.263 | 9.101 | 2.991 | -0.519 | 5.394%
22 | 9.139 | 3.004 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -2.967 | 0.97 | -2.967 | -3.856 | 5.263 | 8.595 | 2.825 | -0.544 | 5.955%
23 | 8.547 | 2.809 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.649 | 0.97 | -2.649 | -4.292 | 5.263 | 7.98 | 2.623 | -0.567 | 6.63%
24 | 8.047 | 2.645 | 0.95 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.386 | 0.97 | -2.386 | -4.653 | 5.263 | 7.469 | 2.455 | -0.578 | 7.188%
1 | 7.716 | 2.536 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.213 | 0.97 | -2.213 | -4.888 | 5.263 | 7.133 | 2.345 | -0.583 | 7.551%
2 | 7.517 | 2.471 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.11 | 0.97 | -2.11 | -5.027 | 5.263 | 6.933 | 2.279 | -0.584 | 7.767%
3 | 7.407 | 2.435 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.054 | 0.97 | -2.054 | -5.104 | 5.263 | 6.823 | 2.243 | -0.584 | 7.886%
4 | 7.398 | 2.432 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.049 | 0.97 | -2.049 | -5.11 | 5.263 | 6.814 | 2.24 | -0.584 | 7.896%
5 | 7.563 | 2.486 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.995 | 5.263 | 6.979 | 2.294 | -0.584 | 7.718%
6 | 7.986 | 2.625 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.354 | 0.97 | -2.354 | -4.696 | 5.263 | 7.407 | 2.434 | -0.579 | 7.255%
7 | 8.626 | 2.835 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.691 | 0.97 | -2.691 | -4.235 | 5.263 | 8.062 | 2.65 | -0.564 | 6.541%
8 | 9.059 | 2.978 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -2.924 | 0.97 | -2.924 | -3.916 | 5.263 | 8.511 | 2.797 | -0.548 | 6.047%
9 | 9.181 | 3.018 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -2.989 | 0.97 | -2.989 | -3.825 | 5.263 | 8.639 | 2.839 | -0.542 | 5.907%
10 | 9.23 | 3.034 | 0.95 | Z | cloudy | 5.263 | 5.258 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.788 | 5.258 | 8.69 | 2.856 | -0.54 | 5.85%
11 | 9.261 | 3.044 | 0.95 | Z | cloudy | 5.263 | 5.242 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.033 | 0.97 | -3.033 | -3.765 | 5.242 | 8.723 | 2.867 | -0.538 | 5.814%
12 | 9.292 | 3.054 | 0.95 | Z | cloudy | 5.263 | 5.226 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.05 | 0.97 | -3.05 | -3.741 | 5.226 | 8.755 | 2.878 | -0.537 | 5.778%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 5.263 | 5.226 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.066 | 0.97 | -3.066 | -3.719 | 5.226 | 8.787 | 2.888 | -0.535 | 5.743%
14 | 9.338 | 3.069 | 0.95 | Z | cloudy | 5.263 | 5.237 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.075 | 0.97 | -3.075 | -3.707 | 5.237 | 8.803 | 2.894 | -0.535 | 5.724%
15 | 9.404 | 3.091 | 0.95 | Z | cloudy | 5.263 | 5.252 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.111 | 0.97 | -3.111 | -3.657 | 5.252 | 8.873 | 2.916 | -0.531 | 5.647%
16 | 9.594 | 3.153 | 0.95 | Z | cloudy | 5.263 | 5.258 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.214 | 0.97 | -3.214 | -3.513 | 5.258 | 9.074 | 2.982 | -0.52 | 5.425%
17 | 9.883 | 3.248 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.374 | 0.97 | -3.374 | -3.292 | 5.263 | 9.381 | 3.083 | -0.502 | 5.083%
18 | 10 | 3.287 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.438 | 0.97 | -3.438 | -3.202 | 5.263 | 9.506 | 3.124 | -0.494 | 4.943%
19 | 9.966 | 3.276 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.42 | 0.97 | -3.42 | -3.228 | 5.263 | 9.469 | 3.112 | -0.497 | 4.984%
20 | 9.857 | 3.24 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.359 | 0.97 | -3.359 | -3.312 | 5.263 | 9.353 | 3.074 | -0.504 | 5.114%
21 | 9.62 | 3.162 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.229 | 0.97 | -3.229 | -3.493 | 5.263 | 9.101 | 2.991 | -0.519 | 5.394%
22 | 9.139 | 3.004 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -2.967 | 0.97 | -2.967 | -3.856 | 5.263 | 8.595 | 2.825 | -0.544 | 5.955%
23 | 8.547 | 2.809 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.649 | 0.97 | -2.649 | -4.292 | 5.263 | 7.98 | 2.623 | -0.567 | 6.63%
24 | 8.047 | 2.645 | 0.95 | Z | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.386 | 0.97 | -2.386 | -4.653 | 5.263 | 7.469 | 2.455 | -0.578 | 7.188%
1 | 7.716 | 2.536 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.213 | 0.97 | -2.213 | -4.888 | 10.526 | 7.133 | 2.345 | -0.583 | 7.551%
2 | 7.517 | 2.471 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.11 | 0.97 | -2.11 | -5.027 | 10.526 | 6.933 | 2.279 | -0.584 | 7.767%
3 | 7.407 | 2.435 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.054 | 0.97 | -2.054 | -5.104 | 10.526 | 6.823 | 2.243 | -0.584 | 7.886%
4 | 7.398 | 2.432 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.049 | 0.97 | -2.049 | -5.11 | 10.526 | 6.814 | 2.24 | -0.584 | 7.896%
5 | 7.563 | 2.486 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.995 | 10.526 | 6.979 | 2.294 | -0.584 | 7.718%
6 | 7.986 | 2.625 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.354 | 0.97 | -2.354 | -4.696 | 10.526 | 7.407 | 2.434 | -0.579 | 7.255%
7 | 8.626 | 2.835 | 0.95 | Z | very sunny | 10.526 | 10.505 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.691 | 0.97 | -2.691 | -4.235 | 10.505 | 8.062 | 2.65 | -0.564 | 6.541%
8 | 9.059 | 2.978 | 0.95 | Z | very sunny | 10.526 | 10.231 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -2.924 | 0.97 | -2.924 | -3.916 | 10.231 | 8.511 | 2.797 | -0.548 | 6.047%
9 | 9.181 | 3.018 | 0.95 | Z | very sunny | 10.526 | 9.41 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -2.989 | 0.97 | -2.989 | -3.825 | 9.41 | 8.639 | 2.839 | -0.542 | 5.907%
10 | 9.23 | 3.034 | 0.95 | Z | very sunny | 10.526 | 8.284 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.788 | 8.284 | 8.69 | 2.856 | -0.54 | 5.85%
11 | 9.261 | 3.044 | 0.95 | Z | very sunny | 10.526 | 7.147 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.033 | 0.97 | -3.033 | -3.765 | 7.147 | 8.723 | 2.867 | -0.538 | 5.814%
12 | 9.292 | 3.054 | 0.95 | Z | very sunny | 10.526 | 6.516 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.05 | 0.97 | -3.05 | -3.741 | 6.516 | 8.755 | 2.878 | -0.537 | 5.778%
13 | 9.322 | 3.064 | 0.95 | Z | very sunny | 10.526 | 6.705 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.066 | 0.97 | -3.066 | -3.719 | 6.705 | 8.787 | 2.888 | -0.535 | 5.743%
14 | 9.338 | 3.069 | 0.95 | Z | very sunny | 10.526 | 7.01 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.075 | 0.97 | -3.075 | -3.707 | 7.01 | 8.803 | 2.894 | -0.535 | 5.724%
15 | 9.404 | 3.091 | 0.95 | Z | very sunny | 10.526 | 7.884 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.111 | 0.97 | -3.111 | -3.657 | 7.884 | 8.873 | 2.916 | -0.531 | 5.647%
16 | 9.594 | 3.153 | 0.95 | Z | very sunny | 10.526 | 8.916 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.214 | 0.97 | -3.214 | -3.513 | 8.916 | 9.074 | 2.982 | -0.52 | 5.425%
17 | 9.883 | 3.248 | 0.95 | Z | very sunny | 10.526 | 9.842 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.374 | 0.97 | -3.374 | -3.292 | 9.842 | 9.381 | 3.083 | -0.502 | 5.083%
18 | 10 | 3.287 | 0.95 | Z | very sunny | 10.526 | 10.379 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.438 | 0.97 | -3.438 | -3.202 | 10.379 | 9.506 | 3.124 | -0.494 | 4.943%
19 | 9.966 | 3.276 | 0.95 | Z | very sunny | 10.526 | 10.515 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.42 | 0.97 | -3.42 | -3.228 | 10.515 | 9.469 | 3.112 | -0.497 | 4.984%
20 | 9.857 | 3.24 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.359 | 0.97 | -3.359 | -3.312 | 10.526 | 9.353 | 3.074 | -0.504 | 5.114%
21 | 9.62 | 3.162 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.229 | 0.97 | -3.229 | -3.493 | 10.526 | 9.101 | 2.991 | -0.519 | 5.394%
22 | 9.139 | 3.004 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -2.967 | 0.97 | -2.967 | -3.856 | 10.526 | 8.595 | 2.825 | -0.544 | 5.955%
23 | 8.547 | 2.809 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.649 | 0.97 | -2.649 | -4.292 | 10.526 | 7.98 | 2.623 | -0.567 | 6.63%
24 | 8.047 | 2.645 | 0.95 | Z | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.386 | 0.97 | -2.386 | -4.653 | 10.526 | 7.469 | 2.455 | -0.578 | 7.188%
1 | 7.716 | 2.536 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.213 | 0.97 | -2.213 | -4.888 | 10.526 | 7.133 | 2.345 | -0.583 | 7.551%
2 | 7.517 | 2.471 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.11 | 0.97 | -2.11 | -5.027 | 10.526 | 6.933 | 2.279 | -0.584 | 7.767%
3 | 7.407 | 2.435 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.054 | 0.97 | -2.054 | -5.104 | 10.526 | 6.823 | 2.243 | -0.584 | 7.886%
4 | 7.398 | 2.432 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.049 | 0.97 | -2.049 | -5.11 | 10.526 | 6.814 | 2.24 | -0.584 | 7.896%
5 | 7.563 | 2.486 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.995 | 10.526 | 6.979 | 2.294 | -0.584 | 7.718%
6 | 7.986 | 2.625 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.354 | 0.97 | -2.354 | -4.696 | 10.526 | 7.407 | 2.434 | -0.579 | 7.255%
7 | 8.626 | 2.835 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.691 | 0.97 | -2.691 | -4.235 | 10.526 | 8.062 | 2.65 | -0.564 | 6.541%
8 | 9.059 | 2.978 | 0.95 | Z | moderate sun | 10.526 | 10.515 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -2.924 | 0.97 | -2.924 | -3.916 | 10.515 | 8.511 | 2.797 | -0.548 | 6.047%
9 | 9.181 | 3.018 | 0.95 | Z | moderate sun | 10.526 | 10.41 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -2.989 | 0.97 | -2.989 | -3.825 | 10.41 | 8.639 | 2.839 | -0.542 | 5.907%
10 | 9.23 | 3.034 | 0.95 | Z | moderate sun | 10.526 | 10.189 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.788 | 10.189 | 8.69 | 2.856 | -0.54 | 5.85%
11 | 9.261 | 3.044 | 0.95 | Z | moderate sun | 10.526 | 9.958 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.033 | 0.97 | -3.033 | -3.765 | 9.958 | 8.723 | 2.867 | -0.538 | 5.814%
12 | 9.292 | 3.054 | 0.95 | Z | moderate sun | 10.526 | 9.831 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.05 | 0.97 | -3.05 | -3.741 | 9.831 | 8.755 | 2.878 | -0.537 | 5.778%
13 | 9.322 | 3.064 | 0.95 | Z | moderate sun | 10.526 | 9.968 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.066 | 0.97 | -3.066 | -3.719 | 9.968 | 8.787 | 2.888 | -0.535 | 5.743%
14 | 9.338 | 3.069 | 0.95 | Z | moderate sun | 10.526 | 10.031 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.075 | 0.97 | -3.075 | -3.707 | 10.031 | 8.803 | 2.894 | -0.535 | 5.724%
15 | 9.404 | 3.091 | 0.95 | Z | moderate sun | 10.526 | 10.294 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.111 | 0.97 | -3.111 | -3.657 | 10.294 | 8.873 | 2.916 | -0.531 | 5.647%
16 | 9.594 | 3.153 | 0.95 | Z | moderate sun | 10.526 | 10.473 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.214 | 0.97 | -3.214 | -3.513 | 10.473 | 9.074 | 2.982 | -0.52 | 5.425%
17 | 9.883 | 3.248 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.374 | 0.97 | -3.374 | -3.292 | 10.526 | 9.381 | 3.083 | -0.502 | 5.083%
18 | 10 | 3.287 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.438 | 0.97 | -3.438 | -3.202 | 10.526 | 9.506 | 3.124 | -0.494 | 4.943%
19 | 9.966 | 3.276 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.42 | 0.97 | -3.42 | -3.228 | 10.526 | 9.469 | 3.112 | -0.497 | 4.984%
20 | 9.857 | 3.24 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.359 | 0.97 | -3.359 | -3.312 | 10.526 | 9.353 | 3.074 | -0.504 | 5.114%
21 | 9.62 | 3.162 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.229 | 0.97 | -3.229 | -3.493 | 10.526 | 9.101 | 2.991 | -0.519 | 5.394%
22 | 9.139 | 3.004 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -2.967 | 0.97 | -2.967 | -3.856 | 10.526 | 8.595 | 2.825 | -0.544 | 5.955%
23 | 8.547 | 2.809 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.649 | 0.97 | -2.649 | -4.292 | 10.526 | 7.98 | 2.623 | -0.567 | 6.63%
24 | 8.047 | 2.645 | 0.95 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.386 | 0.97 | -2.386 | -4.653 | 10.526 | 7.469 | 2.455 | -0.578 | 7.188%
1 | 7.716 | 2.536 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.213 | 0.97 | -2.213 | -4.888 | 10.526 | 7.133 | 2.345 | -0.583 | 7.551%
2 | 7.517 | 2.471 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.11 | 0.97 | -2.11 | -5.027 | 10.526 | 6.933 | 2.279 | -0.584 | 7.767%
3 | 7.407 | 2.435 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.054 | 0.97 | -2.054 | -5.104 | 10.526 | 6.823 | 2.243 | -0.584 | 7.886%
4 | 7.398 | 2.432 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.049 | 0.97 | -2.049 | -5.11 | 10.526 | 6.814 | 2.24 | -0.584 | 7.896%
5 | 7.563 | 2.486 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.134 | 0.97 | -2.134 | -4.995 | 10.526 | 6.979 | 2.294 | -0.584 | 7.718%
6 | 7.986 | 2.625 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.354 | 0.97 | -2.354 | -4.696 | 10.526 | 7.407 | 2.434 | -0.579 | 7.255%
7 | 8.626 | 2.835 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.691 | 0.97 | -2.691 | -4.235 | 10.526 | 8.062 | 2.65 | -0.564 | 6.541%
8 | 9.059 | 2.978 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -2.924 | 0.97 | -2.924 | -3.916 | 10.526 | 8.511 | 2.797 | -0.548 | 6.047%
9 | 9.181 | 3.018 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -2.989 | 0.97 | -2.989 | -3.825 | 10.526 | 8.639 | 2.839 | -0.542 | 5.907%
10 | 9.23 | 3.034 | 0.95 | Z | cloudy | 10.526 | 10.515 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.016 | 0.97 | -3.016 | -3.788 | 10.515 | 8.69 | 2.856 | -0.54 | 5.85%
11 | 9.261 | 3.044 | 0.95 | Z | cloudy | 10.526 | 10.484 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.033 | 0.97 | -3.033 | -3.765 | 10.484 | 8.723 | 2.867 | -0.538 | 5.814%
12 | 9.292 | 3.054 | 0.95 | Z | cloudy | 10.526 | 10.452 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.05 | 0.97 | -3.05 | -3.741 | 10.452 | 8.755 | 2.878 | -0.537 | 5.778%
13 | 9.322 | 3.064 | 0.95 | Z | cloudy | 10.526 | 10.452 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.066 | 0.97 | -3.066 | -3.719 | 10.452 | 8.787 | 2.888 | -0.535 | 5.743%
14 | 9.338 | 3.069 | 0.95 | Z | cloudy | 10.526 | 10.473 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.075 | 0.97 | -3.075 | -3.707 | 10.473 | 8.803 | 2.894 | -0.535 | 5.724%
15 | 9.404 | 3.091 | 0.95 | Z | cloudy | 10.526 | 10.505 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.111 | 0.97 | -3.111 | -3.657 | 10.505 | 8.873 | 2.916 | -0.531 | 5.647%
16 | 9.594 | 3.153 | 0.95 | Z | cloudy | 10.526 | 10.515 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.214 | 0.97 | -3.214 | -3.513 | 10.515 | 9.074 | 2.982 | -0.52 | 5.425%
17 | 9.883 | 3.248 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.374 | 0.97 | -3.374 | -3.292 | 10.526 | 9.381 | 3.083 | -0.502 | 5.083%
18 | 10 | 3.287 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.438 | 0.97 | -3.438 | -3.202 | 10.526 | 9.506 | 3.124 | -0.494 | 4.943%
19 | 9.966 | 3.276 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.42 | 0.97 | -3.42 | -3.228 | 10.526 | 9.469 | 3.112 | -0.497 | 4.984%
20 | 9.857 | 3.24 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.359 | 0.97 | -3.359 | -3.312 | 10.526 | 9.353 | 3.074 | -0.504 | 5.114%
21 | 9.62 | 3.162 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.229 | 0.97 | -3.229 | -3.493 | 10.526 | 9.101 | 2.991 | -0.519 | 5.394%
22 | 9.139 | 3.004 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -2.967 | 0.97 | -2.967 | -3.856 | 10.526 | 8.595 | 2.825 | -0.544 | 5.955%
23 | 8.547 | 2.809 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.649 | 0.97 | -2.649 | -4.292 | 10.526 | 7.98 | 2.623 | -0.567 | 6.63%
24 | 8.047 | 2.645 | 0.95 | Z | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.386 | 0.97 | -2.386 | -4.653 | 10.526 | 7.469 | 2.455 | -0.578 | 7.188%
1 | 7.716 | 1.567 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.937 | 1.004 | -3.041 | -5.263 | 5.263 | 7.518 | 1.527 | -0.198 | 2.566%
2 | 7.517 | 1.526 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.03 | -0.91 | 1.005 | -2.957 | -5.263 | 5.263 | 7.324 | 1.487 | -0.193 | 2.565%
3 | 7.407 | 1.504 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.895 | 1.005 | -2.911 | -5.263 | 5.263 | 7.217 | 1.465 | -0.19 | 2.565%
4 | 7.398 | 1.502 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.894 | 1.005 | -2.907 | -5.263 | 5.263 | 7.208 | 1.464 | -0.19 | 2.565%
5 | 7.563 | 1.536 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.916 | 1.004 | -2.976 | -5.263 | 5.263 | 7.369 | 1.496 | -0.194 | 2.565%
6 | 7.986 | 1.622 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.974 | 1.002 | -3.155 | -5.263 | 5.263 | 7.781 | 1.58 | -0.205 | 2.566%
7 | 8.626 | 1.752 | 0.98 | Z | very sunny | 5.263 | 5.252 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.063 | 0.999 | -3.428 | -5.252 | 5.252 | 8.406 | 1.707 | -0.22 | 2.551%
8 | 9.059 | 1.84 | 0.98 | Z | very sunny | 5.263 | 5.116 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.127 | 0.998 | -3.616 | -5.116 | 5.116 | 8.834 | 1.794 | -0.225 | 2.484%
9 | 9.181 | 1.864 | 0.98 | Z | very sunny | 5.263 | 4.705 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.029 | -1.155 | 0.998 | -3.68 | -4.705 | 4.705 | 8.971 | 1.822 | -0.21 | 2.282%
10 | 9.23 | 1.874 | 0.98 | Z | very sunny | 5.263 | 4.142 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.03 | -1.177 | 0.999 | -3.716 | -4.142 | 4.142 | 9.045 | 1.837 | -0.185 | 2.007%
11 | 9.261 | 1.881 | 0.98 | Z | very sunny | 5.263 | 3.574 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.032 | -1.195 | 1 | -3.744 | -3.574 | 3.574 | 9.099 | 1.848 | -0.162 | 1.745%
12 | 9.292 | 1.887 | 0.98 | Z | very sunny | 5.263 | 3.258 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.032 | -1.208 | 1.001 | -3.766 | -3.258 | 3.258 | 9.144 | 1.857 | -0.148 | 1.59%
13 | 9.322 | 1.893 | 0.98 | Z | very sunny | 5.263 | 3.353 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.032 | -1.211 | 1.001 | -3.777 | -3.353 | 3.353 | 9.171 | 1.862 | -0.151 | 1.618%
14 | 9.338 | 1.896 | 0.98 | Z | very sunny | 5.263 | 3.505 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.032 | -1.209 | 1 | -3.78 | -3.505 | 3.505 | 9.18 | 1.864 | -0.158 | 1.693%
15 | 9.404 | 1.91 | 0.98 | Z | very sunny | 5.263 | 3.942 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.031 | -1.206 | 0.999 | -3.796 | -3.942 | 3.942 | 9.225 | 1.873 | -0.179 | 1.907%
16 | 9.594 | 1.948 | 0.98 | Z | very sunny | 5.263 | 4.458 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.029 | -1.219 | 0.997 | -3.864 | -4.458 | 4.458 | 9.387 | 1.906 | -0.207 | 2.161%
17 | 9.883 | 2.007 | 0.98 | Z | very sunny | 5.263 | 4.921 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.027 | -1.246 | 0.994 | -3.976 | -4.921 | 4.921 | 9.646 | 1.959 | -0.237 | 2.398%
18 | 10 | 2.031 | 0.98 | Z | very sunny | 5.263 | 5.189 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.027 | -1.254 | 0.993 | -4.019 | -5.189 | 5.189 | 9.747 | 1.979 | -0.253 | 2.533%
19 | 9.966 | 2.024 | 0.98 | Z | very sunny | 5.263 | 5.258 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.248 | 0.993 | -4.002 | -5.258 | 5.258 | 9.71 | 1.972 | -0.256 | 2.567%
20 | 9.857 | 2.002 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.027 | -1.233 | 0.993 | -3.955 | -5.263 | 5.263 | 9.604 | 1.95 | -0.253 | 2.569%
21 | 9.62 | 1.953 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.2 | 0.994 | -3.853 | -5.263 | 5.263 | 9.373 | 1.903 | -0.247 | 2.569%
22 | 9.139 | 1.856 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.133 | 0.997 | -3.646 | -5.263 | 5.263 | 8.904 | 1.808 | -0.235 | 2.568%
23 | 8.547 | 1.736 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.051 | 1 | -3.393 | -5.263 | 5.263 | 8.328 | 1.691 | -0.219 | 2.567%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.983 | 1.002 | -3.181 | -5.263 | 5.263 | 7.841 | 1.592 | -0.206 | 2.566%
1 | 7.716 | 1.567 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.937 | 1.004 | -3.041 | -5.263 | 5.263 | 7.518 | 1.527 | -0.198 | 2.565%
2 | 7.517 | 1.526 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.03 | -0.91 | 1.005 | -2.957 | -5.263 | 5.263 | 7.324 | 1.487 | -0.193 | 2.565%
3 | 7.407 | 1.504 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.895 | 1.005 | -2.911 | -5.263 | 5.263 | 7.217 | 1.465 | -0.19 | 2.565%
4 | 7.398 | 1.502 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.894 | 1.005 | -2.907 | -5.263 | 5.263 | 7.208 | 1.464 | -0.19 | 2.565%
5 | 7.563 | 1.536 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.916 | 1.004 | -2.976 | -5.263 | 5.263 | 7.369 | 1.496 | -0.194 | 2.565%
6 | 7.986 | 1.622 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.974 | 1.002 | -3.155 | -5.263 | 5.263 | 7.781 | 1.58 | -0.205 | 2.566%
7 | 8.626 | 1.752 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.062 | 0.999 | -3.427 | -5.263 | 5.263 | 8.405 | 1.707 | -0.221 | 2.567%
8 | 9.059 | 1.84 | 0.98 | Z | moderate sun | 5.263 | 5.258 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.122 | 0.997 | -3.612 | -5.258 | 5.258 | 8.827 | 1.792 | -0.232 | 2.565%
9 | 9.181 | 1.864 | 0.98 | Z | moderate sun | 5.263 | 5.205 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.028 | -1.141 | 0.997 | -3.666 | -5.205 | 5.205 | 8.948 | 1.817 | -0.233 | 2.539%
10 | 9.23 | 1.874 | 0.98 | Z | moderate sun | 5.263 | 5.095 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.028 | -1.151 | 0.997 | -3.69 | -5.095 | 5.095 | 9.002 | 1.828 | -0.228 | 2.474%
11 | 9.261 | 1.881 | 0.98 | Z | moderate sun | 5.263 | 4.979 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.028 | -1.158 | 0.997 | -3.707 | -4.979 | 4.979 | 9.037 | 1.835 | -0.224 | 2.417%
12 | 9.292 | 1.887 | 0.98 | Z | moderate sun | 5.263 | 4.916 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.028 | -1.164 | 0.997 | -3.722 | -4.916 | 4.916 | 9.07 | 1.842 | -0.222 | 2.386%
13 | 9.322 | 1.893 | 0.98 | Z | moderate sun | 5.263 | 4.984 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.028 | -1.167 | 0.997 | -3.733 | -4.984 | 4.984 | 9.096 | 1.847 | -0.226 | 2.42%
14 | 9.338 | 1.896 | 0.98 | Z | moderate sun | 5.263 | 5.016 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.028 | -1.168 | 0.996 | -3.739 | -5.016 | 5.016 | 9.111 | 1.85 | -0.227 | 2.436%
15 | 9.404 | 1.91 | 0.98 | Z | moderate sun | 5.263 | 5.147 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.027 | -1.174 | 0.996 | -3.764 | -5.147 | 5.147 | 9.169 | 1.862 | -0.235 | 2.501%
16 | 9.594 | 1.948 | 0.98 | Z | moderate sun | 5.263 | 5.237 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.027 | -1.197 | 0.995 | -3.843 | -5.237 | 5.237 | 9.35 | 1.899 | -0.244 | 2.545%
17 | 9.883 | 2.007 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.026 | -1.236 | 0.993 | -3.966 | -5.263 | 5.263 | 9.629 | 1.955 | -0.254 | 2.569%
18 | 10 | 2.031 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.252 | 0.992 | -4.017 | -5.263 | 5.263 | 9.743 | 1.978 | -0.257 | 2.57%
19 | 9.966 | 2.024 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.248 | 0.993 | -4.002 | -5.263 | 5.263 | 9.71 | 1.972 | -0.256 | 2.57%
20 | 9.857 | 2.002 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.027 | -1.233 | 0.993 | -3.955 | -5.263 | 5.263 | 9.604 | 1.95 | -0.253 | 2.569%
21 | 9.62 | 1.953 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.2 | 0.994 | -3.853 | -5.263 | 5.263 | 9.373 | 1.903 | -0.247 | 2.569%
22 | 9.139 | 1.856 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.133 | 0.997 | -3.646 | -5.263 | 5.263 | 8.904 | 1.808 | -0.235 | 2.568%
23 | 8.547 | 1.736 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.051 | 1 | -3.393 | -5.263 | 5.263 | 8.328 | 1.691 | -0.219 | 2.567%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.983 | 1.002 | -3.181 | -5.263 | 5.263 | 7.841 | 1.592 | -0.206 | 2.566%
1 | 7.716 | 1.567 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.937 | 1.004 | -3.041 | -5.263 | 5.263 | 7.518 | 1.527 | -0.198 | 2.565%
2 | 7.517 | 1.526 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.03 | -0.91 | 1.005 | -2.957 | -5.263 | 5.263 | 7.324 | 1.487 | -0.193 | 2.565%
3 | 7.407 | 1.504 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.895 | 1.005 | -2.911 | -5.263 | 5.263 | 7.217 | 1.465 | -0.19 | 2.565%
4 | 7.398 | 1.502 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.894 | 1.005 | -2.907 | -5.263 | 5.263 | 7.208 | 1.464 | -0.19 | 2.565%
5 | 7.563 | 1.536 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.916 | 1.004 | -2.976 | -5.263 | 5.263 | 7.369 | 1.496 | -0.194 | 2.565%
6 | 7.986 | 1.622 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.974 | 1.002 | -3.155 | -5.263 | 5.263 | 7.781 | 1.58 | -0.205 | 2.566%
7 | 8.626 | 1.752 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.062 | 0.999 | -3.427 | -5.263 | 5.263 | 8.405 | 1.707 | -0.221 | 2.567%
8 | 9.059 | 1.84 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.122 | 0.997 | -3.612 | -5.263 | 5.263 | 8.826 | 1.792 | -0.233 | 2.568%
9 | 9.181 | 1.864 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.027 | -1.139 | 0.997 | -3.664 | -5.263 | 5.263 | 8.945 | 1.816 | -0.236 | 2.568%
10 | 9.23 | 1.874 | 0.98 | Z | cloudy | 5.263 | 5.258 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.027 | -1.146 | 0.996 | -3.685 | -5.258 | 5.258 | 8.993 | 1.826 | -0.237 | 2.565%
11 | 9.261 | 1.881 | 0.98 | Z | cloudy | 5.263 | 5.242 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.027 | -1.151 | 0.996 | -3.699 | -5.242 | 5.242 | 9.024 | 1.832 | -0.237 | 2.558%
12 | 9.292 | 1.887 | 0.98 | Z | cloudy | 5.263 | 5.226 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.027 | -1.155 | 0.996 | -3.713 | -5.226 | 5.226 | 9.055 | 1.839 | -0.237 | 2.55%
13 | 9.322 | 1.893 | 0.98 | Z | cloudy | 5.263 | 5.226 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.027 | -1.159 | 0.996 | -3.726 | -5.226 | 5.226 | 9.084 | 1.845 | -0.238 | 2.55%
14 | 9.338 | 1.896 | 0.98 | Z | cloudy | 5.263 | 5.237 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.027 | -1.162 | 0.996 | -3.733 | -5.237 | 5.237 | 9.1 | 1.848 | -0.238 | 2.544%
15 | 9.404 | 1.91 | 0.98 | Z | cloudy | 5.263 | 5.252 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.027 | -1.171 | 0.996 | -3.761 | -5.252 | 5.252 | 9.164 | 1.861 | -0.24 | 2.552%
16 | 9.594 | 1.948 | 0.98 | Z | cloudy | 5.263 | 5.258 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.027 | -1.196 | 0.995 | -3.842 | -5.258 | 5.258 | 9.348 | 1.898 | -0.246 | 2.566%
17 | 9.883 | 2.007 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.026 | -1.236 | 0.993 | -3.966 | -5.263 | 5.263 | 9.629 | 1.955 | -0.254 | 2.569%
18 | 10 | 2.031 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.252 | 0.992 | -4.017 | -5.263 | 5.263 | 9.743 | 1.978 | -0.257 | 2.57%
19 | 9.966 | 2.024 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.248 | 0.993 | -4.002 | -5.263 | 5.263 | 9.71 | 1.972 | -0.256 | 2.57%
20 | 9.857 | 2.002 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.027 | -1.233 | 0.993 | -3.955 | -5.263 | 5.263 | 9.604 | 1.95 | -0.253 | 2.569%
21 | 9.62 | 1.953 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.2 | 0.994 | -3.853 | -5.263 | 5.263 | 9.373 | 1.903 | -0.247 | 2.569%
22 | 9.139 | 1.856 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.133 | 0.997 | -3.646 | -5.263 | 5.263 | 8.904 | 1.808 | -0.235 | 2.568%
23 | 8.547 | 1.736 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.051 | 1 | -3.393 | -5.263 | 5.263 | 8.328 | 1.691 | -0.219 | 2.567%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.983 | 1.002 | -3.181 | -5.263 | 5.263 | 7.841 | 1.592 | -0.206 | 2.566%
1 | 7.716 | 1.567 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.795 | 0.99 | -2.898 | -10.526 | 10.526 | 7.316 | 1.486 | -0.4 | 5.182%
2 | 7.517 | 1.526 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.016 | -0.768 | 0.991 | -2.814 | -10.526 | 10.526 | 7.128 | 1.447 | -0.389 | 5.181%
3 | 7.407 | 1.504 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.753 | 0.992 | -2.768 | -10.526 | 10.526 | 7.023 | 1.426 | -0.384 | 5.181%
4 | 7.398 | 1.502 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.752 | 0.992 | -2.765 | -10.526 | 10.526 | 7.015 | 1.424 | -0.383 | 5.181%
5 | 7.563 | 1.536 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.016 | -0.774 | 0.991 | -2.834 | -10.526 | 10.526 | 7.171 | 1.456 | -0.392 | 5.181%
6 | 7.986 | 1.622 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.831 | 0.989 | -3.012 | -10.526 | 10.526 | 7.572 | 1.538 | -0.414 | 5.183%
7 | 8.626 | 1.752 | 0.98 | Z | very sunny | 10.526 | 10.505 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.919 | 0.986 | -3.284 | -10.505 | 10.505 | 8.181 | 1.661 | -0.445 | 5.157%
8 | 9.059 | 1.84 | 0.98 | Z | very sunny | 10.526 | 10.231 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.015 | -0.986 | 0.985 | -3.475 | -10.231 | 10.231 | 8.604 | 1.747 | -0.455 | 5.022%
9 | 9.181 | 1.864 | 0.98 | Z | very sunny | 10.526 | 9.41 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.017 | -1.025 | 0.986 | -3.55 | -9.41 | 9.41 | 8.758 | 1.778 | -0.423 | 4.613%
10 | 9.23 | 1.874 | 0.98 | Z | very sunny | 10.526 | 8.284 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.019 | -1.063 | 0.989 | -3.602 | -8.284 | 8.284 | 8.856 | 1.798 | -0.374 | 4.057%
11 | 9.261 | 1.881 | 0.98 | Z | very sunny | 10.526 | 7.147 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.022 | -1.098 | 0.991 | -3.646 | -7.147 | 7.147 | 8.936 | 1.815 | -0.325 | 3.507%
12 | 9.292 | 1.887 | 0.98 | Z | very sunny | 10.526 | 6.516 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.024 | -1.12 | 0.993 | -3.677 | -6.516 | 6.516 | 8.995 | 1.827 | -0.297 | 3.193%
13 | 9.322 | 1.893 | 0.98 | Z | very sunny | 10.526 | 6.705 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.024 | -1.12 | 0.992 | -3.686 | -6.705 | 6.705 | 9.017 | 1.831 | -0.305 | 3.27%
14 | 9.338 | 1.896 | 0.98 | Z | very sunny | 10.526 | 7.01 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.023 | -1.113 | 0.991 | -3.684 | -7.01 | 7.01 | 9.019 | 1.831 | -0.319 | 3.421%
15 | 9.404 | 1.91 | 0.98 | Z | very sunny | 10.526 | 7.884 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.02 | -1.098 | 0.989 | -3.688 | -7.884 | 7.884 | 9.041 | 1.836 | -0.363 | 3.855%
16 | 9.594 | 1.948 | 0.98 | Z | very sunny | 10.526 | 8.916 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.017 | -1.096 | 0.985 | -3.741 | -8.916 | 8.916 | 9.175 | 1.863 | -0.419 | 4.368%
17 | 9.883 | 2.007 | 0.98 | Z | very sunny | 10.526 | 9.842 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.014 | -1.108 | 0.981 | -3.839 | -9.842 | 9.842 | 9.404 | 1.91 | -0.479 | 4.846%
18 | 10 | 2.031 | 0.98 | Z | very sunny | 10.526 | 10.379 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.013 | -1.109 | 0.979 | -3.874 | -10.379 | 10.379 | 9.488 | 1.927 | -0.512 | 5.117%
19 | 9.966 | 2.024 | 0.98 | Z | very sunny | 10.526 | 10.515 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.101 | 0.979 | -3.855 | -10.515 | 10.515 | 9.449 | 1.919 | -0.517 | 5.186%
20 | 9.857 | 2.002 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.013 | -1.085 | 0.98 | -3.808 | -10.526 | 10.526 | 9.345 | 1.898 | -0.512 | 5.191%
21 | 9.62 | 1.953 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.053 | 0.981 | -3.706 | -10.526 | 10.526 | 9.121 | 1.852 | -0.499 | 5.19%
22 | 9.139 | 1.856 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.014 | -0.988 | 0.983 | -3.5 | -10.526 | 10.526 | 8.665 | 1.759 | -0.474 | 5.188%
23 | 8.547 | 1.736 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.907 | 0.986 | -3.249 | -10.526 | 10.526 | 8.104 | 1.646 | -0.443 | 5.185%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.839 | 0.989 | -3.037 | -10.526 | 10.526 | 7.63 | 1.549 | -0.417 | 5.183%
1 | 7.716 | 1.567 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.795 | 0.99 | -2.898 | -10.526 | 10.526 | 7.316 | 1.486 | -0.4 | 5.182%
2 | 7.517 | 1.526 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.016 | -0.768 | 0.991 | -2.814 | -10.526 | 10.526 | 7.128 | 1.447 | -0.389 | 5.181%
3 | 7.407 | 1.504 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.753 | 0.992 | -2.768 | -10.526 | 10.526 | 7.023 | 1.426 | -0.384 | 5.181%
4 | 7.398 | 1.502 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.752 | 0.992 | -2.765 | -10.526 | 10.526 | 7.015 | 1.424 | -0.383 | 5.181%
5 | 7.563 | 1.536 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.016 | -0.774 | 0.991 | -2.834 | -10.526 | 10.526 | 7.171 | 1.456 | -0.392 | 5.181%
6 | 7.986 | 1.622 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.831 | 0.989 | -3.012 | -10.526 | 10.526 | 7.572 | 1.538 | -0.414 | 5.183%
7 | 8.626 | 1.752 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.918 | 0.986 | -3.282 | -10.526 | 10.526 | 8.179 | 1.661 | -0.447 | 5.185%
8 | 9.059 | 1.84 | 0.98 | Z | moderate sun | 10.526 | 10.515 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.014 | -0.977 | 0.984 | -3.467 | -10.515 | 10.515 | 8.59 | 1.744 | -0.469 | 5.182%
9 | 9.181 | 1.864 | 0.98 | Z | moderate sun | 10.526 | 10.41 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.014 | -0.996 | 0.983 | -3.522 | -10.41 | 10.41 | 8.71 | 1.769 | -0.471 | 5.13%
10 | 9.23 | 1.874 | 0.98 | Z | moderate sun | 10.526 | 10.189 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.014 | -1.01 | 0.984 | -3.55 | -10.189 | 10.189 | 8.768 | 1.78 | -0.462 | 5.002%
11 | 9.261 | 1.881 | 0.98 | Z | moderate sun | 10.526 | 9.958 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.015 | -1.021 | 0.984 | -3.569 | -9.958 | 9.958 | 8.808 | 1.789 | -0.453 | 4.886%
12 | 9.292 | 1.887 | 0.98 | Z | moderate sun | 10.526 | 9.831 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.015 | -1.029 | 0.984 | -3.586 | -9.831 | 9.831 | 8.844 | 1.796 | -0.448 | 4.823%
13 | 9.322 | 1.893 | 0.98 | Z | moderate sun | 10.526 | 9.968 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.015 | -1.029 | 0.984 | -3.595 | -9.968 | 9.968 | 8.866 | 1.8 | -0.456 | 4.892%
14 | 9.338 | 1.896 | 0.98 | Z | moderate sun | 10.526 | 10.031 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.015 | -1.029 | 0.984 | -3.6 | -10.031 | 10.031 | 8.878 | 1.803 | -0.46 | 4.923%
15 | 9.404 | 1.91 | 0.98 | Z | moderate sun | 10.526 | 10.294 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.014 | -1.031 | 0.983 | -3.621 | -10.294 | 10.294 | 8.929 | 1.813 | -0.475 | 5.055%
16 | 9.594 | 1.948 | 0.98 | Z | moderate sun | 10.526 | 10.473 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.013 | -1.052 | 0.981 | -3.697 | -10.473 | 10.473 | 9.1 | 1.848 | -0.494 | 5.145%
17 | 9.883 | 2.007 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.013 | -1.089 | 0.98 | -3.819 | -10.526 | 10.526 | 9.37 | 1.903 | -0.513 | 5.191%
18 | 10 | 2.031 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.012 | -1.105 | 0.979 | -3.87 | -10.526 | 10.526 | 9.481 | 1.925 | -0.519 | 5.191%
19 | 9.966 | 2.024 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.1 | 0.979 | -3.855 | -10.526 | 10.526 | 9.449 | 1.919 | -0.517 | 5.191%
20 | 9.857 | 2.002 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.013 | -1.085 | 0.98 | -3.808 | -10.526 | 10.526 | 9.345 | 1.898 | -0.512 | 5.191%
21 | 9.62 | 1.953 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.053 | 0.981 | -3.706 | -10.526 | 10.526 | 9.121 | 1.852 | -0.499 | 5.19%
22 | 9.139 | 1.856 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.014 | -0.988 | 0.983 | -3.5 | -10.526 | 10.526 | 8.665 | 1.759 | -0.474 | 5.188%
23 | 8.547 | 1.736 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.907 | 0.986 | -3.249 | -10.526 | 10.526 | 8.104 | 1.646 | -0.443 | 5.185%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.839 | 0.989 | -3.037 | -10.526 | 10.526 | 7.63 | 1.549 | -0.417 | 5.183%
1 | 7.716 | 1.567 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.795 | 0.99 | -2.898 | -10.526 | 10.526 | 7.316 | 1.486 | -0.4 | 5.182%
2 | 7.517 | 1.526 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.016 | -0.768 | 0.991 | -2.814 | -10.526 | 10.526 | 7.128 | 1.447 | -0.389 | 5.181%
3 | 7.407 | 1.504 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.753 | 0.992 | -2.768 | -10.526 | 10.526 | 7.023 | 1.426 | -0.384 | 5.181%
4 | 7.398 | 1.502 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.752 | 0.992 | -2.765 | -10.526 | 10.526 | 7.015 | 1.424 | -0.383 | 5.181%
5 | 7.563 | 1.536 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.016 | -0.774 | 0.991 | -2.834 | -10.526 | 10.526 | 7.171 | 1.456 | -0.392 | 5.181%
6 | 7.986 | 1.622 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.831 | 0.989 | -3.012 | -10.526 | 10.526 | 7.572 | 1.538 | -0.414 | 5.183%
7 | 8.626 | 1.752 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.918 | 0.986 | -3.282 | -10.526 | 10.526 | 8.179 | 1.661 | -0.447 | 5.185%
8 | 9.059 | 1.84 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.014 | -0.977 | 0.984 | -3.466 | -10.526 | 10.526 | 8.589 | 1.744 | -0.47 | 5.187%
9 | 9.181 | 1.864 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.014 | -0.993 | 0.983 | -3.518 | -10.526 | 10.526 | 8.705 | 1.768 | -0.476 | 5.188%
10 | 9.23 | 1.874 | 0.98 | Z | cloudy | 10.526 | 10.515 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.013 | -1 | 0.983 | -3.54 | -10.515 | 10.515 | 8.752 | 1.777 | -0.478 | 5.183%
11 | 9.261 | 1.881 | 0.98 | Z | cloudy | 10.526 | 10.484 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.014 | -1.005 | 0.983 | -3.554 | -10.484 | 10.484 | 8.782 | 1.783 | -0.479 | 5.167%
12 | 9.292 | 1.887 | 0.98 | Z | cloudy | 10.526 | 10.452 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.014 | -1.01 | 0.983 | -3.568 | -10.452 | 10.452 | 8.813 | 1.79 | -0.479 | 5.151%
13 | 9.322 | 1.893 | 0.98 | Z | cloudy | 10.526 | 10.452 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.014 | -1.015 | 0.983 | -3.581 | -10.452 | 10.452 | 8.842 | 1.795 | -0.48 | 5.151%
14 | 9.338 | 1.896 | 0.98 | Z | cloudy | 10.526 | 10.473 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.014 | -1.017 | 0.983 | -3.588 | -10.473 | 10.473 | 8.858 | 1.799 | -0.48 | 5.144%
15 | 9.404 | 1.91 | 0.98 | Z | cloudy | 10.526 | 10.505 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.013 | -1.025 | 0.982 | -3.615 | -10.505 | 10.505 | 8.919 | 1.811 | -0.485 | 5.16%
16 | 9.594 | 1.948 | 0.98 | Z | cloudy | 10.526 | 10.515 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.013 | -1.05 | 0.981 | -3.695 | -10.515 | 10.515 | 9.097 | 1.847 | -0.497 | 5.184%
17 | 9.883 | 2.007 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.013 | -1.089 | 0.98 | -3.819 | -10.526 | 10.526 | 9.37 | 1.903 | -0.513 | 5.191%
18 | 10 | 2.031 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.012 | -1.105 | 0.979 | -3.87 | -10.526 | 10.526 | 9.481 | 1.925 | -0.519 | 5.191%
19 | 9.966 | 2.024 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.1 | 0.979 | -3.855 | -10.526 | 10.526 | 9.449 | 1.919 | -0.517 | 5.191%
20 | 9.857 | 2.002 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.013 | -1.085 | 0.98 | -3.808 | -10.526 | 10.526 | 9.345 | 1.898 | -0.512 | 5.191%
21 | 9.62 | 1.953 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.053 | 0.981 | -3.706 | -10.526 | 10.526 | 9.121 | 1.852 | -0.499 | 5.19%
22 | 9.139 | 1.856 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.014 | -0.988 | 0.983 | -3.5 | -10.526 | 10.526 | 8.665 | 1.759 | -0.474 | 5.188%
23 | 8.547 | 1.736 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.907 | 0.986 | -3.249 | -10.526 | 10.526 | 8.104 | 1.646 | -0.443 | 5.185%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.839 | 0.989 | -3.037 | -10.526 | 10.526 | 7.63 | 1.549 | -0.417 | 5.183%
1 | 7.716 | 1.567 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.002 | -1.612 | 0.99 | -2.677 | -5.263 | 5.263 | 7.308 | 1.484 | -0.408 | 5.286%
2 | 7.517 | 1.526 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.003 | -1.559 | 0.991 | -2.594 | -5.263 | 5.263 | 7.12 | 1.446 | -0.397 | 5.285%
3 | 7.407 | 1.504 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.003 | -1.529 | 0.991 | -2.549 | -5.263 | 5.263 | 7.016 | 1.425 | -0.391 | 5.284%
4 | 7.398 | 1.502 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.003 | -1.527 | 0.991 | -2.545 | -5.263 | 5.263 | 7.007 | 1.423 | -0.391 | 5.284%
5 | 7.563 | 1.536 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.003 | -1.571 | 0.99 | -2.613 | -5.263 | 5.263 | 7.163 | 1.455 | -0.4 | 5.285%
6 | 7.986 | 1.622 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.685 | 0.988 | -2.789 | -5.263 | 5.263 | 7.564 | 1.536 | -0.422 | 5.288%
7 | 8.626 | 1.752 | 0.98 | Z | very sunny | 5.263 | 5.252 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.86 | 0.985 | -3.059 | -5.252 | 5.252 | 8.172 | 1.659 | -0.454 | 5.263%
8 | 9.059 | 1.84 | 0.98 | Z | very sunny | 5.263 | 5.116 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.999 | -1.992 | 0.984 | -3.255 | -5.116 | 5.116 | 8.595 | 1.745 | -0.464 | 5.127%
9 | 9.181 | 1.864 | 0.98 | Z | very sunny | 5.263 | 4.705 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 1.001 | -2.066 | 0.986 | -3.347 | -4.705 | 4.705 | 8.749 | 1.776 | -0.432 | 4.709%
10 | 9.23 | 1.874 | 0.98 | Z | very sunny | 5.263 | 4.142 | 4 | 1.025 | -2.537 | 1.009 | -3.826 | 1.003 | -2.135 | 0.988 | -3.424 | -4.142 | 4.142 | 8.848 | 1.797 | -0.382 | 4.142%
11 | 9.261 | 1.881 | 0.98 | Z | very sunny | 5.263 | 3.574 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 1.006 | -2.199 | 0.991 | -3.492 | -3.574 | 3.574 | 8.929 | 1.813 | -0.332 | 3.58%
12 | 9.292 | 1.887 | 0.98 | Z | very sunny | 5.263 | 3.258 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 1.008 | -2.239 | 0.992 | -3.537 | -3.258 | 3.258 | 8.989 | 1.825 | -0.303 | 3.259%
13 | 9.322 | 1.893 | 0.98 | Z | very sunny | 5.263 | 3.353 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 1.007 | -2.239 | 0.992 | -3.542 | -3.353 | 3.353 | 9.011 | 1.83 | -0.311 | 3.337%
14 | 9.338 | 1.896 | 0.98 | Z | very sunny | 5.263 | 3.505 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 1.006 | -2.229 | 0.991 | -3.533 | -3.505 | 3.505 | 9.012 | 1.83 | -0.326 | 3.491%
15 | 9.404 | 1.91 | 0.98 | Z | very sunny | 5.263 | 3.942 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 1.004 | -2.203 | 0.988 | -3.518 | -3.942 | 3.942 | 9.034 | 1.834 | -0.37 | 3.936%
16 | 9.594 | 1.948 | 0.98 | Z | very sunny | 5.263 | 4.458 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 1.001 | -2.204 | 0.985 | -3.547 | -4.458 | 4.458 | 9.166 | 1.861 | -0.428 | 4.46%
17 | 9.883 | 2.007 | 0.98 | Z | very sunny | 5.263 | 4.921 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.997 | -2.235 | 0.981 | -3.622 | -4.921 | 4.921 | 9.394 | 1.907 | -0.489 | 4.951%
18 | 10 | 2.031 | 0.98 | Z | very sunny | 5.263 | 5.189 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.995 | -2.239 | 0.979 | -3.644 | -5.189 | 5.189 | 9.477 | 1.924 | -0.523 | 5.229%
19 | 9.966 | 2.024 | 0.98 | Z | very sunny | 5.263 | 5.258 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.995 | -2.223 | 0.979 | -3.623 | -5.258 | 5.258 | 9.438 | 1.916 | -0.528 | 5.299%
20 | 9.857 | 2.002 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.192 | 0.979 | -3.576 | -5.263 | 5.263 | 9.334 | 1.895 | -0.523 | 5.303%
21 | 9.62 | 1.953 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.996 | -2.128 | 0.98 | -3.475 | -5.263 | 5.263 | 9.11 | 1.85 | -0.51 | 5.301%
22 | 9.139 | 1.856 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.998 | -1.997 | 0.983 | -3.272 | -5.263 | 5.263 | 8.655 | 1.757 | -0.484 | 5.297%
23 | 8.547 | 1.736 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.836 | 0.986 | -3.023 | -5.263 | 5.263 | 8.095 | 1.644 | -0.452 | 5.293%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1.001 | -1.701 | 0.988 | -2.814 | -5.263 | 5.263 | 7.621 | 1.548 | -0.426 | 5.289%
1 | 7.716 | 1.567 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.002 | -1.612 | 0.99 | -2.677 | -5.263 | 5.263 | 7.308 | 1.484 | -0.408 | 5.286%
2 | 7.517 | 1.526 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.003 | -1.559 | 0.991 | -2.594 | -5.263 | 5.263 | 7.12 | 1.446 | -0.397 | 5.285%
3 | 7.407 | 1.504 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.003 | -1.529 | 0.991 | -2.549 | -5.263 | 5.263 | 7.016 | 1.425 | -0.391 | 5.284%
4 | 7.398 | 1.502 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.003 | -1.527 | 0.991 | -2.545 | -5.263 | 5.263 | 7.007 | 1.423 | -0.391 | 5.284%
5 | 7.563 | 1.536 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.003 | -1.571 | 0.99 | -2.613 | -5.263 | 5.263 | 7.163 | 1.455 | -0.4 | 5.285%
6 | 7.986 | 1.622 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.685 | 0.988 | -2.789 | -5.263 | 5.263 | 7.564 | 1.536 | -0.422 | 5.288%
7 | 8.626 | 1.752 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.858 | 0.985 | -3.056 | -5.263 | 5.263 | 8.169 | 1.659 | -0.457 | 5.293%
8 | 9.059 | 1.84 | 0.98 | Z | moderate sun | 5.263 | 5.258 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.998 | -1.976 | 0.983 | -3.239 | -5.258 | 5.258 | 8.58 | 1.742 | -0.479 | 5.291%
9 | 9.181 | 1.864 | 0.98 | Z | moderate sun | 5.263 | 5.205 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.998 | -2.014 | 0.983 | -3.295 | -5.205 | 5.205 | 8.7 | 1.767 | -0.481 | 5.238%
10 | 9.23 | 1.874 | 0.98 | Z | moderate sun | 5.263 | 5.095 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.998 | -2.04 | 0.983 | -3.329 | -5.095 | 5.095 | 8.759 | 1.779 | -0.471 | 5.107%
11 | 9.261 | 1.881 | 0.98 | Z | moderate sun | 5.263 | 4.979 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.999 | -2.06 | 0.984 | -3.354 | -4.979 | 4.979 | 8.799 | 1.787 | -0.462 | 4.989%
12 | 9.292 | 1.887 | 0.98 | Z | moderate sun | 5.263 | 4.916 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.999 | -2.075 | 0.984 | -3.373 | -4.916 | 4.916 | 8.834 | 1.794 | -0.458 | 4.924%
13 | 9.322 | 1.893 | 0.98 | Z | moderate sun | 5.263 | 4.984 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.999 | -2.076 | 0.983 | -3.379 | -4.984 | 4.984 | 8.856 | 1.798 | -0.466 | 4.994%
14 | 9.338 | 1.896 | 0.98 | Z | moderate sun | 5.263 | 5.016 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.998 | -2.078 | 0.983 | -3.383 | -5.016 | 5.016 | 8.869 | 1.801 | -0.469 | 5.027%
15 | 9.404 | 1.91 | 0.98 | Z | moderate sun | 5.263 | 5.147 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.998 | -2.082 | 0.982 | -3.397 | -5.147 | 5.147 | 8.919 | 1.811 | -0.485 | 5.162%
16 | 9.594 | 1.948 | 0.98 | Z | moderate sun | 5.263 | 5.237 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.996 | -2.125 | 0.981 | -3.469 | -5.237 | 5.237 | 9.09 | 1.846 | -0.504 | 5.255%
17 | 9.883 | 2.007 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.995 | -2.2 | 0.979 | -3.587 | -5.263 | 5.263 | 9.359 | 1.9 | -0.524 | 5.304%
18 | 10 | 2.031 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.995 | -2.232 | 0.978 | -3.637 | -5.263 | 5.263 | 9.47 | 1.923 | -0.53 | 5.305%
19 | 9.966 | 2.024 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.995 | -2.222 | 0.979 | -3.622 | -5.263 | 5.263 | 9.437 | 1.916 | -0.529 | 5.304%
20 | 9.857 | 2.002 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.192 | 0.979 | -3.576 | -5.263 | 5.263 | 9.334 | 1.895 | -0.523 | 5.303%
21 | 9.62 | 1.953 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.996 | -2.128 | 0.98 | -3.475 | -5.263 | 5.263 | 9.11 | 1.85 | -0.51 | 5.301%
22 | 9.139 | 1.856 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.998 | -1.997 | 0.983 | -3.272 | -5.263 | 5.263 | 8.655 | 1.757 | -0.484 | 5.297%
23 | 8.547 | 1.736 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.836 | 0.986 | -3.023 | -5.263 | 5.263 | 8.095 | 1.644 | -0.452 | 5.293%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1.001 | -1.701 | 0.988 | -2.814 | -5.263 | 5.263 | 7.621 | 1.548 | -0.426 | 5.289%
1 | 7.716 | 1.567 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.002 | -1.612 | 0.99 | -2.677 | -5.263 | 5.263 | 7.308 | 1.484 | -0.408 | 5.286%
2 | 7.517 | 1.526 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.003 | -1.559 | 0.991 | -2.594 | -5.263 | 5.263 | 7.12 | 1.446 | -0.397 | 5.285%
3 | 7.407 | 1.504 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.003 | -1.529 | 0.991 | -2.549 | -5.263 | 5.263 | 7.016 | 1.425 | -0.391 | 5.284%
4 | 7.398 | 1.502 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.003 | -1.527 | 0.991 | -2.545 | -5.263 | 5.263 | 7.007 | 1.423 | -0.391 | 5.284%
5 | 7.563 | 1.536 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.003 | -1.571 | 0.99 | -2.613 | -5.263 | 5.263 | 7.163 | 1.455 | -0.4 | 5.285%
6 | 7.986 | 1.622 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.685 | 0.988 | -2.789 | -5.263 | 5.263 | 7.564 | 1.536 | -0.422 | 5.288%
7 | 8.626 | 1.752 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.858 | 0.985 | -3.056 | -5.263 | 5.263 | 8.169 | 1.659 | -0.457 | 5.293%
8 | 9.059 | 1.84 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.998 | -1.975 | 0.983 | -3.238 | -5.263 | 5.263 | 8.579 | 1.742 | -0.48 | 5.297%
9 | 9.181 | 1.864 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.997 | -2.008 | 0.983 | -3.289 | -5.263 | 5.263 | 8.695 | 1.766 | -0.486 | 5.298%
10 | 9.23 | 1.874 | 0.98 | Z | cloudy | 5.263 | 5.258 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.997 | -2.022 | 0.982 | -3.311 | -5.258 | 5.258 | 8.741 | 1.775 | -0.489 | 5.293%
11 | 9.261 | 1.881 | 0.98 | Z | cloudy | 5.263 | 5.242 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.997 | -2.032 | 0.982 | -3.325 | -5.242 | 5.242 | 8.772 | 1.781 | -0.489 | 5.277%
12 | 9.292 | 1.887 | 0.98 | Z | cloudy | 5.263 | 5.226 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.997 | -2.042 | 0.982 | -3.34 | -5.226 | 5.226 | 8.803 | 1.788 | -0.489 | 5.261%
13 | 9.322 | 1.893 | 0.98 | Z | cloudy | 5.263 | 5.226 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.997 | -2.05 | 0.982 | -3.353 | -5.226 | 5.226 | 8.832 | 1.793 | -0.49 | 5.261%
14 | 9.338 | 1.896 | 0.98 | Z | cloudy | 5.263 | 5.237 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.997 | -2.055 | 0.982 | -3.36 | -5.237 | 5.237 | 8.847 | 1.797 | -0.491 | 5.253%
15 | 9.404 | 1.91 | 0.98 | Z | cloudy | 5.263 | 5.252 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.997 | -2.072 | 0.982 | -3.387 | -5.252 | 5.252 | 8.908 | 1.809 | -0.496 | 5.269%
16 | 9.594 | 1.948 | 0.98 | Z | cloudy | 5.263 | 5.258 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.996 | -2.121 | 0.98 | -3.465 | -5.258 | 5.258 | 9.086 | 1.845 | -0.508 | 5.296%
17 | 9.883 | 2.007 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.995 | -2.2 | 0.979 | -3.587 | -5.263 | 5.263 | 9.359 | 1.9 | -0.524 | 5.304%
18 | 10 | 2.031 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.995 | -2.232 | 0.978 | -3.637 | -5.263 | 5.263 | 9.47 | 1.923 | -0.53 | 5.305%
19 | 9.966 | 2.024 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.995 | -2.222 | 0.979 | -3.622 | -5.263 | 5.263 | 9.437 | 1.916 | -0.529 | 5.304%
20 | 9.857 | 2.002 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.192 | 0.979 | -3.576 | -5.263 | 5.263 | 9.334 | 1.895 | -0.523 | 5.303%
21 | 9.62 | 1.953 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.996 | -2.128 | 0.98 | -3.475 | -5.263 | 5.263 | 9.11 | 1.85 | -0.51 | 5.301%
22 | 9.139 | 1.856 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.998 | -1.997 | 0.983 | -3.272 | -5.263 | 5.263 | 8.655 | 1.757 | -0.484 | 5.297%
23 | 8.547 | 1.736 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.836 | 0.986 | -3.023 | -5.263 | 5.263 | 8.095 | 1.644 | -0.452 | 5.293%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1.001 | -1.701 | 0.988 | -2.814 | -5.263 | 5.263 | 7.621 | 1.548 | -0.426 | 5.289%
1 | 7.716 | 1.567 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.386 | 0.977 | -2.451 | -7.531 | 10.526 | 7.128 | 1.447 | -0.588 | 7.619%
2 | 7.517 | 1.526 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.334 | 0.978 | -2.369 | -7.529 | 10.526 | 6.945 | 1.41 | -0.572 | 7.614%
3 | 7.407 | 1.504 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.305 | 0.979 | -2.325 | -7.527 | 10.526 | 6.843 | 1.39 | -0.564 | 7.612%
4 | 7.398 | 1.502 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.303 | 0.979 | -2.321 | -7.527 | 10.526 | 6.835 | 1.388 | -0.563 | 7.612%
5 | 7.563 | 1.536 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.346 | 0.978 | -2.388 | -7.529 | 10.526 | 6.987 | 1.419 | -0.576 | 7.615%
6 | 7.986 | 1.622 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.458 | 0.976 | -2.562 | -7.534 | 10.526 | 7.377 | 1.498 | -0.609 | 7.625%
7 | 8.626 | 1.752 | 0.98 | Z | very sunny | 10.526 | 10.505 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.627 | 0.973 | -2.826 | -7.54 | 10.505 | 7.967 | 1.618 | -0.659 | 7.64%
8 | 9.059 | 1.84 | 0.98 | Z | very sunny | 10.526 | 10.231 | 4 | 1.025 | -2.49 | 1.01 | -3.753 | 0.985 | -1.742 | 0.971 | -3.005 | -7.545 | 10.231 | 8.366 | 1.699 | -0.693 | 7.65%
9 | 9.181 | 1.864 | 0.98 | Z | very sunny | 10.526 | 9.41 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.985 | -1.775 | 0.97 | -3.056 | -7.546 | 9.41 | 8.478 | 1.722 | -0.703 | 7.652%
10 | 9.23 | 1.874 | 0.98 | Z | very sunny | 10.526 | 8.284 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -1.975 | 0.98 | -3.264 | -5.721 | 8.284 | 8.698 | 1.766 | -0.532 | 5.769%
11 | 9.261 | 1.881 | 0.98 | Z | very sunny | 10.526 | 7.147 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -1.983 | 0.98 | -3.277 | -5.721 | 7.147 | 8.727 | 1.772 | -0.534 | 5.769%
12 | 9.292 | 1.887 | 0.98 | Z | very sunny | 10.526 | 6.516 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -1.992 | 0.98 | -3.29 | -5.722 | 6.516 | 8.756 | 1.778 | -0.536 | 5.77%
13 | 9.322 | 1.893 | 0.98 | Z | very sunny | 10.526 | 6.705 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2 | 0.979 | -3.302 | -5.722 | 6.705 | 8.784 | 1.784 | -0.538 | 5.77%
14 | 9.338 | 1.896 | 0.98 | Z | very sunny | 10.526 | 7.01 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.004 | 0.979 | -3.309 | -5.722 | 7.01 | 8.799 | 1.787 | -0.539 | 5.771%
15 | 9.404 | 1.91 | 0.98 | Z | very sunny | 10.526 | 7.884 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.022 | 0.979 | -3.337 | -5.723 | 7.884 | 8.861 | 1.799 | -0.543 | 5.772%
16 | 9.594 | 1.948 | 0.98 | Z | very sunny | 10.526 | 8.916 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.074 | 0.978 | -3.417 | -5.724 | 8.916 | 9.04 | 1.836 | -0.554 | 5.775%
17 | 9.883 | 2.007 | 0.98 | Z | very sunny | 10.526 | 9.842 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.152 | 0.977 | -3.539 | -5.727 | 9.842 | 9.312 | 1.891 | -0.571 | 5.781%
18 | 10 | 2.031 | 0.98 | Z | very sunny | 10.526 | 10.379 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.184 | 0.976 | -3.589 | -5.728 | 10.379 | 9.422 | 1.913 | -0.578 | 5.783%
19 | 9.966 | 2.024 | 0.98 | Z | very sunny | 10.526 | 10.515 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.175 | 0.976 | -3.574 | -5.727 | 10.515 | 9.39 | 1.907 | -0.576 | 5.782%
20 | 9.857 | 2.002 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.145 | 0.977 | -3.528 | -5.726 | 10.526 | 9.287 | 1.886 | -0.57 | 5.78%
21 | 9.62 | 1.953 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.081 | 0.978 | -3.428 | -5.724 | 10.526 | 9.064 | 1.841 | -0.556 | 5.776%
22 | 9.139 | 1.856 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.985 | -1.764 | 0.97 | -3.039 | -7.546 | 10.526 | 8.44 | 1.714 | -0.699 | 7.651%
23 | 8.547 | 1.736 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.606 | 0.973 | -2.793 | -7.539 | 10.526 | 7.894 | 1.603 | -0.653 | 7.638%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.474 | 0.976 | -2.587 | -7.534 | 10.526 | 7.433 | 1.509 | -0.614 | 7.626%
1 | 7.716 | 1.567 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.387 | 0.977 | -2.451 | -7.531 | 10.526 | 7.128 | 1.447 | -0.588 | 7.619%
2 | 7.517 | 1.526 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.334 | 0.978 | -2.369 | -7.529 | 10.526 | 6.945 | 1.41 | -0.572 | 7.614%
3 | 7.407 | 1.504 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.305 | 0.979 | -2.325 | -7.527 | 10.526 | 6.843 | 1.39 | -0.564 | 7.612%
4 | 7.398 | 1.502 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.303 | 0.979 | -2.321 | -7.527 | 10.526 | 6.835 | 1.388 | -0.563 | 7.612%
5 | 7.563 | 1.536 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.346 | 0.978 | -2.388 | -7.529 | 10.526 | 6.987 | 1.419 | -0.576 | 7.615%
6 | 7.986 | 1.622 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.458 | 0.976 | -2.562 | -7.534 | 10.526 | 7.377 | 1.498 | -0.609 | 7.625%
7 | 8.626 | 1.752 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.627 | 0.973 | -2.826 | -7.54 | 10.526 | 7.967 | 1.618 | -0.659 | 7.64%
8 | 9.059 | 1.84 | 0.98 | Z | moderate sun | 10.526 | 10.515 | 4 | 1.025 | -2.49 | 1.01 | -3.753 | 0.985 | -1.742 | 0.971 | -3.005 | -7.545 | 10.515 | 8.366 | 1.699 | -0.693 | 7.65%
9 | 9.181 | 1.864 | 0.98 | Z | moderate sun | 10.526 | 10.41 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.985 | -1.775 | 0.97 | -3.056 | -7.546 | 10.41 | 8.478 | 1.722 | -0.703 | 7.652%
10 | 9.23 | 1.874 | 0.98 | Z | moderate sun | 10.526 | 10.189 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -1.975 | 0.98 | -3.264 | -5.721 | 10.189 | 8.698 | 1.766 | -0.532 | 5.769%
11 | 9.261 | 1.881 | 0.98 | Z | moderate sun | 10.526 | 9.958 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -1.983 | 0.98 | -3.277 | -5.721 | 9.958 | 8.727 | 1.772 | -0.534 | 5.769%
12 | 9.292 | 1.887 | 0.98 | Z | moderate sun | 10.526 | 9.831 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -1.992 | 0.98 | -3.29 | -5.722 | 9.831 | 8.756 | 1.778 | -0.536 | 5.77%
13 | 9.322 | 1.893 | 0.98 | Z | moderate sun | 10.526 | 9.968 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2 | 0.979 | -3.302 | -5.722 | 9.968 | 8.784 | 1.784 | -0.538 | 5.77%
14 | 9.338 | 1.896 | 0.98 | Z | moderate sun | 10.526 | 10.031 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.004 | 0.979 | -3.309 | -5.722 | 10.031 | 8.799 | 1.787 | -0.539 | 5.771%
15 | 9.404 | 1.91 | 0.98 | Z | moderate sun | 10.526 | 10.294 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.022 | 0.979 | -3.337 | -5.723 | 10.294 | 8.861 | 1.799 | -0.543 | 5.772%
16 | 9.594 | 1.948 | 0.98 | Z | moderate sun | 10.526 | 10.473 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.074 | 0.978 | -3.417 | -5.724 | 10.473 | 9.04 | 1.836 | -0.554 | 5.775%
17 | 9.883 | 2.007 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.152 | 0.977 | -3.539 | -5.727 | 10.526 | 9.312 | 1.891 | -0.571 | 5.781%
18 | 10 | 2.031 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.184 | 0.976 | -3.589 | -5.728 | 10.526 | 9.422 | 1.913 | -0.578 | 5.783%
19 | 9.966 | 2.024 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.175 | 0.976 | -3.574 | -5.727 | 10.526 | 9.39 | 1.907 | -0.576 | 5.782%
20 | 9.857 | 2.002 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.145 | 0.977 | -3.528 | -5.726 | 10.526 | 9.287 | 1.886 | -0.57 | 5.78%
21 | 9.62 | 1.953 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.081 | 0.978 | -3.428 | -5.724 | 10.526 | 9.064 | 1.841 | -0.556 | 5.776%
22 | 9.139 | 1.856 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.985 | -1.764 | 0.97 | -3.039 | -7.546 | 10.526 | 8.44 | 1.714 | -0.699 | 7.651%
23 | 8.547 | 1.736 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.606 | 0.973 | -2.793 | -7.539 | 10.526 | 7.894 | 1.603 | -0.653 | 7.638%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.474 | 0.976 | -2.587 | -7.534 | 10.526 | 7.433 | 1.509 | -0.614 | 7.626%
1 | 7.716 | 1.567 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.387 | 0.977 | -2.451 | -7.531 | 10.526 | 7.128 | 1.447 | -0.588 | 7.619%
2 | 7.517 | 1.526 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.334 | 0.978 | -2.369 | -7.529 | 10.526 | 6.945 | 1.41 | -0.572 | 7.614%
3 | 7.407 | 1.504 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.305 | 0.979 | -2.325 | -7.527 | 10.526 | 6.843 | 1.39 | -0.564 | 7.612%
4 | 7.398 | 1.502 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.303 | 0.979 | -2.321 | -7.527 | 10.526 | 6.835 | 1.388 | -0.563 | 7.612%
5 | 7.563 | 1.536 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.346 | 0.978 | -2.388 | -7.529 | 10.526 | 6.987 | 1.419 | -0.576 | 7.615%
6 | 7.986 | 1.622 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.458 | 0.976 | -2.562 | -7.534 | 10.526 | 7.377 | 1.498 | -0.609 | 7.625%
7 | 8.626 | 1.752 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.627 | 0.973 | -2.826 | -7.54 | 10.526 | 7.967 | 1.618 | -0.659 | 7.64%
8 | 9.059 | 1.84 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.49 | 1.01 | -3.753 | 0.985 | -1.742 | 0.971 | -3.005 | -7.545 | 10.526 | 8.366 | 1.699 | -0.693 | 7.65%
9 | 9.181 | 1.864 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.985 | -1.775 | 0.97 | -3.056 | -7.546 | 10.526 | 8.478 | 1.722 | -0.703 | 7.652%
10 | 9.23 | 1.874 | 0.98 | Z | cloudy | 10.526 | 10.515 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -1.975 | 0.98 | -3.264 | -5.721 | 10.515 | 8.698 | 1.766 | -0.532 | 5.769%
11 | 9.261 | 1.881 | 0.98 | Z | cloudy | 10.526 | 10.484 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -1.983 | 0.98 | -3.277 | -5.721 | 10.484 | 8.727 | 1.772 | -0.534 | 5.769%
12 | 9.292 | 1.887 | 0.98 | Z | cloudy | 10.526 | 10.452 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -1.992 | 0.98 | -3.29 | -5.722 | 10.452 | 8.756 | 1.778 | -0.536 | 5.77%
13 | 9.322 | 1.893 | 0.98 | Z | cloudy | 10.526 | 10.452 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2 | 0.979 | -3.302 | -5.722 | 10.452 | 8.784 | 1.784 | -0.538 | 5.77%
14 | 9.338 | 1.896 | 0.98 | Z | cloudy | 10.526 | 10.473 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.004 | 0.979 | -3.309 | -5.722 | 10.473 | 8.799 | 1.787 | -0.539 | 5.771%
15 | 9.404 | 1.91 | 0.98 | Z | cloudy | 10.526 | 10.505 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.022 | 0.979 | -3.337 | -5.723 | 10.505 | 8.861 | 1.799 | -0.543 | 5.772%
16 | 9.594 | 1.948 | 0.98 | Z | cloudy | 10.526 | 10.515 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.074 | 0.978 | -3.417 | -5.724 | 10.515 | 9.04 | 1.836 | -0.554 | 5.775%
17 | 9.883 | 2.007 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.152 | 0.977 | -3.539 | -5.727 | 10.526 | 9.312 | 1.891 | -0.571 | 5.781%
18 | 10 | 2.031 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.184 | 0.976 | -3.589 | -5.728 | 10.526 | 9.422 | 1.913 | -0.578 | 5.783%
19 | 9.966 | 2.024 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.175 | 0.976 | -3.574 | -5.727 | 10.526 | 9.39 | 1.907 | -0.576 | 5.782%
20 | 9.857 | 2.002 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.145 | 0.977 | -3.528 | -5.726 | 10.526 | 9.287 | 1.886 | -0.57 | 5.78%
21 | 9.62 | 1.953 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.081 | 0.978 | -3.428 | -5.724 | 10.526 | 9.064 | 1.841 | -0.556 | 5.776%
22 | 9.139 | 1.856 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.985 | -1.764 | 0.97 | -3.039 | -7.546 | 10.526 | 8.44 | 1.714 | -0.699 | 7.651%
23 | 8.547 | 1.736 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.606 | 0.973 | -2.793 | -7.539 | 10.526 | 7.894 | 1.603 | -0.653 | 7.638%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.474 | 0.976 | -2.587 | -7.534 | 10.526 | 7.433 | 1.509 | -0.614 | 7.626%
1 | 7.716 | 1.567 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.975 | -2.263 | 0.975 | -2.263 | -5.263 | 5.263 | 7.093 | 1.44 | -0.623 | 8.069%
2 | 7.517 | 1.526 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.976 | -2.184 | 0.976 | -2.184 | -5.263 | 5.263 | 6.911 | 1.403 | -0.606 | 8.064%
3 | 7.407 | 1.504 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.976 | -2.14 | 0.976 | -2.14 | -5.263 | 5.263 | 6.81 | 1.383 | -0.597 | 8.061%
4 | 7.398 | 1.502 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.976 | -2.136 | 0.976 | -2.136 | -5.263 | 5.263 | 6.802 | 1.381 | -0.596 | 8.06%
5 | 7.563 | 1.536 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.976 | -2.202 | 0.976 | -2.202 | -5.263 | 5.263 | 6.953 | 1.412 | -0.61 | 8.065%
6 | 7.986 | 1.622 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.974 | -2.372 | 0.974 | -2.372 | -5.263 | 5.263 | 7.341 | 1.491 | -0.645 | 8.076%
7 | 8.626 | 1.752 | 0.98 | Z | very sunny | 5.263 | 5.252 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.971 | -2.632 | 0.971 | -2.632 | -5.252 | 5.252 | 7.93 | 1.61 | -0.696 | 8.073%
8 | 9.059 | 1.84 | 0.98 | Z | very sunny | 5.263 | 5.116 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -2.841 | 0.97 | -2.841 | -5.078 | 5.116 | 8.352 | 1.696 | -0.707 | 7.806%
9 | 9.181 | 1.864 | 0.98 | Z | very sunny | 5.263 | 4.705 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.972 | -2.961 | 0.972 | -2.961 | -4.705 | 4.705 | 8.518 | 1.73 | -0.663 | 7.219%
10 | 9.23 | 1.874 | 0.98 | Z | very sunny | 5.263 | 4.142 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.977 | -3.087 | 0.977 | -3.087 | -4.142 | 4.142 | 8.646 | 1.756 | -0.584 | 6.329%
11 | 9.261 | 1.881 | 0.98 | Z | very sunny | 5.263 | 3.574 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.981 | -3.206 | 0.981 | -3.206 | -3.574 | 3.574 | 8.758 | 1.778 | -0.503 | 5.426%
12 | 9.292 | 1.887 | 0.98 | Z | very sunny | 5.263 | 3.258 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.984 | -3.278 | 0.984 | -3.278 | -3.258 | 3.258 | 8.835 | 1.794 | -0.457 | 4.924%
13 | 9.322 | 1.893 | 0.98 | Z | very sunny | 5.263 | 3.353 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.983 | -3.273 | 0.983 | -3.273 | -3.353 | 3.353 | 8.849 | 1.797 | -0.473 | 5.076%
14 | 9.338 | 1.896 | 0.98 | Z | very sunny | 5.263 | 3.505 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.982 | -3.251 | 0.982 | -3.251 | -3.505 | 3.505 | 8.841 | 1.795 | -0.497 | 5.32%
15 | 9.404 | 1.91 | 0.98 | Z | very sunny | 5.263 | 3.942 | 5 | 1.008 | -3.901 | 1.008 | -3.901 | 0.978 | -3.196 | 0.978 | -3.196 | -3.942 | 3.942 | 8.838 | 1.795 | -0.566 | 6.016%
16 | 9.594 | 1.948 | 0.98 | Z | very sunny | 5.263 | 4.458 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.972 | -3.178 | 0.972 | -3.178 | -4.458 | 4.458 | 8.938 | 1.815 | -0.656 | 6.837%
17 | 9.883 | 2.007 | 0.98 | Z | very sunny | 5.263 | 4.921 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.273 | 0.97 | -3.273 | -4.586 | 4.921 | 9.187 | 1.865 | -0.696 | 7.044%
18 | 10 | 2.031 | 0.98 | Z | very sunny | 5.263 | 5.189 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.335 | 0.97 | -3.335 | -4.515 | 5.189 | 9.307 | 1.89 | -0.693 | 6.934%
19 | 9.966 | 2.024 | 0.98 | Z | very sunny | 5.263 | 5.258 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.317 | 0.97 | -3.317 | -4.535 | 5.258 | 9.272 | 1.883 | -0.694 | 6.966%
20 | 9.857 | 2.002 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.006 | -4.098 | 1.006 | -4.098 | 0.97 | -3.259 | 0.97 | -3.259 | -4.602 | 5.263 | 9.16 | 1.86 | -0.697 | 7.068%
21 | 9.62 | 1.953 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.134 | 0.97 | -3.134 | -4.745 | 5.263 | 8.919 | 1.811 | -0.701 | 7.289%
22 | 9.139 | 1.856 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -2.883 | 0.97 | -2.883 | -5.031 | 5.263 | 8.432 | 1.712 | -0.707 | 7.733%
23 | 8.547 | 1.736 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.971 | -2.598 | 0.971 | -2.598 | -5.263 | 5.263 | 7.856 | 1.595 | -0.691 | 8.088%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.973 | -2.396 | 0.973 | -2.396 | -5.263 | 5.263 | 7.397 | 1.502 | -0.65 | 8.078%
1 | 7.716 | 1.567 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.975 | -2.263 | 0.975 | -2.263 | -5.263 | 5.263 | 7.093 | 1.44 | -0.623 | 8.069%
2 | 7.517 | 1.526 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.976 | -2.184 | 0.976 | -2.184 | -5.263 | 5.263 | 6.911 | 1.403 | -0.606 | 8.064%
3 | 7.407 | 1.504 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.976 | -2.14 | 0.976 | -2.14 | -5.263 | 5.263 | 6.81 | 1.383 | -0.597 | 8.061%
4 | 7.398 | 1.502 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.976 | -2.136 | 0.976 | -2.136 | -5.263 | 5.263 | 6.802 | 1.381 | -0.596 | 8.06%
5 | 7.563 | 1.536 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.976 | -2.202 | 0.976 | -2.202 | -5.263 | 5.263 | 6.953 | 1.412 | -0.61 | 8.065%
6 | 7.986 | 1.622 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.974 | -2.372 | 0.974 | -2.372 | -5.263 | 5.263 | 7.341 | 1.491 | -0.645 | 8.076%
7 | 8.626 | 1.752 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.971 | -2.63 | 0.971 | -2.63 | -5.263 | 5.263 | 7.928 | 1.61 | -0.698 | 8.09%
8 | 9.059 | 1.84 | 0.98 | Z | moderate sun | 5.263 | 5.258 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -2.841 | 0.97 | -2.841 | -5.078 | 5.258 | 8.352 | 1.696 | -0.707 | 7.806%
9 | 9.181 | 1.864 | 0.98 | Z | moderate sun | 5.263 | 5.205 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -2.905 | 0.97 | -2.905 | -5.006 | 5.205 | 8.475 | 1.721 | -0.706 | 7.694%
10 | 9.23 | 1.874 | 0.98 | Z | moderate sun | 5.263 | 5.095 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -2.93 | 0.97 | -2.93 | -4.977 | 5.095 | 8.524 | 1.731 | -0.706 | 7.65%
11 | 9.261 | 1.881 | 0.98 | Z | moderate sun | 5.263 | 4.979 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -2.946 | 0.97 | -2.946 | -4.959 | 4.979 | 8.555 | 1.737 | -0.706 | 7.621%
12 | 9.292 | 1.887 | 0.98 | Z | moderate sun | 5.263 | 4.916 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -2.967 | 0.97 | -2.967 | -4.916 | 4.916 | 8.59 | 1.744 | -0.702 | 7.553%
13 | 9.322 | 1.893 | 0.98 | Z | moderate sun | 5.263 | 4.984 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -2.978 | 0.97 | -2.978 | -4.923 | 4.984 | 8.617 | 1.75 | -0.705 | 7.565%
14 | 9.338 | 1.896 | 0.98 | Z | moderate sun | 5.263 | 5.016 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -2.986 | 0.97 | -2.986 | -4.913 | 5.016 | 8.633 | 1.753 | -0.705 | 7.55%
15 | 9.404 | 1.91 | 0.98 | Z | moderate sun | 5.263 | 5.147 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.021 | 0.97 | -3.021 | -4.874 | 5.147 | 8.7 | 1.767 | -0.704 | 7.49%
16 | 9.594 | 1.948 | 0.98 | Z | moderate sun | 5.263 | 5.237 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.121 | 0.97 | -3.121 | -4.76 | 5.237 | 8.892 | 1.806 | -0.702 | 7.314%
17 | 9.883 | 2.007 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.273 | 0.97 | -3.273 | -4.586 | 5.263 | 9.187 | 1.865 | -0.696 | 7.044%
18 | 10 | 2.031 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.335 | 0.97 | -3.335 | -4.515 | 5.263 | 9.307 | 1.89 | -0.693 | 6.934%
19 | 9.966 | 2.024 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.317 | 0.97 | -3.317 | -4.535 | 5.263 | 9.272 | 1.883 | -0.694 | 6.966%
20 | 9.857 | 2.002 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.098 | 1.006 | -4.098 | 0.97 | -3.259 | 0.97 | -3.259 | -4.602 | 5.263 | 9.16 | 1.86 | -0.697 | 7.068%
21 | 9.62 | 1.953 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.134 | 0.97 | -3.134 | -4.745 | 5.263 | 8.919 | 1.811 | -0.701 | 7.289%
22 | 9.139 | 1.856 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -2.883 | 0.97 | -2.883 | -5.031 | 5.263 | 8.432 | 1.712 | -0.707 | 7.733%
23 | 8.547 | 1.736 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.971 | -2.598 | 0.971 | -2.598 | -5.263 | 5.263 | 7.856 | 1.595 | -0.691 | 8.088%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.973 | -2.396 | 0.973 | -2.396 | -5.263 | 5.263 | 7.397 | 1.502 | -0.65 | 8.078%
1 | 7.716 | 1.567 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.975 | -2.263 | 0.975 | -2.263 | -5.263 | 5.263 | 7.093 | 1.44 | -0.623 | 8.069%
2 | 7.517 | 1.526 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.976 | -2.184 | 0.976 | -2.184 | -5.263 | 5.263 | 6.911 | 1.403 | -0.606 | 8.064%
3 | 7.407 | 1.504 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.976 | -2.14 | 0.976 | -2.14 | -5.263 | 5.263 | 6.81 | 1.383 | -0.597 | 8.061%
4 | 7.398 | 1.502 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.976 | -2.136 | 0.976 | -2.136 | -5.263 | 5.263 | 6.802 | 1.381 | -0.596 | 8.06%
5 | 7.563 | 1.536 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.976 | -2.202 | 0.976 | -2.202 | -5.263 | 5.263 | 6.953 | 1.412 | -0.61 | 8.065%
6 | 7.986 | 1.622 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.974 | -2.372 | 0.974 | -2.372 | -5.263 | 5.263 | 7.341 | 1.491 | -0.645 | 8.076%
7 | 8.626 | 1.752 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.971 | -2.63 | 0.971 | -2.63 | -5.263 | 5.263 | 7.928 | 1.61 | -0.698 | 8.09%
8 | 9.059 | 1.84 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -2.841 | 0.97 | -2.841 | -5.078 | 5.263 | 8.352 | 1.696 | -0.707 | 7.806%
9 | 9.181 | 1.864 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -2.905 | 0.97 | -2.905 | -5.006 | 5.263 | 8.475 | 1.721 | -0.706 | 7.694%
10 | 9.23 | 1.874 | 0.98 | Z | cloudy | 5.263 | 5.258 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -2.93 | 0.97 | -2.93 | -4.977 | 5.258 | 8.524 | 1.731 | -0.706 | 7.65%
11 | 9.261 | 1.881 | 0.98 | Z | cloudy | 5.263 | 5.242 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -2.946 | 0.97 | -2.946 | -4.959 | 5.242 | 8.555 | 1.737 | -0.706 | 7.621%
12 | 9.292 | 1.887 | 0.98 | Z | cloudy | 5.263 | 5.226 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -2.962 | 0.97 | -2.962 | -4.941 | 5.226 | 8.586 | 1.744 | -0.706 | 7.593%
13 | 9.322 | 1.893 | 0.98 | Z | cloudy | 5.263 | 5.226 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -2.978 | 0.97 | -2.978 | -4.923 | 5.226 | 8.617 | 1.75 | -0.705 | 7.565%
14 | 9.338 | 1.896 | 0.98 | Z | cloudy | 5.263 | 5.237 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -2.986 | 0.97 | -2.986 | -4.913 | 5.237 | 8.633 | 1.753 | -0.705 | 7.55%
15 | 9.404 | 1.91 | 0.98 | Z | cloudy | 5.263 | 5.252 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.021 | 0.97 | -3.021 | -4.874 | 5.252 | 8.7 | 1.767 | -0.704 | 7.49%
16 | 9.594 | 1.948 | 0.98 | Z | cloudy | 5.263 | 5.258 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.121 | 0.97 | -3.121 | -4.76 | 5.258 | 8.892 | 1.806 | -0.702 | 7.314%
17 | 9.883 | 2.007 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.273 | 0.97 | -3.273 | -4.586 | 5.263 | 9.187 | 1.865 | -0.696 | 7.044%
18 | 10 | 2.031 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.335 | 0.97 | -3.335 | -4.515 | 5.263 | 9.307 | 1.89 | -0.693 | 6.934%
19 | 9.966 | 2.024 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.317 | 0.97 | -3.317 | -4.535 | 5.263 | 9.272 | 1.883 | -0.694 | 6.966%
20 | 9.857 | 2.002 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.098 | 1.006 | -4.098 | 0.97 | -3.259 | 0.97 | -3.259 | -4.602 | 5.263 | 9.16 | 1.86 | -0.697 | 7.068%
21 | 9.62 | 1.953 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.134 | 0.97 | -3.134 | -4.745 | 5.263 | 8.919 | 1.811 | -0.701 | 7.289%
22 | 9.139 | 1.856 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -2.883 | 0.97 | -2.883 | -5.031 | 5.263 | 8.432 | 1.712 | -0.707 | 7.733%
23 | 8.547 | 1.736 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.971 | -2.598 | 0.971 | -2.598 | -5.263 | 5.263 | 7.856 | 1.595 | -0.691 | 8.088%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.973 | -2.396 | 0.973 | -2.396 | -5.263 | 5.263 | 7.397 | 1.502 | -0.65 | 8.078%
1 | 7.716 | 1.567 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.156 | 0.97 | -2.156 | -5.848 | 10.526 | 7.022 | 1.426 | -0.694 | 8.998%
2 | 7.517 | 1.526 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.056 | 0.97 | -2.056 | -5.958 | 10.526 | 6.828 | 1.386 | -0.689 | 9.17%
3 | 7.407 | 1.504 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.001 | 0.97 | -2.001 | -6.019 | 10.526 | 6.721 | 1.365 | -0.686 | 9.265%
4 | 7.398 | 1.502 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -1.997 | 0.97 | -1.997 | -6.024 | 10.526 | 6.712 | 1.363 | -0.686 | 9.273%
5 | 7.563 | 1.536 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.079 | 0.97 | -2.079 | -5.933 | 10.526 | 6.872 | 1.396 | -0.691 | 9.131%
6 | 7.986 | 1.622 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.292 | 0.97 | -2.292 | -5.696 | 10.526 | 7.286 | 1.48 | -0.7 | 8.764%
7 | 8.626 | 1.752 | 0.98 | Z | very sunny | 10.526 | 10.505 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.618 | 0.97 | -2.618 | -5.331 | 10.505 | 7.919 | 1.608 | -0.707 | 8.197%
8 | 9.059 | 1.84 | 0.98 | Z | very sunny | 10.526 | 10.231 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -2.841 | 0.97 | -2.841 | -5.078 | 10.231 | 8.352 | 1.696 | -0.707 | 7.806%
9 | 9.181 | 1.864 | 0.98 | Z | very sunny | 10.526 | 9.41 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -2.905 | 0.97 | -2.905 | -5.006 | 9.41 | 8.475 | 1.721 | -0.706 | 7.694%
10 | 9.23 | 1.874 | 0.98 | Z | very sunny | 10.526 | 8.284 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -2.93 | 0.97 | -2.93 | -4.977 | 8.284 | 8.524 | 1.731 | -0.706 | 7.65%
11 | 9.261 | 1.881 | 0.98 | Z | very sunny | 10.526 | 7.147 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -2.946 | 0.97 | -2.946 | -4.959 | 7.147 | 8.555 | 1.737 | -0.706 | 7.621%
12 | 9.292 | 1.887 | 0.98 | Z | very sunny | 10.526 | 6.516 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -2.962 | 0.97 | -2.962 | -4.941 | 6.516 | 8.586 | 1.744 | -0.706 | 7.593%
13 | 9.322 | 1.893 | 0.98 | Z | very sunny | 10.526 | 6.705 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -2.978 | 0.97 | -2.978 | -4.923 | 6.705 | 8.617 | 1.75 | -0.705 | 7.565%
14 | 9.338 | 1.896 | 0.98 | Z | very sunny | 10.526 | 7.01 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -2.986 | 0.97 | -2.986 | -4.913 | 7.01 | 8.633 | 1.753 | -0.705 | 7.55%
15 | 9.404 | 1.91 | 0.98 | Z | very sunny | 10.526 | 7.884 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.021 | 0.97 | -3.021 | -4.874 | 7.884 | 8.7 | 1.767 | -0.704 | 7.49%
16 | 9.594 | 1.948 | 0.98 | Z | very sunny | 10.526 | 8.916 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.121 | 0.97 | -3.121 | -4.76 | 8.916 | 8.892 | 1.806 | -0.702 | 7.314%
17 | 9.883 | 2.007 | 0.98 | Z | very sunny | 10.526 | 9.842 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.273 | 0.97 | -3.273 | -4.586 | 9.842 | 9.187 | 1.865 | -0.696 | 7.044%
18 | 10 | 2.031 | 0.98 | Z | very sunny | 10.526 | 10.379 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.335 | 0.97 | -3.335 | -4.515 | 10.379 | 9.307 | 1.89 | -0.693 | 6.934%
19 | 9.966 | 2.024 | 0.98 | Z | very sunny | 10.526 | 10.515 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.317 | 0.97 | -3.317 | -4.535 | 10.515 | 9.272 | 1.883 | -0.694 | 6.966%
20 | 9.857 | 2.002 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.006 | -4.098 | 1.006 | -4.098 | 0.97 | -3.259 | 0.97 | -3.259 | -4.602 | 10.526 | 9.16 | 1.86 | -0.697 | 7.068%
21 | 9.62 | 1.953 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.134 | 0.97 | -3.134 | -4.745 | 10.526 | 8.919 | 1.811 | -0.701 | 7.289%
22 | 9.139 | 1.856 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -2.883 | 0.97 | -2.883 | -5.031 | 10.526 | 8.432 | 1.712 | -0.707 | 7.733%
23 | 8.547 | 1.736 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.577 | 0.97 | -2.577 | -5.376 | 10.526 | 7.84 | 1.592 | -0.707 | 8.267%
24 | 8.047 | 1.634 | 0.98 | Z | very sunny | 10.526 | 10.526 | 5 | 1.015 | -3.32 | 1.015 | -3.32 | 0.97 | -2.323 | 0.97 | -2.323 | -5.662 | 10.526 | 7.346 | 1.492 | -0.701 | 8.71%
1 | 7.716 | 1.567 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.156 | 0.97 | -2.156 | -5.848 | 10.526 | 7.022 | 1.426 | -0.694 | 8.999%
2 | 7.517 | 1.526 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.056 | 0.97 | -2.056 | -5.958 | 10.526 | 6.828 | 1.386 | -0.689 | 9.17%
3 | 7.407 | 1.504 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.001 | 0.97 | -2.001 | -6.019 | 10.526 | 6.721 | 1.365 | -0.686 | 9.265%
4 | 7.398 | 1.502 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -1.997 | 0.97 | -1.997 | -6.024 | 10.526 | 6.712 | 1.363 | -0.686 | 9.273%
5 | 7.563 | 1.536 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.079 | 0.97 | -2.079 | -5.933 | 10.526 | 6.872 | 1.396 | -0.691 | 9.131%
6 | 7.986 | 1.622 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.292 | 0.97 | -2.292 | -5.696 | 10.526 | 7.286 | 1.48 | -0.7 | 8.764%
7 | 8.626 | 1.752 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.618 | 0.97 | -2.618 | -5.331 | 10.526 | 7.919 | 1.608 | -0.707 | 8.197%
8 | 9.059 | 1.84 | 0.98 | Z | moderate sun | 10.526 | 10.515 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -2.841 | 0.97 | -2.841 | -5.078 | 10.515 | 8.352 | 1.696 | -0.707 | 7.806%
9 | 9.181 | 1.864 | 0.98 | Z | moderate sun | 10.526 | 10.41 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -2.905 | 0.97 | -2.905 | -5.006 | 10.41 | 8.475 | 1.721 | -0.706 | 7.694%
10 | 9.23 | 1.874 | 0.98 | Z | moderate sun | 10.526 | 10.189 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -2.93 | 0.97 | -2.93 | -4.977 | 10.189 | 8.524 | 1.731 | -0.706 | 7.65%
11 | 9.261 | 1.881 | 0.98 | Z | moderate sun | 10.526 | 9.958 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -2.946 | 0.97 | -2.946 | -4.959 | 9.958 | 8.555 | 1.737 | -0.706 | 7.621%
12 | 9.292 | 1.887 | 0.98 | Z | moderate sun | 10.526 | 9.831 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -2.962 | 0.97 | -2.962 | -4.941 | 9.831 | 8.586 | 1.744 | -0.706 | 7.593%
13 | 9.322 | 1.893 | 0.98 | Z | moderate sun | 10.526 | 9.968 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -2.978 | 0.97 | -2.978 | -4.923 | 9.968 | 8.617 | 1.75 | -0.705 | 7.565%
14 | 9.338 | 1.896 | 0.98 | Z | moderate sun | 10.526 | 10.031 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -2.986 | 0.97 | -2.986 | -4.913 | 10.031 | 8.633 | 1.753 | -0.705 | 7.55%
15 | 9.404 | 1.91 | 0.98 | Z | moderate sun | 10.526 | 10.294 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.021 | 0.97 | -3.021 | -4.874 | 10.294 | 8.7 | 1.767 | -0.704 | 7.49%
16 | 9.594 | 1.948 | 0.98 | Z | moderate sun | 10.526 | 10.473 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.121 | 0.97 | -3.121 | -4.76 | 10.473 | 8.892 | 1.806 | -0.702 | 7.314%
17 | 9.883 | 2.007 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.273 | 0.97 | -3.273 | -4.586 | 10.526 | 9.187 | 1.865 | -0.696 | 7.044%
18 | 10 | 2.031 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.335 | 0.97 | -3.335 | -4.515 | 10.526 | 9.307 | 1.89 | -0.693 | 6.934%
19 | 9.966 | 2.024 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.317 | 0.97 | -3.317 | -4.535 | 10.526 | 9.272 | 1.883 | -0.694 | 6.966%
20 | 9.857 | 2.002 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.098 | 1.006 | -4.098 | 0.97 | -3.259 | 0.97 | -3.259 | -4.602 | 10.526 | 9.16 | 1.86 | -0.697 | 7.068%
21 | 9.62 | 1.953 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.134 | 0.97 | -3.134 | -4.745 | 10.526 | 8.919 | 1.811 | -0.701 | 7.289%
22 | 9.139 | 1.856 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -2.883 | 0.97 | -2.883 | -5.031 | 10.526 | 8.432 | 1.712 | -0.707 | 7.733%
23 | 8.547 | 1.736 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.577 | 0.97 | -2.577 | -5.376 | 10.526 | 7.84 | 1.592 | -0.707 | 8.267%
24 | 8.047 | 1.634 | 0.98 | Z | moderate sun | 10.526 | 10.526 | 5 | 1.015 | -3.32 | 1.015 | -3.32 | 0.97 | -2.323 | 0.97 | -2.323 | -5.662 | 10.526 | 7.346 | 1.492 | -0.701 | 8.71%
1 | 7.716 | 1.567 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.156 | 0.97 | -2.156 | -5.848 | 10.526 | 7.022 | 1.426 | -0.694 | 8.999%
2 | 7.517 | 1.526 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.056 | 0.97 | -2.056 | -5.958 | 10.526 | 6.828 | 1.386 | -0.689 | 9.17%
3 | 7.407 | 1.504 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.001 | 0.97 | -2.001 | -6.019 | 10.526 | 6.721 | 1.365 | -0.686 | 9.265%
4 | 7.398 | 1.502 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -1.997 | 0.97 | -1.997 | -6.024 | 10.526 | 6.712 | 1.363 | -0.686 | 9.273%
5 | 7.563 | 1.536 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.079 | 0.97 | -2.079 | -5.933 | 10.526 | 6.872 | 1.396 | -0.691 | 9.131%
6 | 7.986 | 1.622 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.292 | 0.97 | -2.292 | -5.696 | 10.526 | 7.286 | 1.48 | -0.7 | 8.764%
7 | 8.626 | 1.752 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.618 | 0.97 | -2.618 | -5.331 | 10.526 | 7.919 | 1.608 | -0.707 | 8.197%
8 | 9.059 | 1.84 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -2.841 | 0.97 | -2.841 | -5.078 | 10.526 | 8.352 | 1.696 | -0.707 | 7.806%
9 | 9.181 | 1.864 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -2.905 | 0.97 | -2.905 | -5.006 | 10.526 | 8.475 | 1.721 | -0.706 | 7.694%
10 | 9.23 | 1.874 | 0.98 | Z | cloudy | 10.526 | 10.515 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -2.93 | 0.97 | -2.93 | -4.977 | 10.515 | 8.524 | 1.731 | -0.706 | 7.65%
11 | 9.261 | 1.881 | 0.98 | Z | cloudy | 10.526 | 10.484 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -2.946 | 0.97 | -2.946 | -4.959 | 10.484 | 8.555 | 1.737 | -0.706 | 7.621%
12 | 9.292 | 1.887 | 0.98 | Z | cloudy | 10.526 | 10.452 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -2.962 | 0.97 | -2.962 | -4.941 | 10.452 | 8.586 | 1.744 | -0.706 | 7.593%
13 | 9.322 | 1.893 | 0.98 | Z | cloudy | 10.526 | 10.452 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -2.978 | 0.97 | -2.978 | -4.923 | 10.452 | 8.617 | 1.75 | -0.705 | 7.565%
14 | 9.338 | 1.896 | 0.98 | Z | cloudy | 10.526 | 10.473 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -2.986 | 0.97 | -2.986 | -4.913 | 10.473 | 8.633 | 1.753 | -0.705 | 7.55%
15 | 9.404 | 1.91 | 0.98 | Z | cloudy | 10.526 | 10.505 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.021 | 0.97 | -3.021 | -4.874 | 10.505 | 8.7 | 1.767 | -0.704 | 7.49%
16 | 9.594 | 1.948 | 0.98 | Z | cloudy | 10.526 | 10.515 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.121 | 0.97 | -3.121 | -4.76 | 10.515 | 8.892 | 1.806 | -0.702 | 7.314%
17 | 9.883 | 2.007 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.273 | 0.97 | -3.273 | -4.586 | 10.526 | 9.187 | 1.865 | -0.696 | 7.044%
18 | 10 | 2.031 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.335 | 0.97 | -3.335 | -4.515 | 10.526 | 9.307 | 1.89 | -0.693 | 6.934%
19 | 9.966 | 2.024 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.317 | 0.97 | -3.317 | -4.535 | 10.526 | 9.272 | 1.883 | -0.694 | 6.966%
20 | 9.857 | 2.002 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.098 | 1.006 | -4.098 | 0.97 | -3.259 | 0.97 | -3.259 | -4.602 | 10.526 | 9.16 | 1.86 | -0.697 | 7.068%
21 | 9.62 | 1.953 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.134 | 0.97 | -3.134 | -4.745 | 10.526 | 8.919 | 1.811 | -0.701 | 7.289%
22 | 9.139 | 1.856 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -2.883 | 0.97 | -2.883 | -5.031 | 10.526 | 8.432 | 1.712 | -0.707 | 7.733%
23 | 8.547 | 1.736 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.577 | 0.97 | -2.577 | -5.376 | 10.526 | 7.84 | 1.592 | -0.707 | 8.267%
24 | 8.047 | 1.634 | 0.98 | Z | cloudy | 10.526 | 10.526 | 5 | 1.015 | -3.32 | 1.015 | -3.32 | 0.97 | -2.323 | 0.97 | -2.323 | -5.662 | 10.526 | 7.346 | 1.492 | -0.701 | 8.71%

## ConstantILoad(Consolidated Data
Input Parameters | [8 empty] | NO CVR Voltages and Angles |  |  |  | WITH CVR Voltages and Angles |  |  |  | WITH CVR Q output and load |  |  |  | WITH VS WITHOUT CVR
hour | load |  | PF | load type | sun rating | PV_size | Q limit | PV bus # | PV bus V | PV bus angle | Load bus (5) V | Load bus (5) angle | PV bus V pu | PV bus angle | Load bus (5) pu | Load bus (5) angle | PV bus Q output | PV bus Q limit | load |  | Reduction in P
hour | MW | MVAR | PF | load type | sun rating | MVA | MVAR | PV Bus # | pu | degrees | pu | degrees | pu | degrees | pu | degrees | MVAR | MVAR | MW | MVAR | MW reduction | %
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.92 | 1.023 | -0.9 | 0.985 | -2.797 | -5.263 | 5.263 | 7.613 | 3.687 | -0.103 | 1.335%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.873 | 0.987 | -2.718 | -5.263 | 5.263 | 7.417 | 3.592 | -0.1 | 1.33% | *MUST
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.859 | 0.988 | -2.675 | -5.263 | 5.263 | 7.309 | 3.54 | -0.098 | 1.323% | PF: Exterme case( and average PF
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.857 | 0.988 | -2.671 | -5.263 | 5.263 | 7.3 | 3.535 | -0.098 | 1.325%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.879 | 0.987 | -2.737 | -5.263 | 5.263 | 7.463 | 3.614 | -0.1 | 1.322%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.936 | 0.983 | -2.904 | -5.263 | 5.263 | 7.88 | 3.816 | -0.106 | 1.327%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 5.263 | 5.252 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.021 | -1.022 | 0.979 | -3.161 | -5.252 | 5.252 | 8.511 | 4.122 | -0.115 | 1.333%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 5.263 | 5.116 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 5.116 | 8.968 | 4.343 | -0.091 | 1.005% | Combine Constant Load and Constant Z and average them to create a graph
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 5.263 | 4.705 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 4.705 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 5.263 | 4.142 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 4.142 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 5.263 | 3.574 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.155 | 0.978 | -3.471 | -3.574 | 3.574 | 9.175 | 4.443 | -0.086 | 0.9286%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 5.263 | 3.258 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.025 | -1.166 | 0.979 | -3.486 | -3.258 | 3.258 | 9.214 | 4.462 | -0.078 | 0.8394%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 5.263 | 3.353 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.025 | -1.168 | 0.978 | -3.497 | -3.353 | 3.353 | 9.241 | 4.476 | -0.081 | 0.8689%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 5.263 | 3.505 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.024 | -1.167 | 0.978 | -3.503 | -3.505 | 3.505 | 9.253 | 4.481 | -0.085 | 0.9103%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 5.263 | 3.942 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 3.942 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 5.263 | 4.458 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 4.458 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 5.263 | 4.921 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 4.921 | 9.783 | 4.738 | -0.1 | 1.012%
18 | 10 | 4.843 | 0.9 | I | very sunny | 5.263 | 5.189 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 5.189 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 5.263 | 5.258 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 5.258 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.011 | 0.979 | -3.129 | -5.263 | 5.263 | 8.433 | 4.084 | -0.114 | 1.334%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.944 | 0.983 | -2.929 | -5.263 | 5.263 | 7.94 | 3.845 | -0.107 | 1.33%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.023 | -0.9 | 0.985 | -2.797 | -5.263 | 5.263 | 7.613 | 3.687 | -0.103 | 1.335%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.873 | 0.987 | -2.718 | -5.263 | 5.263 | 7.417 | 3.592 | -0.1 | 1.33%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.859 | 0.988 | -2.675 | -5.263 | 5.263 | 7.309 | 3.54 | -0.098 | 1.323%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.857 | 0.988 | -2.671 | -5.263 | 5.263 | 7.3 | 3.535 | -0.098 | 1.325%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.879 | 0.987 | -2.737 | -5.263 | 5.263 | 7.463 | 3.614 | -0.1 | 1.322%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.936 | 0.983 | -2.904 | -5.263 | 5.263 | 7.88 | 3.816 | -0.106 | 1.327%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.021 | -1.021 | 0.979 | -3.161 | -5.263 | 5.263 | 8.511 | 4.122 | -0.115 | 1.333%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 5.263 | 5.258 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 5.258 | 8.968 | 4.343 | -0.091 | 1.005%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 5.263 | 5.205 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 5.205 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 5.263 | 5.095 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 5.095 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 5.263 | 4.979 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 4.979 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 5.263 | 4.916 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 4.916 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 5.263 | 4.984 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 4.984 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 5.263 | 5.016 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 5.016 | 9.244 | 4.477 | -0.094 | 1.007%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 5.263 | 5.147 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 5.147 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 5.263 | 5.237 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 5.237 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 5.263 | 9.783 | 4.738 | -0.1 | 1.012%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.011 | 0.979 | -3.129 | -5.263 | 5.263 | 8.433 | 4.084 | -0.114 | 1.334%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.944 | 0.983 | -2.929 | -5.263 | 5.263 | 7.94 | 3.845 | -0.107 | 1.33%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.023 | -0.9 | 0.985 | -2.797 | -5.263 | 5.263 | 7.613 | 3.687 | -0.103 | 1.335%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.024 | -0.873 | 0.987 | -2.718 | -5.263 | 5.263 | 7.417 | 3.592 | -0.1 | 1.33%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.024 | -0.859 | 0.988 | -2.675 | -5.263 | 5.263 | 7.309 | 3.54 | -0.098 | 1.323%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.024 | -0.857 | 0.988 | -2.671 | -5.263 | 5.263 | 7.3 | 3.535 | -0.098 | 1.325%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.024 | -0.879 | 0.987 | -2.737 | -5.263 | 5.263 | 7.463 | 3.614 | -0.1 | 1.322%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.023 | -0.936 | 0.983 | -2.904 | -5.263 | 5.263 | 7.88 | 3.816 | -0.106 | 1.327%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.021 | -1.021 | 0.979 | -3.161 | -5.263 | 5.263 | 8.511 | 4.122 | -0.115 | 1.333%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 5.263 | 8.968 | 4.343 | -0.091 | 1.005%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 5.263 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 5.263 | 5.258 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 5.258 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 5.263 | 5.242 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 5.242 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 5.263 | 5.226 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 5.226 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 5.263 | 5.226 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 5.226 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 5.263 | 5.237 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 5.237 | 9.244 | 4.477 | -0.094 | 1.007%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 5.263 | 5.252 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 5.252 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 5.263 | 5.258 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 5.258 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 5.263 | 9.783 | 4.738 | -0.1 | 1.012%
18 | 10 | 4.843 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.022 | -1.011 | 0.979 | -3.129 | -5.263 | 5.263 | 8.433 | 4.084 | -0.114 | 1.334%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.023 | -0.944 | 0.983 | -2.929 | -5.263 | 5.263 | 7.94 | 3.845 | -0.107 | 1.33%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.848 | 0.979 | -2.771 | -7.636 | 10.526 | 7.562 | 3.662 | -0.154 | 1.996%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.748 | 0.973 | -2.627 | -10.526 | 10.526 | 7.309 | 3.54 | -0.208 | 2.767%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.733 | 0.973 | -2.583 | -10.526 | 10.526 | 7.202 | 3.488 | -0.205 | 2.768%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.732 | 0.973 | -2.58 | -10.526 | 10.526 | 7.194 | 3.484 | -0.204 | 2.757%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.017 | -0.828 | 0.98 | -2.71 | -7.637 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.885 | 0.977 | -2.88 | -7.632 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 10.526 | 10.505 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.971 | 0.972 | -3.139 | -7.624 | 10.505 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 10.526 | 10.231 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 10.231 | 8.968 | 4.343 | -0.091 | 1.005%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 10.526 | 9.41 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 9.41 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 10.526 | 8.284 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 8.284 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 10.526 | 7.147 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 7.147 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 10.526 | 6.516 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 6.516 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 10.526 | 6.705 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 6.705 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 10.526 | 7.01 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 7.01 | 9.244 | 4.477 | -0.094 | 1.007%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 10.526 | 7.884 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 7.884 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 10.526 | 8.916 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 8.916 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 10.526 | 9.842 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 9.842 | 9.783 | 4.738 | -0.1 | 1.012%
18 | 10 | 4.843 | 0.9 | I | very sunny | 10.526 | 10.379 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 10.379 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 10.526 | 10.515 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 10.515 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.96 | 0.973 | -3.107 | -7.625 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.893 | 0.976 | -2.904 | -7.631 | 10.526 | 7.886 | 3.819 | -0.161 | 2.001%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.848 | 0.979 | -2.771 | -7.635 | 10.526 | 7.562 | 3.662 | -0.154 | 1.996%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.748 | 0.973 | -2.627 | -10.526 | 10.526 | 7.309 | 3.54 | -0.208 | 2.767%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.733 | 0.973 | -2.583 | -10.526 | 10.526 | 7.202 | 3.488 | -0.205 | 2.768%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.732 | 0.973 | -2.58 | -10.526 | 10.526 | 7.194 | 3.484 | -0.204 | 2.757%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.017 | -0.828 | 0.98 | -2.71 | -7.637 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.885 | 0.977 | -2.88 | -7.632 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.971 | 0.972 | -3.139 | -7.624 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 10.526 | 10.515 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 10.515 | 8.968 | 4.343 | -0.091 | 1.005%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 10.526 | 10.41 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 10.41 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 10.526 | 10.189 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 10.189 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 10.526 | 9.958 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 9.958 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 10.526 | 9.831 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 9.831 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 10.526 | 9.968 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 9.968 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 10.526 | 10.031 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 10.031 | 9.244 | 4.477 | -0.094 | 1.007%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 10.526 | 10.294 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 10.294 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 10.526 | 10.473 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 10.473 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 10.526 | 9.783 | 4.738 | -0.1 | 1.012%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.96 | 0.973 | -3.107 | -7.625 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.893 | 0.976 | -2.904 | -7.631 | 10.526 | 7.886 | 3.819 | -0.161 | 2.001%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.033 | 0.999 | -2.919 | 1.017 | -0.848 | 0.979 | -2.771 | -7.635 | 10.526 | 7.562 | 3.662 | -0.154 | 1.996%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.006 | 1 | -2.841 | 1.01 | -0.748 | 0.973 | -2.627 | -10.526 | 10.526 | 7.309 | 3.54 | -0.208 | 2.767%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -0.991 | 1.001 | -2.797 | 1.01 | -0.733 | 0.973 | -2.583 | -10.526 | 10.526 | 7.202 | 3.488 | -0.205 | 2.768%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -0.99 | 1.001 | -2.794 | 1.01 | -0.732 | 0.973 | -2.58 | -10.526 | 10.526 | 7.194 | 3.484 | -0.204 | 2.757%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.012 | 1 | -2.859 | 1.017 | -0.828 | 0.98 | -2.71 | -7.637 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.069 | 0.997 | -3.027 | 1.016 | -0.885 | 0.977 | -2.88 | -7.632 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.156 | 0.992 | -3.283 | 1.015 | -0.971 | 0.972 | -3.139 | -7.624 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.215 | 0.989 | -3.458 | 1.024 | -1.122 | 0.979 | -3.386 | -3.849 | 10.526 | 8.968 | 4.343 | -0.091 | 1.005%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.231 | 0.988 | -3.508 | 1.024 | -1.138 | 0.978 | -3.436 | -3.848 | 10.526 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 10.526 | 10.515 | 3 | 1.034 | -1.238 | 0.987 | -3.528 | 1.024 | -1.145 | 0.977 | -3.456 | -3.848 | 10.515 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 10.526 | 10.484 | 3 | 1.034 | -1.242 | 0.987 | -3.54 | 1.024 | -1.149 | 0.977 | -3.469 | -3.848 | 10.484 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 10.526 | 10.452 | 3 | 1.034 | -1.246 | 0.987 | -3.553 | 1.024 | -1.153 | 0.977 | -3.481 | -3.847 | 10.452 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 10.526 | 10.452 | 3 | 1.034 | -1.25 | 0.987 | -3.565 | 1.024 | -1.158 | 0.977 | -3.494 | -3.847 | 10.452 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 10.526 | 10.473 | 3 | 1.033 | -1.253 | 0.987 | -3.572 | 1.023 | -1.16 | 0.977 | -3.5 | -3.847 | 10.473 | 9.244 | 4.477 | -0.094 | 1.007%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 10.526 | 10.505 | 3 | 1.033 | -1.262 | 0.986 | -3.599 | 1.023 | -1.169 | 0.976 | -3.527 | -3.847 | 10.505 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 10.526 | 10.515 | 3 | 1.033 | -1.288 | 0.985 | -3.676 | 1.023 | -1.195 | 0.975 | -3.605 | -3.846 | 10.515 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.327 | 0.982 | -3.795 | 1.022 | -1.234 | 0.972 | -3.725 | -3.844 | 10.526 | 9.783 | 4.738 | -0.1 | 1.012%
18 | 10 | 4.843 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.343 | 0.981 | -3.843 | 1.022 | -1.25 | 0.971 | -3.773 | -3.843 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.339 | 0.982 | -3.829 | 1.022 | -1.246 | 0.972 | -3.759 | -3.843 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.032 | -1.324 | 0.983 | -3.784 | 1.022 | -1.231 | 0.973 | -3.714 | -3.844 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.033 | -1.291 | 0.984 | -3.687 | 1.023 | -1.198 | 0.974 | -3.616 | -3.845 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.034 | -1.225 | 0.988 | -3.491 | 1.024 | -1.133 | 0.978 | -3.419 | -3.848 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.145 | 0.993 | -3.251 | 1.015 | -0.96 | 0.973 | -3.107 | -7.625 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.077 | 0.996 | -3.051 | 1.016 | -0.893 | 0.976 | -2.904 | -7.631 | 10.526 | 7.886 | 3.819 | -0.161 | 2.001%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 5.263 | 7.561 | 3.662 | -0.155 | 2.009%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.99 | -1.451 | 0.972 | -2.41 | -5.263 | 5.263 | 7.303 | 3.537 | -0.214 | 2.847%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.991 | -1.423 | 0.973 | -2.366 | -5.263 | 5.263 | 7.196 | 3.485 | -0.211 | 2.849%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.991 | -1.421 | 0.973 | -2.363 | -5.263 | 5.263 | 7.188 | 3.481 | -0.21 | 2.839%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 5.263 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 5.263 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 5.263 | 5.252 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 5.252 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 5.263 | 5.116 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 5.116 | 8.967 | 4.343 | -0.092 | 1.016%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 5.263 | 4.705 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 4.705 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 5.263 | 4.142 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 4.142 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 5.263 | 3.574 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 3.574 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 5.263 | 3.258 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 3.258 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 5.263 | 3.353 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 3.353 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 5.263 | 3.505 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 3.505 | 9.243 | 4.477 | -0.095 | 1.017%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 5.263 | 3.942 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 3.942 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 5.263 | 4.458 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 4.458 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 5.263 | 4.921 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 4.921 | 9.782 | 4.738 | -0.101 | 1.022%
18 | 10 | 4.843 | 0.9 | I | very sunny | 5.263 | 5.189 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 5.189 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 5.263 | 5.258 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 5.258 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 5.263 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 5.263 | 7.885 | 3.819 | -0.162 | 2.013%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 5.263 | 7.561 | 3.662 | -0.155 | 2.009%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.99 | -1.451 | 0.972 | -2.41 | -5.263 | 5.263 | 7.303 | 3.537 | -0.214 | 2.847%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.991 | -1.423 | 0.973 | -2.366 | -5.263 | 5.263 | 7.196 | 3.485 | -0.211 | 2.849%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.991 | -1.421 | 0.973 | -2.363 | -5.263 | 5.263 | 7.188 | 3.481 | -0.21 | 2.839%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 5.263 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 5.263 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 5.263 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 5.263 | 5.258 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 5.258 | 8.967 | 4.343 | -0.092 | 1.016%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 5.263 | 5.205 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 5.205 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 5.263 | 5.095 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 5.095 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 5.263 | 4.979 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 4.979 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 5.263 | 4.916 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 4.916 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 5.263 | 4.984 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 4.984 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 5.263 | 5.016 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 5.016 | 9.243 | 4.477 | -0.095 | 1.017%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 5.263 | 5.147 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 5.147 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 5.263 | 5.237 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 5.237 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 5.263 | 9.782 | 4.738 | -0.101 | 1.022%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 5.263 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 5.263 | 7.885 | 3.819 | -0.162 | 2.013%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 5.263 | 7.561 | 3.662 | -0.155 | 2.009%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.99 | -1.451 | 0.972 | -2.41 | -5.263 | 5.263 | 7.303 | 3.537 | -0.214 | 2.847%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.991 | -1.423 | 0.973 | -2.366 | -5.263 | 5.263 | 7.196 | 3.485 | -0.211 | 2.849%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.991 | -1.421 | 0.973 | -2.363 | -5.263 | 5.263 | 7.188 | 3.481 | -0.21 | 2.839%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 5.263 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 5.263 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 5.263 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 5.263 | 8.967 | 4.343 | -0.092 | 1.016%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 5.263 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 5.263 | 5.258 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 5.258 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 5.263 | 5.242 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 5.242 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 5.263 | 5.226 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 5.226 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 5.263 | 5.226 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 5.226 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 5.263 | 5.237 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 5.237 | 9.243 | 4.477 | -0.095 | 1.017%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 5.263 | 5.252 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 5.252 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 5.263 | 5.258 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 5.258 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 5.263 | 9.782 | 4.738 | -0.101 | 1.022%
18 | 10 | 4.843 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 5.263 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 5.263 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 5.263 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 5.263 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 5.263 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 5.263 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 5.263 | 7.885 | 3.819 | -0.162 | 2.013%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 10.526 | 7.561 | 3.662 | -0.155 | 2.009%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.431 | 0.97 | -2.393 | -5.521 | 10.526 | 7.292 | 3.531 | -0.225 | 2.993%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.403 | 0.971 | -2.349 | -5.523 | 10.526 | 7.185 | 3.48 | -0.222 | 2.997%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.4 | 0.971 | -2.346 | -5.523 | 10.526 | 7.176 | 3.476 | -0.222 | 3.001%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 10.526 | 10.505 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 10.505 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 10.526 | 10.231 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 10.231 | 8.967 | 4.343 | -0.092 | 1.016%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 10.526 | 9.41 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 9.41 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 10.526 | 8.284 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 8.284 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 10.526 | 7.147 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 7.147 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 10.526 | 6.516 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 6.516 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 10.526 | 6.705 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 6.705 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 10.526 | 7.01 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 7.01 | 9.243 | 4.477 | -0.095 | 1.017%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 10.526 | 7.884 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 7.884 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 10.526 | 8.916 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 8.916 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 10.526 | 9.842 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 9.842 | 9.782 | 4.738 | -0.101 | 1.022%
18 | 10 | 4.843 | 0.9 | I | very sunny | 10.526 | 10.379 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 10.379 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 10.526 | 10.515 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 10.515 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 10.526 | 7.885 | 3.819 | -0.162 | 2.013%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 10.526 | 7.561 | 3.662 | -0.155 | 2.009%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.431 | 0.97 | -2.393 | -5.521 | 10.526 | 7.292 | 3.531 | -0.225 | 2.993%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.403 | 0.971 | -2.349 | -5.523 | 10.526 | 7.185 | 3.48 | -0.222 | 2.997%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.4 | 0.971 | -2.346 | -5.523 | 10.526 | 7.176 | 3.476 | -0.222 | 3.001%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 10.526 | 10.515 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 10.515 | 8.967 | 4.343 | -0.092 | 1.016%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 10.526 | 10.41 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 10.41 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 10.526 | 10.189 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 10.189 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 10.526 | 9.958 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 9.958 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 10.526 | 9.831 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 9.831 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 10.526 | 9.968 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 9.968 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 10.526 | 10.031 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 10.031 | 9.243 | 4.477 | -0.095 | 1.017%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 10.526 | 10.294 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 10.294 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 10.526 | 10.473 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 10.473 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 10.526 | 9.782 | 4.738 | -0.101 | 1.022%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 10.526 | 7.885 | 3.819 | -0.162 | 2.013%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.018 | -1.959 | 0.999 | -2.919 | 0.998 | -1.641 | 0.979 | -2.621 | -3.717 | 10.526 | 7.561 | 3.662 | -0.155 | 2.009%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.907 | 1 | -2.841 | 0.989 | -1.431 | 0.97 | -2.393 | -5.521 | 10.526 | 7.292 | 3.531 | -0.225 | 2.993%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.878 | 1.001 | -2.797 | 0.989 | -1.403 | 0.971 | -2.349 | -5.523 | 10.526 | 7.185 | 3.48 | -0.222 | 2.997%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -1.876 | 1.001 | -2.794 | 0.989 | -1.4 | 0.971 | -2.346 | -5.523 | 10.526 | 7.176 | 3.476 | -0.222 | 3.001%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.018 | -1.919 | 1 | -2.859 | 0.998 | -1.602 | 0.98 | -2.56 | -3.719 | 10.526 | 7.412 | 3.59 | -0.151 | 1.997%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.029 | 0.997 | -3.027 | 0.996 | -1.712 | 0.977 | -2.729 | -3.713 | 10.526 | 7.826 | 3.79 | -0.16 | 2.004%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.013 | -2.197 | 0.992 | -3.283 | 0.993 | -1.879 | 0.972 | -2.986 | -3.705 | 10.526 | 8.452 | 4.094 | -0.174 | 2.017%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.312 | 0.989 | -3.458 | 1.001 | -2.152 | 0.979 | -3.31 | -1.87 | 10.526 | 8.967 | 4.343 | -0.092 | 1.016%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.344 | 0.988 | -3.508 | 1.001 | -2.184 | 0.978 | -3.359 | -1.869 | 10.526 | 9.088 | 4.402 | -0.093 | 1.013%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 10.526 | 10.515 | 4 | 1.01 | -2.357 | 0.987 | -3.528 | 1 | -2.197 | 0.977 | -3.379 | -1.869 | 10.515 | 9.137 | 4.425 | -0.093 | 1.008%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 10.526 | 10.484 | 4 | 1.01 | -2.365 | 0.987 | -3.54 | 1 | -2.205 | 0.977 | -3.392 | -1.869 | 10.484 | 9.167 | 4.44 | -0.094 | 1.015%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 10.526 | 10.452 | 4 | 1.01 | -2.373 | 0.987 | -3.553 | 1 | -2.214 | 0.977 | -3.405 | -1.868 | 10.452 | 9.198 | 4.455 | -0.094 | 1.012%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 10.526 | 10.452 | 4 | 1.01 | -2.381 | 0.987 | -3.565 | 1 | -2.222 | 0.977 | -3.417 | -1.868 | 10.452 | 9.228 | 4.469 | -0.094 | 1.008%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 10.526 | 10.473 | 4 | 1.01 | -2.386 | 0.987 | -3.572 | 1 | -2.226 | 0.977 | -3.423 | -1.868 | 10.473 | 9.243 | 4.477 | -0.095 | 1.017%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 10.526 | 10.505 | 4 | 1.01 | -2.403 | 0.986 | -3.599 | 1 | -2.243 | 0.976 | -3.45 | -1.868 | 10.505 | 9.309 | 4.508 | -0.095 | 1.01%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 10.526 | 10.515 | 4 | 1.009 | -2.454 | 0.985 | -3.676 | 0.999 | -2.294 | 0.975 | -3.528 | -1.866 | 10.515 | 9.497 | 4.599 | -0.097 | 1.011%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.531 | 0.982 | -3.795 | 0.997 | -2.371 | 0.972 | -3.647 | -1.865 | 10.526 | 9.782 | 4.738 | -0.101 | 1.022%
18 | 10 | 4.843 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.562 | 0.981 | -3.843 | 0.997 | -2.402 | 0.971 | -3.695 | -1.864 | 10.526 | 9.898 | 4.794 | -0.102 | 1.02%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.553 | 0.982 | -3.829 | 0.997 | -2.393 | 0.972 | -3.681 | -1.864 | 10.526 | 9.865 | 4.778 | -0.101 | 1.013%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.007 | -2.524 | 0.983 | -3.784 | 0.997 | -2.364 | 0.973 | -3.636 | -1.865 | 10.526 | 9.757 | 4.725 | -0.1 | 1.015%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.008 | -2.461 | 0.984 | -3.687 | 0.998 | -2.301 | 0.974 | -3.539 | -1.866 | 10.526 | 9.522 | 4.612 | -0.098 | 1.019%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.011 | -2.333 | 0.988 | -3.491 | 1.001 | -2.173 | 0.978 | -3.342 | -1.869 | 10.526 | 9.047 | 4.381 | -0.092 | 1.007%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.014 | -2.176 | 0.993 | -3.251 | 0.994 | -1.858 | 0.973 | -2.954 | -3.706 | 10.526 | 8.375 | 4.056 | -0.172 | 2.012%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.045 | 0.996 | -3.051 | 0.996 | -1.727 | 0.976 | -2.753 | -3.713 | 10.526 | 7.885 | 3.819 | -0.162 | 2.013%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 5.263 | 7.494 | 3.629 | -0.222 | 2.877%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 5.263 | 7.29 | 3.531 | -0.227 | 3.02%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 5.263 | 7.177 | 3.476 | -0.23 | 3.105%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 5.263 | 7.168 | 3.472 | -0.23 | 3.109%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 5.263 | 7.337 | 3.553 | -0.226 | 2.988%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 5.263 | 7.772 | 3.764 | -0.214 | 2.68%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 5.263 | 5.252 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 5.252 | 8.435 | 4.085 | -0.191 | 2.214%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 5.263 | 5.116 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 5.116 | 8.888 | 4.305 | -0.171 | 1.888%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 5.263 | 4.705 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 4.705 | 9.016 | 4.367 | -0.165 | 1.797%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 5.263 | 4.142 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 4.142 | 9.068 | 4.392 | -0.162 | 1.755%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 5.263 | 3.574 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 3.574 | 9.1 | 4.407 | -0.161 | 1.738%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 5.263 | 3.258 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 3.258 | 9.133 | 4.423 | -0.159 | 1.711%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 5.263 | 3.353 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 3.353 | 9.164 | 4.439 | -0.158 | 1.695%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 5.263 | 3.505 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 3.505 | 9.181 | 4.447 | -0.157 | 1.681%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 5.263 | 3.942 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 3.942 | 9.251 | 4.48 | -0.153 | 1.627%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 5.263 | 4.458 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 4.458 | 9.452 | 4.578 | -0.142 | 1.48%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 5.263 | 4.921 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 4.921 | 9.759 | 4.726 | -0.124 | 1.255%
18 | 10 | 4.843 | 0.9 | I | very sunny | 5.263 | 5.189 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 5.189 | 9.883 | 4.787 | -0.117 | 1.17%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 5.263 | 5.258 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 5.258 | 9.847 | 4.769 | -0.119 | 1.194%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 5.263 | 9.731 | 4.713 | -0.126 | 1.278%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 5.263 | 9.479 | 4.591 | -0.141 | 1.466%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 5.263 | 8.972 | 4.345 | -0.167 | 1.827%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 5.263 | 8.353 | 4.045 | -0.194 | 2.27%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 5.263 | 7.835 | 3.794 | -0.212 | 2.635%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 5.263 | 7.494 | 3.629 | -0.222 | 2.877%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 5.263 | 7.29 | 3.531 | -0.227 | 3.02%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 5.263 | 7.177 | 3.476 | -0.23 | 3.105%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 5.263 | 7.168 | 3.472 | -0.23 | 3.109%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 5.263 | 7.337 | 3.553 | -0.226 | 2.988%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 5.263 | 7.772 | 3.764 | -0.214 | 2.68%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 5.263 | 8.435 | 4.085 | -0.191 | 2.214%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 5.263 | 5.258 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 5.258 | 8.888 | 4.305 | -0.171 | 1.888%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 5.263 | 5.205 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 5.205 | 9.016 | 4.367 | -0.165 | 1.797%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 5.263 | 5.095 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 5.095 | 9.068 | 4.392 | -0.162 | 1.755%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 5.263 | 4.979 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 4.979 | 9.1 | 4.407 | -0.161 | 1.738%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 5.263 | 4.916 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 4.916 | 9.133 | 4.423 | -0.159 | 1.711%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 5.263 | 4.984 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 4.984 | 9.164 | 4.439 | -0.158 | 1.695%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 5.263 | 5.016 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 5.016 | 9.181 | 4.447 | -0.157 | 1.681%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 5.263 | 5.147 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 5.147 | 9.251 | 4.48 | -0.153 | 1.627%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 5.263 | 5.237 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 5.237 | 9.452 | 4.578 | -0.142 | 1.48%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 5.263 | 9.759 | 4.726 | -0.124 | 1.255%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 5.263 | 9.883 | 4.787 | -0.117 | 1.17%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 5.263 | 9.847 | 4.769 | -0.119 | 1.194%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 5.263 | 9.731 | 4.713 | -0.126 | 1.278%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 5.263 | 9.479 | 4.591 | -0.141 | 1.466%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 5.263 | 8.972 | 4.345 | -0.167 | 1.827%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 5.263 | 8.353 | 4.045 | -0.194 | 2.27%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 5.263 | 7.835 | 3.794 | -0.212 | 2.635%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 5.263 | 7.494 | 3.629 | -0.222 | 2.877%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 5.263 | 7.29 | 3.531 | -0.227 | 3.02%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 5.263 | 7.177 | 3.476 | -0.23 | 3.105%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 5.263 | 7.168 | 3.472 | -0.23 | 3.109%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 5.263 | 7.337 | 3.553 | -0.226 | 2.988%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 5.263 | 7.772 | 3.764 | -0.214 | 2.68%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 5.263 | 8.435 | 4.085 | -0.191 | 2.214%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 5.263 | 8.888 | 4.305 | -0.171 | 1.888%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 5.263 | 9.016 | 4.367 | -0.165 | 1.797%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 5.263 | 5.258 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 5.258 | 9.068 | 4.392 | -0.162 | 1.755%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 5.263 | 5.242 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 5.242 | 9.1 | 4.407 | -0.161 | 1.738%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 5.263 | 5.226 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 5.226 | 9.133 | 4.423 | -0.159 | 1.711%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 5.263 | 5.226 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 5.226 | 9.164 | 4.439 | -0.158 | 1.695%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 5.263 | 5.237 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 5.237 | 9.181 | 4.447 | -0.157 | 1.681%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 5.263 | 5.252 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 5.252 | 9.251 | 4.48 | -0.153 | 1.627%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 5.263 | 5.258 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 5.258 | 9.452 | 4.578 | -0.142 | 1.48%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 5.263 | 9.759 | 4.726 | -0.124 | 1.255%
18 | 10 | 4.843 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 5.263 | 9.883 | 4.787 | -0.117 | 1.17%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 5.263 | 9.847 | 4.769 | -0.119 | 1.194%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 5.263 | 9.731 | 4.713 | -0.126 | 1.278%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 5.263 | 9.479 | 4.591 | -0.141 | 1.466%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 5.263 | 8.972 | 4.345 | -0.167 | 1.827%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 5.263 | 8.353 | 4.045 | -0.194 | 2.27%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 5.263 | 7.835 | 3.794 | -0.212 | 2.635%
1 | 7.716 | 3.737 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 10.526 | 7.494 | 3.629 | -0.222 | 2.877%
2 | 7.517 | 3.641 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 10.526 | 7.29 | 3.531 | -0.227 | 3.02%
3 | 7.407 | 3.587 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 10.526 | 7.177 | 3.476 | -0.23 | 3.105%
4 | 7.398 | 3.583 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 10.526 | 7.168 | 3.472 | -0.23 | 3.109%
5 | 7.563 | 3.663 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 10.526 | 7.337 | 3.553 | -0.226 | 2.988%
6 | 7.986 | 3.868 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 10.526 | 7.772 | 3.764 | -0.214 | 2.68%
7 | 8.626 | 4.178 | 0.9 | I | very sunny | 10.526 | 10.505 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 10.505 | 8.435 | 4.085 | -0.191 | 2.214%
8 | 9.059 | 4.387 | 0.9 | I | very sunny | 10.526 | 10.231 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 10.231 | 8.888 | 4.305 | -0.171 | 1.888%
9 | 9.181 | 4.447 | 0.9 | I | very sunny | 10.526 | 9.41 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 9.41 | 9.016 | 4.367 | -0.165 | 1.797%
10 | 9.23 | 4.47 | 0.9 | I | very sunny | 10.526 | 8.284 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 8.284 | 9.068 | 4.392 | -0.162 | 1.755%
11 | 9.261 | 4.485 | 0.9 | I | very sunny | 10.526 | 7.147 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 7.147 | 9.1 | 4.407 | -0.161 | 1.738%
12 | 9.292 | 4.5 | 0.9 | I | very sunny | 10.526 | 6.516 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 6.516 | 9.133 | 4.423 | -0.159 | 1.711%
13 | 9.322 | 4.515 | 0.9 | I | very sunny | 10.526 | 6.705 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 6.705 | 9.164 | 4.439 | -0.158 | 1.695%
14 | 9.338 | 4.523 | 0.9 | I | very sunny | 10.526 | 7.01 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 7.01 | 9.181 | 4.447 | -0.157 | 1.681%
15 | 9.404 | 4.555 | 0.9 | I | very sunny | 10.526 | 7.884 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 7.884 | 9.251 | 4.48 | -0.153 | 1.627%
16 | 9.594 | 4.647 | 0.9 | I | very sunny | 10.526 | 8.916 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 8.916 | 9.452 | 4.578 | -0.142 | 1.48%
17 | 9.883 | 4.787 | 0.9 | I | very sunny | 10.526 | 9.842 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 9.842 | 9.759 | 4.726 | -0.124 | 1.255%
18 | 10 | 4.843 | 0.9 | I | very sunny | 10.526 | 10.379 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 10.379 | 9.883 | 4.787 | -0.117 | 1.17%
19 | 9.966 | 4.827 | 0.9 | I | very sunny | 10.526 | 10.515 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 10.515 | 9.847 | 4.769 | -0.119 | 1.194%
20 | 9.857 | 4.774 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 10.526 | 9.731 | 4.713 | -0.126 | 1.278%
21 | 9.62 | 4.659 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 10.526 | 9.479 | 4.591 | -0.141 | 1.466%
22 | 9.139 | 4.426 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 10.526 | 8.972 | 4.345 | -0.167 | 1.827%
23 | 8.547 | 4.14 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 10.526 | 8.353 | 4.045 | -0.194 | 2.27%
24 | 8.047 | 3.897 | 0.9 | I | very sunny | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 10.526 | 7.835 | 3.794 | -0.212 | 2.635%
1 | 7.716 | 3.737 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 10.526 | 7.494 | 3.629 | -0.222 | 2.877%
2 | 7.517 | 3.641 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 10.526 | 7.29 | 3.531 | -0.227 | 3.02%
3 | 7.407 | 3.587 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 10.526 | 7.177 | 3.476 | -0.23 | 3.105%
4 | 7.398 | 3.583 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 10.526 | 7.168 | 3.472 | -0.23 | 3.109%
5 | 7.563 | 3.663 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 10.526 | 7.337 | 3.553 | -0.226 | 2.988%
6 | 7.986 | 3.868 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 10.526 | 7.772 | 3.764 | -0.214 | 2.68%
7 | 8.626 | 4.178 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 10.526 | 8.435 | 4.085 | -0.191 | 2.214%
8 | 9.059 | 4.387 | 0.9 | I | moderate sun | 10.526 | 10.515 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 10.515 | 8.888 | 4.305 | -0.171 | 1.888%
9 | 9.181 | 4.447 | 0.9 | I | moderate sun | 10.526 | 10.41 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 10.41 | 9.016 | 4.367 | -0.165 | 1.797%
10 | 9.23 | 4.47 | 0.9 | I | moderate sun | 10.526 | 10.189 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 10.189 | 9.068 | 4.392 | -0.162 | 1.755%
11 | 9.261 | 4.485 | 0.9 | I | moderate sun | 10.526 | 9.958 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 9.958 | 9.1 | 4.407 | -0.161 | 1.738%
12 | 9.292 | 4.5 | 0.9 | I | moderate sun | 10.526 | 9.831 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 9.831 | 9.133 | 4.423 | -0.159 | 1.711%
13 | 9.322 | 4.515 | 0.9 | I | moderate sun | 10.526 | 9.968 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 9.968 | 9.164 | 4.439 | -0.158 | 1.695%
14 | 9.338 | 4.523 | 0.9 | I | moderate sun | 10.526 | 10.031 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 10.031 | 9.181 | 4.447 | -0.157 | 1.681%
15 | 9.404 | 4.555 | 0.9 | I | moderate sun | 10.526 | 10.294 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 10.294 | 9.251 | 4.48 | -0.153 | 1.627%
16 | 9.594 | 4.647 | 0.9 | I | moderate sun | 10.526 | 10.473 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 10.473 | 9.452 | 4.578 | -0.142 | 1.48%
17 | 9.883 | 4.787 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 10.526 | 9.759 | 4.726 | -0.124 | 1.255%
18 | 10 | 4.843 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 10.526 | 9.883 | 4.787 | -0.117 | 1.17%
19 | 9.966 | 4.827 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 10.526 | 9.847 | 4.769 | -0.119 | 1.194%
20 | 9.857 | 4.774 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 10.526 | 9.731 | 4.713 | -0.126 | 1.278%
21 | 9.62 | 4.659 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 10.526 | 9.479 | 4.591 | -0.141 | 1.466%
22 | 9.139 | 4.426 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 10.526 | 8.972 | 4.345 | -0.167 | 1.827%
23 | 8.547 | 4.14 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 10.526 | 8.353 | 4.045 | -0.194 | 2.27%
24 | 8.047 | 3.897 | 0.9 | I | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 10.526 | 7.835 | 3.794 | -0.212 | 2.635%
1 | 7.716 | 3.737 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.999 | -2.919 | 0.999 | -2.919 | 0.97 | -2.399 | 0.97 | -2.399 | -3.469 | 10.526 | 7.494 | 3.629 | -0.222 | 2.877%
2 | 7.517 | 3.641 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -2.841 | 1 | -2.841 | 0.97 | -2.294 | 0.97 | -2.294 | -3.644 | 10.526 | 7.29 | 3.531 | -0.227 | 3.02%
3 | 7.407 | 3.587 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.797 | 1.001 | -2.797 | 0.97 | -2.236 | 0.97 | -2.236 | -3.74 | 10.526 | 7.177 | 3.476 | -0.23 | 3.105%
4 | 7.398 | 3.583 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.794 | 1.001 | -2.794 | 0.97 | -2.231 | 0.97 | -2.231 | -3.748 | 10.526 | 7.168 | 3.472 | -0.23 | 3.109%
5 | 7.563 | 3.663 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -2.859 | 1 | -2.859 | 0.97 | -2.318 | 0.97 | -2.318 | -3.603 | 10.526 | 7.337 | 3.553 | -0.226 | 2.988%
6 | 7.986 | 3.868 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.997 | -3.027 | 0.997 | -3.027 | 0.97 | -2.542 | 0.97 | -2.542 | -3.23 | 10.526 | 7.772 | 3.764 | -0.214 | 2.68%
7 | 8.626 | 4.178 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.992 | -3.283 | 0.992 | -3.283 | 0.97 | -2.884 | 0.97 | -2.884 | -2.657 | 10.526 | 8.435 | 4.085 | -0.191 | 2.214%
8 | 9.059 | 4.387 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.989 | -3.458 | 0.989 | -3.458 | 0.97 | -3.118 | 0.97 | -3.118 | -2.263 | 10.526 | 8.888 | 4.305 | -0.171 | 1.888%
9 | 9.181 | 4.447 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.988 | -3.508 | 0.988 | -3.508 | 0.97 | -3.185 | 0.97 | -3.185 | -2.151 | 10.526 | 9.016 | 4.367 | -0.165 | 1.797%
10 | 9.23 | 4.47 | 0.9 | I | cloudy | 10.526 | 10.515 | 5 | 0.987 | -3.528 | 0.987 | -3.528 | 0.97 | -3.211 | 0.97 | -3.211 | -2.106 | 10.515 | 9.068 | 4.392 | -0.162 | 1.755%
11 | 9.261 | 4.485 | 0.9 | I | cloudy | 10.526 | 10.484 | 5 | 0.987 | -3.54 | 0.987 | -3.54 | 0.97 | -3.228 | 0.97 | -3.228 | -2.078 | 10.484 | 9.1 | 4.407 | -0.161 | 1.738%
12 | 9.292 | 4.5 | 0.9 | I | cloudy | 10.526 | 10.452 | 5 | 0.987 | -3.553 | 0.987 | -3.553 | 0.97 | -3.245 | 0.97 | -3.245 | -2.049 | 10.452 | 9.133 | 4.423 | -0.159 | 1.711%
13 | 9.322 | 4.515 | 0.9 | I | cloudy | 10.526 | 10.452 | 5 | 0.987 | -3.565 | 0.987 | -3.565 | 0.97 | -3.261 | 0.97 | -3.261 | -2.022 | 10.452 | 9.164 | 4.439 | -0.158 | 1.695%
14 | 9.338 | 4.523 | 0.9 | I | cloudy | 10.526 | 10.473 | 5 | 0.987 | -3.572 | 0.987 | -3.572 | 0.97 | -3.27 | 0.97 | -3.27 | -2.007 | 10.473 | 9.181 | 4.447 | -0.157 | 1.681%
15 | 9.404 | 4.555 | 0.9 | I | cloudy | 10.526 | 10.505 | 5 | 0.986 | -3.599 | 0.986 | -3.599 | 0.97 | -3.306 | 0.97 | -3.306 | -1.946 | 10.505 | 9.251 | 4.48 | -0.153 | 1.627%
16 | 9.594 | 4.647 | 0.9 | I | cloudy | 10.526 | 10.515 | 5 | 0.985 | -3.676 | 0.985 | -3.676 | 0.97 | -3.41 | 0.97 | -3.41 | -1.77 | 10.515 | 9.452 | 4.578 | -0.142 | 1.48%
17 | 9.883 | 4.787 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.982 | -3.795 | 0.982 | -3.795 | 0.97 | -3.57 | 0.97 | -3.57 | -1.5 | 10.526 | 9.759 | 4.726 | -0.124 | 1.255%
18 | 10 | 4.843 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.981 | -3.843 | 0.981 | -3.843 | 0.97 | -3.634 | 0.97 | -3.634 | -1.39 | 10.526 | 9.883 | 4.787 | -0.117 | 1.17%
19 | 9.966 | 4.827 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.982 | -3.829 | 0.982 | -3.829 | 0.97 | -3.616 | 0.97 | -3.616 | -1.422 | 10.526 | 9.847 | 4.769 | -0.119 | 1.194%
20 | 9.857 | 4.774 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.983 | -3.784 | 0.983 | -3.784 | 0.97 | -3.555 | 0.97 | -3.555 | -1.524 | 10.526 | 9.731 | 4.713 | -0.126 | 1.278%
21 | 9.62 | 4.659 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.984 | -3.687 | 0.984 | -3.687 | 0.97 | -3.425 | 0.97 | -3.425 | -1.745 | 10.526 | 9.479 | 4.591 | -0.141 | 1.466%
22 | 9.139 | 4.426 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.988 | -3.491 | 0.988 | -3.491 | 0.97 | -3.162 | 0.97 | -3.162 | -2.19 | 10.526 | 8.972 | 4.345 | -0.167 | 1.827%
23 | 8.547 | 4.14 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.993 | -3.251 | 0.993 | -3.251 | 0.97 | -2.842 | 0.97 | -2.842 | -2.728 | 10.526 | 8.353 | 4.045 | -0.194 | 2.27%
24 | 8.047 | 3.897 | 0.9 | I | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.051 | 0.996 | -3.051 | 0.97 | -2.574 | 0.97 | -2.574 | -3.176 | 10.526 | 7.835 | 3.794 | -0.212 | 2.635%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.924 | 0.996 | -2.943 | -5.263 | 5.263 | 7.614 | 2.503 | -0.102 | 1.322%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.897 | 0.997 | -2.861 | -5.263 | 5.263 | 7.418 | 2.438 | -0.099 | 1.317%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.882 | 0.997 | -2.816 | -5.263 | 5.263 | 7.309 | 2.402 | -0.098 | 1.323%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.881 | 0.997 | -2.812 | -5.263 | 5.263 | 7.3 | 2.4 | -0.098 | 1.325%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.903 | 0.996 | -2.88 | -5.263 | 5.263 | 7.463 | 2.453 | -0.1 | 1.322%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.96 | 0.994 | -3.054 | -5.263 | 5.263 | 7.881 | 2.59 | -0.105 | 1.315%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 5.263 | 5.252 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.044 | 0.99 | -3.307 | -5.252 | 5.252 | 8.514 | 2.798 | -0.112 | 1.298%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 5.263 | 5.116 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.025 | -1.119 | 0.987 | -3.533 | -5.116 | 5.116 | 8.938 | 2.938 | -0.121 | 1.336%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 5.263 | 4.705 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.026 | -1.146 | 0.988 | -3.592 | -4.705 | 4.705 | 9.068 | 2.981 | -0.113 | 1.231%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 5.263 | 4.142 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.027 | -1.154 | 0.99 | -3.581 | -4.142 | 4.142 | 9.137 | 3.003 | -0.093 | 1.008%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 5.263 | 3.574 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.028 | -1.182 | 0.99 | -3.639 | -3.574 | 3.574 | 9.176 | 3.016 | -0.085 | 0.9178%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 5.263 | 3.258 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.029 | -1.193 | 0.991 | -3.654 | -3.258 | 3.258 | 9.215 | 3.029 | -0.077 | 0.8287%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 5.263 | 3.353 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.029 | -1.198 | 0.99 | -3.676 | -3.353 | 3.353 | 9.241 | 3.037 | -0.081 | 0.8689%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 5.263 | 3.505 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.028 | -1.197 | 0.99 | -3.68 | -3.505 | 3.505 | 9.253 | 3.041 | -0.085 | 0.9103%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 5.263 | 3.942 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.027 | -1.196 | 0.988 | -3.701 | -3.942 | 3.942 | 9.307 | 3.059 | -0.097 | 1.031%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 5.263 | 4.458 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.025 | -1.21 | 0.986 | -3.773 | -4.458 | 4.458 | 9.482 | 3.117 | -0.112 | 1.167%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 5.263 | 4.921 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.024 | -1.227 | 0.983 | -3.851 | -4.921 | 4.921 | 9.761 | 3.208 | -0.122 | 1.234%
18 | 10 | 3.287 | 0.95 | I | very sunny | 5.263 | 5.189 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.237 | 0.982 | -3.899 | -5.189 | 5.189 | 9.869 | 3.244 | -0.131 | 1.31%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 5.263 | 5.258 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.231 | 0.982 | -3.884 | -5.258 | 5.258 | 9.834 | 3.232 | -0.132 | 1.324%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.216 | 0.983 | -3.838 | -5.263 | 5.263 | 9.726 | 3.197 | -0.131 | 1.329%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.023 | -1.184 | 0.984 | -3.737 | -5.263 | 5.263 | 9.492 | 3.12 | -0.128 | 1.331%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.118 | 0.987 | -3.535 | -5.263 | 5.263 | 9.018 | 2.964 | -0.121 | 1.324%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.037 | 0.991 | -3.287 | -5.263 | 5.263 | 8.434 | 2.772 | -0.113 | 1.322%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.969 | 0.994 | -3.08 | -5.263 | 5.263 | 7.941 | 2.61 | -0.106 | 1.317%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.924 | 0.996 | -2.943 | -5.263 | 5.263 | 7.614 | 2.503 | -0.102 | 1.322%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.897 | 0.997 | -2.861 | -5.263 | 5.263 | 7.418 | 2.438 | -0.099 | 1.317%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.882 | 0.997 | -2.816 | -5.263 | 5.263 | 7.309 | 2.402 | -0.098 | 1.323%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.881 | 0.997 | -2.812 | -5.263 | 5.263 | 7.3 | 2.4 | -0.098 | 1.325%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.903 | 0.996 | -2.88 | -5.263 | 5.263 | 7.463 | 2.453 | -0.1 | 1.322%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.96 | 0.994 | -3.054 | -5.263 | 5.263 | 7.881 | 2.59 | -0.105 | 1.315%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.047 | 0.99 | -3.32 | -5.263 | 5.263 | 8.512 | 2.798 | -0.114 | 1.322%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 5.263 | 5.258 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.024 | -1.107 | 0.987 | -3.501 | -5.258 | 5.258 | 8.939 | 2.938 | -0.12 | 1.325%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 5.263 | 5.205 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.024 | -1.125 | 0.987 | -3.553 | -5.205 | 5.205 | 9.061 | 2.978 | -0.12 | 1.307%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 5.263 | 5.095 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.024 | -1.144 | 0.986 | -3.606 | -5.095 | 5.095 | 9.107 | 2.993 | -0.123 | 1.333%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 5.263 | 4.979 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.025 | -1.151 | 0.986 | -3.622 | -4.979 | 4.979 | 9.141 | 3.004 | -0.12 | 1.296%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 5.263 | 4.916 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.025 | -1.157 | 0.986 | -3.636 | -4.916 | 4.916 | 9.173 | 3.015 | -0.119 | 1.281%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 5.263 | 4.984 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.025 | -1.159 | 0.986 | -3.647 | -4.984 | 4.984 | 9.201 | 3.024 | -0.121 | 1.298%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 5.263 | 5.016 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.024 | -1.161 | 0.986 | -3.654 | -5.016 | 5.016 | 9.216 | 3.029 | -0.122 | 1.306%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 5.263 | 5.147 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.024 | -1.166 | 0.985 | -3.679 | -5.147 | 5.147 | 9.277 | 3.049 | -0.127 | 1.35%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 5.263 | 5.237 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.023 | -1.191 | 0.984 | -3.759 | -5.237 | 5.237 | 9.462 | 3.11 | -0.132 | 1.376%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.023 | -1.22 | 0.982 | -3.849 | -5.263 | 5.263 | 9.752 | 3.205 | -0.131 | 1.326%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.236 | 0.982 | -3.898 | -5.263 | 5.263 | 9.867 | 3.243 | -0.133 | 1.33%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.231 | 0.982 | -3.884 | -5.263 | 5.263 | 9.833 | 3.232 | -0.133 | 1.335%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.216 | 0.983 | -3.838 | -5.263 | 5.263 | 9.726 | 3.197 | -0.131 | 1.329%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.023 | -1.184 | 0.984 | -3.737 | -5.263 | 5.263 | 9.492 | 3.12 | -0.128 | 1.331%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.118 | 0.987 | -3.535 | -5.263 | 5.263 | 9.018 | 2.964 | -0.121 | 1.324%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.037 | 0.991 | -3.287 | -5.263 | 5.263 | 8.434 | 2.772 | -0.113 | 1.322%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.969 | 0.994 | -3.08 | -5.263 | 5.263 | 7.941 | 2.61 | -0.106 | 1.317%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.027 | -0.924 | 0.996 | -2.943 | -5.263 | 5.263 | 7.614 | 2.503 | -0.102 | 1.322%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.027 | -0.897 | 0.997 | -2.861 | -5.263 | 5.263 | 7.418 | 2.438 | -0.099 | 1.317%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.027 | -0.882 | 0.997 | -2.816 | -5.263 | 5.263 | 7.309 | 2.402 | -0.098 | 1.323%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.027 | -0.881 | 0.997 | -2.812 | -5.263 | 5.263 | 7.3 | 2.4 | -0.098 | 1.325%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.027 | -0.903 | 0.996 | -2.88 | -5.263 | 5.263 | 7.463 | 2.453 | -0.1 | 1.322%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.026 | -0.96 | 0.994 | -3.054 | -5.263 | 5.263 | 7.881 | 2.59 | -0.105 | 1.315%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.025 | -1.047 | 0.99 | -3.32 | -5.263 | 5.263 | 8.512 | 2.798 | -0.114 | 1.322%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.024 | -1.107 | 0.987 | -3.501 | -5.263 | 5.263 | 8.939 | 2.938 | -0.12 | 1.325%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.024 | -1.123 | 0.987 | -3.552 | -5.263 | 5.263 | 9.059 | 2.978 | -0.122 | 1.329%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 5.263 | 5.258 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.024 | -1.13 | 0.986 | -3.573 | -5.258 | 5.258 | 9.108 | 2.994 | -0.122 | 1.322%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 5.263 | 5.242 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.024 | -1.135 | 0.986 | -3.586 | -5.242 | 5.242 | 9.139 | 3.004 | -0.122 | 1.317%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 5.263 | 5.226 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.024 | -1.139 | 0.986 | -3.599 | -5.226 | 5.226 | 9.17 | 3.014 | -0.122 | 1.313%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 5.263 | 5.226 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.024 | -1.143 | 0.986 | -3.612 | -5.226 | 5.226 | 9.199 | 3.024 | -0.123 | 1.319%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 5.263 | 5.237 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.024 | -1.155 | 0.985 | -3.65 | -5.237 | 5.237 | 9.21 | 3.027 | -0.128 | 1.371%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 5.263 | 5.252 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.024 | -1.164 | 0.985 | -3.677 | -5.252 | 5.252 | 9.275 | 3.048 | -0.129 | 1.372%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 5.263 | 5.258 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.024 | -1.18 | 0.984 | -3.726 | -5.258 | 5.258 | 9.467 | 3.112 | -0.127 | 1.324%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.023 | -1.22 | 0.982 | -3.849 | -5.263 | 5.263 | 9.752 | 3.205 | -0.131 | 1.326%
18 | 10 | 3.287 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.023 | -1.236 | 0.982 | -3.898 | -5.263 | 5.263 | 9.867 | 3.243 | -0.133 | 1.33%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.023 | -1.231 | 0.982 | -3.884 | -5.263 | 5.263 | 9.833 | 3.232 | -0.133 | 1.335%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.023 | -1.216 | 0.983 | -3.838 | -5.263 | 5.263 | 9.726 | 3.197 | -0.131 | 1.329%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.023 | -1.184 | 0.984 | -3.737 | -5.263 | 5.263 | 9.492 | 3.12 | -0.128 | 1.331%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.024 | -1.118 | 0.987 | -3.535 | -5.263 | 5.263 | 9.018 | 2.964 | -0.121 | 1.324%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.025 | -1.037 | 0.991 | -3.287 | -5.263 | 5.263 | 8.434 | 2.772 | -0.113 | 1.322%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.102 | 1.007 | -3.201 | 1.026 | -0.969 | 0.994 | -3.08 | -5.263 | 5.263 | 7.941 | 2.61 | -0.106 | 1.317%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.799 | 0.981 | -2.855 | -10.526 | 10.526 | 7.505 | 2.467 | -0.211 | 2.735%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.772 | 0.982 | -2.772 | -10.526 | 10.526 | 7.312 | 2.403 | -0.205 | 2.727%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.757 | 0.983 | -2.727 | -10.526 | 10.526 | 7.205 | 2.368 | -0.202 | 2.727%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.756 | 0.983 | -2.723 | -10.526 | 10.526 | 7.196 | 2.365 | -0.202 | 2.73%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.778 | 0.982 | -2.791 | -10.526 | 10.526 | 7.356 | 2.418 | -0.207 | 2.737%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.835 | 0.98 | -2.968 | -10.526 | 10.526 | 7.767 | 2.553 | -0.219 | 2.742%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 10.526 | 10.505 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.923 | 0.976 | -3.238 | -10.505 | 10.505 | 8.389 | 2.757 | -0.237 | 2.748%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 10.526 | 10.231 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.011 | -0.989 | 0.974 | -3.424 | -10.231 | 10.231 | 8.817 | 2.898 | -0.242 | 2.671%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 10.526 | 9.41 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.018 | -1.073 | 0.98 | -3.535 | -7.644 | 9.41 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 10.526 | 8.284 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.018 | -1.08 | 0.98 | -3.556 | -7.644 | 8.284 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 10.526 | 7.147 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.019 | -1.095 | 0.981 | -3.573 | -7.147 | 7.147 | 9.089 | 2.987 | -0.172 | 1.857%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 10.526 | 6.516 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.021 | -1.112 | 0.982 | -3.59 | -6.516 | 6.516 | 9.136 | 3.003 | -0.156 | 1.679%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 10.526 | 6.705 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.02 | -1.117 | 0.982 | -3.617 | -6.705 | 6.705 | 9.158 | 3.01 | -0.164 | 1.759%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 10.526 | 7.01 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.019 | -1.112 | 0.981 | -3.618 | -7.01 | 7.01 | 9.166 | 3.013 | -0.172 | 1.842%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 10.526 | 7.884 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.104 | 0.979 | -3.63 | -7.642 | 7.884 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 10.526 | 8.916 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.13 | 0.977 | -3.711 | -7.64 | 8.916 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 10.526 | 9.842 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.17 | 0.976 | -3.835 | -7.637 | 9.842 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | very sunny | 10.526 | 10.379 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.187 | 0.975 | -3.885 | -7.636 | 10.379 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 10.526 | 10.515 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.182 | 0.975 | -3.871 | -7.636 | 10.515 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.167 | 0.976 | -3.824 | -7.637 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.134 | 0.977 | -3.722 | -7.64 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.993 | 0.973 | -3.455 | -10.526 | 10.526 | 8.887 | 2.921 | -0.252 | 2.757%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.912 | 0.976 | -3.204 | -10.526 | 10.526 | 8.312 | 2.732 | -0.235 | 2.75%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.2 | 1.012 | -0.844 | 0.979 | -2.994 | -10.526 | 10.526 | 7.826 | 2.572 | -0.221 | 2.746%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.799 | 0.981 | -2.855 | -10.526 | 10.526 | 7.505 | 2.467 | -0.211 | 2.735%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.772 | 0.982 | -2.772 | -10.526 | 10.526 | 7.312 | 2.403 | -0.205 | 2.727%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.757 | 0.983 | -2.727 | -10.526 | 10.526 | 7.205 | 2.368 | -0.202 | 2.727%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.756 | 0.983 | -2.723 | -10.526 | 10.526 | 7.196 | 2.365 | -0.202 | 2.73%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.778 | 0.982 | -2.791 | -10.526 | 10.526 | 7.356 | 2.418 | -0.207 | 2.737%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.835 | 0.98 | -2.968 | -10.526 | 10.526 | 7.767 | 2.553 | -0.219 | 2.742%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.923 | 0.976 | -3.238 | -10.526 | 10.526 | 8.389 | 2.757 | -0.237 | 2.748%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 10.526 | 10.515 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.01 | -0.982 | 0.973 | -3.421 | -10.515 | 10.515 | 8.809 | 2.895 | -0.25 | 2.76%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 10.526 | 10.41 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.018 | -1.073 | 0.98 | -3.535 | -7.644 | 10.41 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 10.526 | 10.189 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.018 | -1.08 | 0.98 | -3.556 | -7.644 | 10.189 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 10.526 | 9.958 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.018 | -1.084 | 0.979 | -3.569 | -7.643 | 9.958 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 10.526 | 9.831 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.018 | -1.089 | 0.979 | -3.582 | -7.643 | 9.831 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 10.526 | 9.968 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.018 | -1.093 | 0.979 | -3.595 | -7.643 | 9.968 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 10.526 | 10.031 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.018 | -1.095 | 0.979 | -3.602 | -7.643 | 10.031 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 10.526 | 10.294 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.104 | 0.979 | -3.63 | -7.642 | 10.294 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 10.526 | 10.473 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.13 | 0.977 | -3.711 | -7.64 | 10.473 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.17 | 0.976 | -3.835 | -7.637 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.187 | 0.975 | -3.885 | -7.636 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.182 | 0.975 | -3.871 | -7.636 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.167 | 0.976 | -3.824 | -7.637 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.134 | 0.977 | -3.722 | -7.64 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.993 | 0.973 | -3.455 | -10.526 | 10.526 | 8.887 | 2.921 | -0.252 | 2.757%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.912 | 0.976 | -3.204 | -10.526 | 10.526 | 8.312 | 2.732 | -0.235 | 2.75%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.2 | 1.012 | -0.844 | 0.979 | -2.994 | -10.526 | 10.526 | 7.826 | 2.572 | -0.221 | 2.746%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.056 | 1.009 | -3.064 | 1.013 | -0.799 | 0.981 | -2.855 | -10.526 | 10.526 | 7.505 | 2.467 | -0.211 | 2.735%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.029 | 1.01 | -2.982 | 1.013 | -0.772 | 0.982 | -2.772 | -10.526 | 10.526 | 7.312 | 2.403 | -0.205 | 2.727%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.014 | 1.011 | -2.937 | 1.013 | -0.757 | 0.983 | -2.727 | -10.526 | 10.526 | 7.205 | 2.368 | -0.202 | 2.727%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.013 | 1.011 | -2.933 | 1.013 | -0.756 | 0.983 | -2.723 | -10.526 | 10.526 | 7.196 | 2.365 | -0.202 | 2.73%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.035 | 1.01 | -3.001 | 1.013 | -0.778 | 0.982 | -2.791 | -10.526 | 10.526 | 7.356 | 2.418 | -0.207 | 2.737%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.093 | 1.007 | -3.175 | 1.012 | -0.835 | 0.98 | -2.968 | -10.526 | 10.526 | 7.767 | 2.553 | -0.219 | 2.742%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.039 | -1.181 | 1.003 | -3.441 | 1.011 | -0.923 | 0.976 | -3.238 | -10.526 | 10.526 | 8.389 | 2.757 | -0.237 | 2.748%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.001 | -3.622 | 1.01 | -0.982 | 0.973 | -3.421 | -10.526 | 10.526 | 8.809 | 2.895 | -0.25 | 2.76%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.258 | 1 | -3.673 | 1.018 | -1.073 | 0.98 | -3.535 | -7.644 | 10.526 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 10.526 | 10.515 | 3 | 1.038 | -1.265 | 1 | -3.694 | 1.018 | -1.08 | 0.98 | -3.556 | -7.644 | 10.515 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 10.526 | 10.484 | 3 | 1.038 | -1.269 | 0.999 | -3.707 | 1.018 | -1.084 | 0.979 | -3.569 | -7.643 | 10.484 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 10.526 | 10.452 | 3 | 1.038 | -1.273 | 0.999 | -3.72 | 1.018 | -1.089 | 0.979 | -3.582 | -7.643 | 10.452 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 10.526 | 10.452 | 3 | 1.038 | -1.277 | 0.999 | -3.733 | 1.018 | -1.093 | 0.979 | -3.595 | -7.643 | 10.452 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 10.526 | 10.473 | 3 | 1.038 | -1.28 | 0.999 | -3.739 | 1.018 | -1.095 | 0.979 | -3.602 | -7.643 | 10.473 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 10.526 | 10.505 | 3 | 1.037 | -1.289 | 0.999 | -3.767 | 1.017 | -1.104 | 0.979 | -3.63 | -7.642 | 10.505 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 10.526 | 10.515 | 3 | 1.037 | -1.315 | 0.997 | -3.847 | 1.017 | -1.13 | 0.977 | -3.711 | -7.64 | 10.515 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.355 | 0.996 | -3.97 | 1.017 | -1.17 | 0.976 | -3.835 | -7.637 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.372 | 0.995 | -4.02 | 1.016 | -1.187 | 0.975 | -3.885 | -7.636 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.036 | -1.367 | 0.995 | -4.005 | 1.016 | -1.182 | 0.975 | -3.871 | -7.636 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.352 | 0.996 | -3.959 | 1.017 | -1.167 | 0.976 | -3.824 | -7.637 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.319 | 0.997 | -3.858 | 1.017 | -1.134 | 0.977 | -3.722 | -7.64 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.252 | 1 | -3.656 | 1.01 | -0.993 | 0.973 | -3.455 | -10.526 | 10.526 | 8.887 | 2.921 | -0.252 | 2.757%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.039 | -1.17 | 1.004 | -3.408 | 1.011 | -0.912 | 0.976 | -3.204 | -10.526 | 10.526 | 8.312 | 2.732 | -0.235 | 2.75%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.102 | 1.007 | -3.2 | 1.012 | -0.844 | 0.979 | -2.994 | -10.526 | 10.526 | 7.826 | 2.572 | -0.221 | 2.746%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.996 | -1.592 | 0.981 | -2.637 | -5.263 | 5.263 | 7.5 | 2.465 | -0.216 | 2.799%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.997 | -1.538 | 0.982 | -2.555 | -5.263 | 5.263 | 7.307 | 2.402 | -0.21 | 2.794%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.997 | -1.509 | 0.982 | -2.51 | -5.263 | 5.263 | 7.2 | 2.366 | -0.207 | 2.795%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.997 | -1.507 | 0.982 | -2.506 | -5.263 | 5.263 | 7.191 | 2.364 | -0.207 | 2.798%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.551 | 0.981 | -2.574 | -5.263 | 5.263 | 7.351 | 2.416 | -0.212 | 2.803%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.995 | -1.664 | 0.979 | -2.749 | -5.263 | 5.263 | 7.762 | 2.551 | -0.224 | 2.805%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 5.263 | 5.252 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.993 | -1.837 | 0.975 | -3.016 | -5.252 | 5.252 | 8.383 | 2.755 | -0.243 | 2.817%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 5.263 | 5.116 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.992 | -1.964 | 0.973 | -3.206 | -5.116 | 5.116 | 8.81 | 2.896 | -0.249 | 2.749%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 5.263 | 4.705 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 4.705 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 5.263 | 4.142 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 4.142 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 5.263 | 3.574 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.999 | -2.158 | 0.98 | -3.422 | -3.574 | 3.574 | 9.084 | 2.986 | -0.177 | 1.911%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 5.263 | 3.258 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 1.001 | -2.19 | 0.982 | -3.453 | -3.258 | 3.258 | 9.131 | 3.001 | -0.161 | 1.733%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 5.263 | 3.353 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 1 | -2.199 | 0.981 | -3.472 | -3.353 | 3.353 | 9.154 | 3.009 | -0.168 | 1.802%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 5.263 | 3.505 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.999 | -2.19 | 0.98 | -3.467 | -3.505 | 3.505 | 9.162 | 3.011 | -0.176 | 1.885%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 5.263 | 3.942 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 3.942 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 5.263 | 4.458 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 4.458 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 5.263 | 4.921 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 4.921 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | very sunny | 5.263 | 5.189 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 5.189 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 5.263 | 5.258 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 5.258 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 5.263 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 5.263 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.99 | -1.975 | 0.972 | -3.231 | -5.263 | 5.263 | 8.88 | 2.919 | -0.259 | 2.834%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.993 | -1.815 | 0.975 | -2.983 | -5.263 | 5.263 | 8.306 | 2.73 | -0.241 | 2.82%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.995 | -1.68 | 0.979 | -2.774 | -5.263 | 5.263 | 7.821 | 2.571 | -0.226 | 2.808%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.996 | -1.592 | 0.981 | -2.637 | -5.263 | 5.263 | 7.5 | 2.465 | -0.216 | 2.799%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.997 | -1.538 | 0.982 | -2.555 | -5.263 | 5.263 | 7.307 | 2.402 | -0.21 | 2.794%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.997 | -1.509 | 0.982 | -2.51 | -5.263 | 5.263 | 7.2 | 2.366 | -0.207 | 2.795%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.997 | -1.507 | 0.982 | -2.506 | -5.263 | 5.263 | 7.191 | 2.364 | -0.207 | 2.798%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.551 | 0.981 | -2.574 | -5.263 | 5.263 | 7.351 | 2.416 | -0.212 | 2.803%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.995 | -1.664 | 0.979 | -2.749 | -5.263 | 5.263 | 7.762 | 2.551 | -0.224 | 2.805%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.992 | -1.836 | 0.975 | -3.016 | -5.263 | 5.263 | 8.382 | 2.755 | -0.244 | 2.829%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 5.263 | 5.258 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.991 | -1.954 | 0.972 | -3.198 | -5.258 | 5.258 | 8.802 | 2.893 | -0.257 | 2.837%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 5.263 | 5.205 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 5.205 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 5.263 | 5.095 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 5.095 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 5.263 | 4.979 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 4.979 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 5.263 | 4.916 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 4.916 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 5.263 | 4.984 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 4.984 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 5.263 | 5.016 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 5.016 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 5.263 | 5.147 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 5.147 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 5.263 | 5.237 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 5.237 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 5.263 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 5.263 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 5.263 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 5.263 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 5.263 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.99 | -1.975 | 0.972 | -3.231 | -5.263 | 5.263 | 8.88 | 2.919 | -0.259 | 2.834%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.993 | -1.815 | 0.975 | -2.983 | -5.263 | 5.263 | 8.306 | 2.73 | -0.241 | 2.82%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.995 | -1.68 | 0.979 | -2.774 | -5.263 | 5.263 | 7.821 | 2.571 | -0.226 | 2.808%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.996 | -1.592 | 0.981 | -2.637 | -5.263 | 5.263 | 7.5 | 2.465 | -0.216 | 2.799%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.997 | -1.538 | 0.982 | -2.555 | -5.263 | 5.263 | 7.307 | 2.402 | -0.21 | 2.794%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.997 | -1.509 | 0.982 | -2.51 | -5.263 | 5.263 | 7.2 | 2.366 | -0.207 | 2.795%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.997 | -1.507 | 0.982 | -2.506 | -5.263 | 5.263 | 7.191 | 2.364 | -0.207 | 2.798%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.997 | -1.551 | 0.981 | -2.574 | -5.263 | 5.263 | 7.351 | 2.416 | -0.212 | 2.803%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.995 | -1.664 | 0.979 | -2.749 | -5.263 | 5.263 | 7.762 | 2.551 | -0.224 | 2.805%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.992 | -1.836 | 0.975 | -3.016 | -5.263 | 5.263 | 8.382 | 2.755 | -0.244 | 2.829%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.991 | -1.953 | 0.972 | -3.198 | -5.263 | 5.263 | 8.802 | 2.893 | -0.257 | 2.837%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 5.263 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 5.263 | 5.258 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 5.258 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 5.263 | 5.242 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 5.242 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 5.263 | 5.226 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 5.226 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 5.263 | 5.226 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 5.226 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 5.263 | 5.237 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 5.237 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 5.263 | 5.252 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 5.252 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 5.263 | 5.258 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 5.258 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 5.263 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 5.263 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 5.263 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 5.263 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 5.263 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.99 | -1.975 | 0.972 | -3.231 | -5.263 | 5.263 | 8.88 | 2.919 | -0.259 | 2.834%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.993 | -1.815 | 0.975 | -2.983 | -5.263 | 5.263 | 8.306 | 2.73 | -0.241 | 2.82%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.995 | -1.68 | 0.979 | -2.774 | -5.263 | 5.263 | 7.821 | 2.571 | -0.226 | 2.808%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.569 | 0.979 | -2.619 | -5.555 | 10.526 | 7.487 | 2.461 | -0.229 | 2.968%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.358 | 0.97 | -2.388 | -7.333 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.328 | 0.971 | -2.343 | -7.335 | 10.526 | 7.114 | 2.338 | -0.293 | 3.956%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.326 | 0.971 | -2.339 | -7.335 | 10.526 | 7.105 | 2.335 | -0.293 | 3.961%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.995 | -1.528 | 0.98 | -2.555 | -5.557 | 10.526 | 7.338 | 2.412 | -0.225 | 2.975%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.642 | 0.977 | -2.731 | -5.551 | 10.526 | 7.748 | 2.547 | -0.238 | 2.98%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 10.526 | 10.505 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.815 | 0.973 | -2.999 | -5.542 | 10.505 | 8.368 | 2.75 | -0.258 | 2.991%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 10.526 | 10.231 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.933 | 0.971 | -3.181 | -5.535 | 10.231 | 8.787 | 2.888 | -0.272 | 3.003%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 10.526 | 9.41 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 9.41 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 10.526 | 8.284 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 8.284 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 10.526 | 7.147 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 7.147 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 10.526 | 6.516 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 6.516 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 10.526 | 6.705 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 6.705 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 10.526 | 7.01 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 7.01 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 10.526 | 7.884 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 7.884 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 10.526 | 8.916 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 8.916 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 10.526 | 9.842 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 9.842 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | very sunny | 10.526 | 10.379 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 10.379 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 10.526 | 10.515 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 10.515 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.955 | 0.97 | -3.215 | -5.534 | 10.526 | 8.865 | 2.914 | -0.274 | 2.998%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.794 | 0.974 | -2.966 | -5.543 | 10.526 | 8.292 | 2.725 | -0.255 | 2.984%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.658 | 0.977 | -2.756 | -5.55 | 10.526 | 7.807 | 2.566 | -0.24 | 2.982%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.569 | 0.979 | -2.619 | -5.555 | 10.526 | 7.487 | 2.461 | -0.229 | 2.968%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.358 | 0.97 | -2.388 | -7.333 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.328 | 0.971 | -2.343 | -7.335 | 10.526 | 7.114 | 2.338 | -0.293 | 3.956%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.326 | 0.971 | -2.339 | -7.335 | 10.526 | 7.105 | 2.335 | -0.293 | 3.961%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.995 | -1.528 | 0.98 | -2.555 | -5.557 | 10.526 | 7.338 | 2.412 | -0.225 | 2.975%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.642 | 0.977 | -2.731 | -5.551 | 10.526 | 7.748 | 2.547 | -0.238 | 2.98%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.815 | 0.973 | -2.999 | -5.542 | 10.526 | 8.368 | 2.75 | -0.258 | 2.991%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 10.526 | 10.515 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.933 | 0.971 | -3.181 | -5.535 | 10.515 | 8.787 | 2.888 | -0.272 | 3.003%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 10.526 | 10.41 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 10.41 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 10.526 | 10.189 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 10.189 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 10.526 | 9.958 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 9.958 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 10.526 | 9.831 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 9.831 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 10.526 | 9.968 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 9.968 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 10.526 | 10.031 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 10.031 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 10.526 | 10.294 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 10.294 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 10.526 | 10.473 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 10.473 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.955 | 0.97 | -3.215 | -5.534 | 10.526 | 8.865 | 2.914 | -0.274 | 2.998%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.794 | 0.974 | -2.966 | -5.543 | 10.526 | 8.292 | 2.725 | -0.255 | 2.984%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.658 | 0.977 | -2.756 | -5.55 | 10.526 | 7.807 | 2.566 | -0.24 | 2.982%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.024 | -2.045 | 1.009 | -3.064 | 0.994 | -1.569 | 0.979 | -2.619 | -5.555 | 10.526 | 7.487 | 2.461 | -0.229 | 2.968%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -1.991 | 1.01 | -2.982 | 0.985 | -1.358 | 0.97 | -2.388 | -7.333 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.026 | -1.962 | 1.011 | -2.937 | 0.986 | -1.328 | 0.971 | -2.343 | -7.335 | 10.526 | 7.114 | 2.338 | -0.293 | 3.956%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.026 | -1.959 | 1.011 | -2.933 | 0.986 | -1.326 | 0.971 | -2.339 | -7.335 | 10.526 | 7.105 | 2.335 | -0.293 | 3.961%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.004 | 1.01 | -3.001 | 0.995 | -1.528 | 0.98 | -2.555 | -5.557 | 10.526 | 7.338 | 2.412 | -0.225 | 2.975%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.118 | 1.007 | -3.175 | 0.993 | -1.642 | 0.977 | -2.731 | -5.551 | 10.526 | 7.748 | 2.547 | -0.238 | 2.98%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.021 | -2.292 | 1.003 | -3.441 | 0.991 | -1.815 | 0.973 | -2.999 | -5.542 | 10.526 | 8.368 | 2.75 | -0.258 | 2.991%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.41 | 1.001 | -3.622 | 0.989 | -1.933 | 0.971 | -3.181 | -5.535 | 10.526 | 8.787 | 2.888 | -0.272 | 3.003%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.444 | 1 | -3.673 | 0.999 | -2.125 | 0.98 | -3.379 | -3.728 | 10.526 | 8.997 | 2.957 | -0.184 | 2.004%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 10.526 | 10.515 | 4 | 1.018 | -2.457 | 1 | -3.694 | 0.998 | -2.138 | 0.98 | -3.4 | -3.728 | 10.515 | 9.045 | 2.973 | -0.185 | 2.004%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 10.526 | 10.484 | 4 | 1.018 | -2.466 | 0.999 | -3.707 | 0.998 | -2.147 | 0.979 | -3.413 | -3.728 | 10.484 | 9.076 | 2.983 | -0.185 | 1.998%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 10.526 | 10.452 | 4 | 1.018 | -2.474 | 0.999 | -3.72 | 0.998 | -2.155 | 0.979 | -3.426 | -3.727 | 10.452 | 9.106 | 2.993 | -0.186 | 2.002%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 10.526 | 10.452 | 4 | 1.018 | -2.482 | 0.999 | -3.733 | 0.998 | -2.164 | 0.979 | -3.439 | -3.727 | 10.452 | 9.135 | 3.003 | -0.187 | 2.006%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 10.526 | 10.473 | 4 | 1.018 | -2.487 | 0.999 | -3.739 | 0.998 | -2.168 | 0.979 | -3.446 | -3.727 | 10.473 | 9.151 | 3.008 | -0.187 | 2.003%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 10.526 | 10.505 | 4 | 1.018 | -2.505 | 0.999 | -3.767 | 0.998 | -2.186 | 0.979 | -3.473 | -3.726 | 10.505 | 9.216 | 3.029 | -0.188 | 1.999%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 10.526 | 10.515 | 4 | 1.017 | -2.557 | 0.997 | -3.847 | 0.997 | -2.238 | 0.977 | -3.554 | -3.724 | 10.515 | 9.402 | 3.09 | -0.192 | 2.001%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.637 | 0.996 | -3.97 | 0.996 | -2.318 | 0.976 | -3.677 | -3.721 | 10.526 | 9.684 | 3.183 | -0.199 | 2.014%
18 | 10 | 3.287 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.015 | -2.669 | 0.995 | -4.02 | 0.995 | -2.35 | 0.975 | -3.727 | -3.72 | 10.526 | 9.799 | 3.221 | -0.201 | 2.01%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.66 | 0.995 | -4.005 | 0.996 | -2.34 | 0.975 | -3.713 | -3.72 | 10.526 | 9.766 | 3.21 | -0.2 | 2.007%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.63 | 0.996 | -3.959 | 0.996 | -2.31 | 0.976 | -3.666 | -3.721 | 10.526 | 9.659 | 3.175 | -0.198 | 2.009%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.017 | -2.564 | 0.997 | -3.858 | 0.997 | -2.245 | 0.977 | -3.565 | -3.724 | 10.526 | 9.427 | 3.099 | -0.193 | 2.006%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.019 | -2.432 | 1 | -3.656 | 0.989 | -1.955 | 0.97 | -3.215 | -5.534 | 10.526 | 8.865 | 2.914 | -0.274 | 2.998%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.021 | -2.271 | 1.004 | -3.408 | 0.991 | -1.794 | 0.974 | -2.966 | -5.543 | 10.526 | 8.292 | 2.725 | -0.255 | 2.984%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.135 | 1.007 | -3.201 | 0.993 | -1.658 | 0.977 | -2.756 | -5.55 | 10.526 | 7.807 | 2.566 | -0.24 | 2.982%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 5.263 | 7.419 | 2.438 | -0.297 | 3.849%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 5.263 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 5.263 | 7.109 | 2.337 | -0.298 | 4.023%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 5.263 | 7.1 | 2.334 | -0.298 | 4.028%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 5.263 | 7.265 | 2.388 | -0.298 | 3.94%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 5.263 | 7.691 | 2.528 | -0.295 | 3.694%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 5.263 | 5.252 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 5.252 | 8.339 | 2.741 | -0.287 | 3.327%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 5.263 | 5.116 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 5.116 | 8.781 | 2.886 | -0.278 | 3.069%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 5.263 | 4.705 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 4.705 | 8.906 | 2.927 | -0.275 | 2.995%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 5.263 | 4.142 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 4.142 | 8.956 | 2.944 | -0.274 | 2.969%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 5.263 | 3.574 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.574 | 3.574 | 8.988 | 2.954 | -0.273 | 2.948%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 5.263 | 3.258 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.973 | -3.222 | 0.973 | -3.222 | -3.258 | 3.258 | 9.044 | 2.973 | -0.248 | 2.669%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 5.263 | 3.353 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.972 | -3.224 | 0.972 | -3.224 | -3.353 | 3.353 | 9.065 | 2.98 | -0.257 | 2.757%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 5.263 | 3.505 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.505 | 3.505 | 9.067 | 2.98 | -0.271 | 2.902%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 5.263 | 3.942 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 3.942 | 9.135 | 3.002 | -0.269 | 2.86%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 5.263 | 4.458 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 4.458 | 9.33 | 3.067 | -0.264 | 2.752%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 5.263 | 4.921 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 4.921 | 9.629 | 3.165 | -0.254 | 2.57%
18 | 10 | 3.287 | 0.95 | I | very sunny | 5.263 | 5.189 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 5.189 | 9.75 | 3.205 | -0.25 | 2.5%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 5.263 | 5.258 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 5.258 | 9.714 | 3.193 | -0.252 | 2.529%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 5.263 | 9.602 | 3.156 | -0.255 | 2.587%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 5.263 | 9.357 | 3.075 | -0.263 | 2.734%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 5.263 | 8.863 | 2.913 | -0.276 | 3.02%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 5.263 | 8.259 | 2.715 | -0.288 | 3.37%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 5.263 | 7.752 | 2.548 | -0.295 | 3.666%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 5.263 | 7.419 | 2.438 | -0.297 | 3.849%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 5.263 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 5.263 | 7.109 | 2.337 | -0.298 | 4.023%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 5.263 | 7.1 | 2.334 | -0.298 | 4.028%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 5.263 | 7.265 | 2.388 | -0.298 | 3.94%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 5.263 | 7.691 | 2.528 | -0.295 | 3.694%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 5.263 | 8.339 | 2.741 | -0.287 | 3.327%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 5.263 | 5.258 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 5.258 | 8.781 | 2.886 | -0.278 | 3.069%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 5.263 | 5.205 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 5.205 | 8.906 | 2.927 | -0.275 | 2.995%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 5.263 | 5.095 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 5.095 | 8.956 | 2.944 | -0.274 | 2.969%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 5.263 | 4.979 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 4.979 | 8.988 | 2.954 | -0.273 | 2.948%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 5.263 | 4.916 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 4.916 | 9.02 | 2.965 | -0.272 | 2.927%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 5.263 | 4.984 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 4.984 | 9.05 | 2.975 | -0.272 | 2.918%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 5.263 | 5.016 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 5.016 | 9.067 | 2.98 | -0.271 | 2.902%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 5.263 | 5.147 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 5.147 | 9.135 | 3.002 | -0.269 | 2.86%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 5.263 | 5.237 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 5.237 | 9.33 | 3.067 | -0.264 | 2.752%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 5.263 | 9.629 | 3.165 | -0.254 | 2.57%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 5.263 | 9.75 | 3.205 | -0.25 | 2.5%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 5.263 | 9.714 | 3.193 | -0.252 | 2.529%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 5.263 | 9.602 | 3.156 | -0.255 | 2.587%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 5.263 | 9.357 | 3.075 | -0.263 | 2.734%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 5.263 | 8.863 | 2.913 | -0.276 | 3.02%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 5.263 | 8.259 | 2.715 | -0.288 | 3.37%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 5.263 | 7.752 | 2.548 | -0.295 | 3.666%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 5.263 | 7.419 | 2.438 | -0.297 | 3.849%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 5.263 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 5.263 | 7.109 | 2.337 | -0.298 | 4.023%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 5.263 | 7.1 | 2.334 | -0.298 | 4.028%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 5.263 | 7.265 | 2.388 | -0.298 | 3.94%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 5.263 | 7.691 | 2.528 | -0.295 | 3.694%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 5.263 | 8.339 | 2.741 | -0.287 | 3.327%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 5.263 | 8.781 | 2.886 | -0.278 | 3.069%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 5.263 | 8.906 | 2.927 | -0.275 | 2.995%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 5.263 | 5.258 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 5.258 | 8.956 | 2.944 | -0.274 | 2.969%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 5.263 | 5.242 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 5.242 | 8.988 | 2.954 | -0.273 | 2.948%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 5.263 | 5.226 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 5.226 | 9.02 | 2.965 | -0.272 | 2.927%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 5.263 | 5.226 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 5.226 | 9.05 | 2.975 | -0.272 | 2.918%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 5.263 | 5.237 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 5.237 | 9.067 | 2.98 | -0.271 | 2.902%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 5.263 | 5.252 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 5.252 | 9.135 | 3.002 | -0.269 | 2.86%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 5.263 | 5.258 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 5.258 | 9.33 | 3.067 | -0.264 | 2.752%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 5.263 | 9.629 | 3.165 | -0.254 | 2.57%
18 | 10 | 3.287 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 5.263 | 9.75 | 3.205 | -0.25 | 2.5%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 5.263 | 9.714 | 3.193 | -0.252 | 2.529%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 5.263 | 9.602 | 3.156 | -0.255 | 2.587%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 5.263 | 9.357 | 3.075 | -0.263 | 2.734%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 5.263 | 8.863 | 2.913 | -0.276 | 3.02%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 5.263 | 8.259 | 2.715 | -0.288 | 3.37%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 5.263 | 7.752 | 2.548 | -0.295 | 3.666%
1 | 7.716 | 2.536 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 10.526 | 7.419 | 2.438 | -0.297 | 3.849%
2 | 7.517 | 2.471 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 10.526 | 7.109 | 2.337 | -0.298 | 4.023%
4 | 7.398 | 2.432 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 10.526 | 7.1 | 2.334 | -0.298 | 4.028%
5 | 7.563 | 2.486 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 10.526 | 7.265 | 2.388 | -0.298 | 3.94%
6 | 7.986 | 2.625 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 10.526 | 7.691 | 2.528 | -0.295 | 3.694%
7 | 8.626 | 2.835 | 0.95 | I | very sunny | 10.526 | 10.505 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 10.505 | 8.339 | 2.741 | -0.287 | 3.327%
8 | 9.059 | 2.978 | 0.95 | I | very sunny | 10.526 | 10.231 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 10.231 | 8.781 | 2.886 | -0.278 | 3.069%
9 | 9.181 | 3.018 | 0.95 | I | very sunny | 10.526 | 9.41 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 9.41 | 8.906 | 2.927 | -0.275 | 2.995%
10 | 9.23 | 3.034 | 0.95 | I | very sunny | 10.526 | 8.284 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 8.284 | 8.956 | 2.944 | -0.274 | 2.969%
11 | 9.261 | 3.044 | 0.95 | I | very sunny | 10.526 | 7.147 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 7.147 | 8.988 | 2.954 | -0.273 | 2.948%
12 | 9.292 | 3.054 | 0.95 | I | very sunny | 10.526 | 6.516 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 6.516 | 9.02 | 2.965 | -0.272 | 2.927%
13 | 9.322 | 3.064 | 0.95 | I | very sunny | 10.526 | 6.705 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 6.705 | 9.05 | 2.975 | -0.272 | 2.918%
14 | 9.338 | 3.069 | 0.95 | I | very sunny | 10.526 | 7.01 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 7.01 | 9.067 | 2.98 | -0.271 | 2.902%
15 | 9.404 | 3.091 | 0.95 | I | very sunny | 10.526 | 7.884 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 7.884 | 9.135 | 3.002 | -0.269 | 2.86%
16 | 9.594 | 3.153 | 0.95 | I | very sunny | 10.526 | 8.916 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 8.916 | 9.33 | 3.067 | -0.264 | 2.752%
17 | 9.883 | 3.248 | 0.95 | I | very sunny | 10.526 | 9.842 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 9.842 | 9.629 | 3.165 | -0.254 | 2.57%
18 | 10 | 3.287 | 0.95 | I | very sunny | 10.526 | 10.379 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 10.379 | 9.75 | 3.205 | -0.25 | 2.5%
19 | 9.966 | 3.276 | 0.95 | I | very sunny | 10.526 | 10.515 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 10.515 | 9.714 | 3.193 | -0.252 | 2.529%
20 | 9.857 | 3.24 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 10.526 | 9.602 | 3.156 | -0.255 | 2.587%
21 | 9.62 | 3.162 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 10.526 | 9.357 | 3.075 | -0.263 | 2.734%
22 | 9.139 | 3.004 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 10.526 | 8.863 | 2.913 | -0.276 | 3.02%
23 | 8.547 | 2.809 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 10.526 | 8.259 | 2.715 | -0.288 | 3.37%
24 | 8.047 | 2.645 | 0.95 | I | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 10.526 | 7.752 | 2.548 | -0.295 | 3.666%
1 | 7.716 | 2.536 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 10.526 | 7.419 | 2.438 | -0.297 | 3.849%
2 | 7.517 | 2.471 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 10.526 | 7.109 | 2.337 | -0.298 | 4.023%
4 | 7.398 | 2.432 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 10.526 | 7.1 | 2.334 | -0.298 | 4.028%
5 | 7.563 | 2.486 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 10.526 | 7.265 | 2.388 | -0.298 | 3.94%
6 | 7.986 | 2.625 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 10.526 | 7.691 | 2.528 | -0.295 | 3.694%
7 | 8.626 | 2.835 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 10.526 | 8.339 | 2.741 | -0.287 | 3.327%
8 | 9.059 | 2.978 | 0.95 | I | moderate sun | 10.526 | 10.515 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 10.515 | 8.781 | 2.886 | -0.278 | 3.069%
9 | 9.181 | 3.018 | 0.95 | I | moderate sun | 10.526 | 10.41 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 10.41 | 8.906 | 2.927 | -0.275 | 2.995%
10 | 9.23 | 3.034 | 0.95 | I | moderate sun | 10.526 | 10.189 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 10.189 | 8.956 | 2.944 | -0.274 | 2.969%
11 | 9.261 | 3.044 | 0.95 | I | moderate sun | 10.526 | 9.958 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 9.958 | 8.988 | 2.954 | -0.273 | 2.948%
12 | 9.292 | 3.054 | 0.95 | I | moderate sun | 10.526 | 9.831 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 9.831 | 9.02 | 2.965 | -0.272 | 2.927%
13 | 9.322 | 3.064 | 0.95 | I | moderate sun | 10.526 | 9.968 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 9.968 | 9.05 | 2.975 | -0.272 | 2.918%
14 | 9.338 | 3.069 | 0.95 | I | moderate sun | 10.526 | 10.031 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 10.031 | 9.067 | 2.98 | -0.271 | 2.902%
15 | 9.404 | 3.091 | 0.95 | I | moderate sun | 10.526 | 10.294 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 10.294 | 9.135 | 3.002 | -0.269 | 2.86%
16 | 9.594 | 3.153 | 0.95 | I | moderate sun | 10.526 | 10.473 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 10.473 | 9.33 | 3.067 | -0.264 | 2.752%
17 | 9.883 | 3.248 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 10.526 | 9.629 | 3.165 | -0.254 | 2.57%
18 | 10 | 3.287 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 10.526 | 9.75 | 3.205 | -0.25 | 2.5%
19 | 9.966 | 3.276 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 10.526 | 9.714 | 3.193 | -0.252 | 2.529%
20 | 9.857 | 3.24 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 10.526 | 9.602 | 3.156 | -0.255 | 2.587%
21 | 9.62 | 3.162 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 10.526 | 9.357 | 3.075 | -0.263 | 2.734%
22 | 9.139 | 3.004 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 10.526 | 8.863 | 2.913 | -0.276 | 3.02%
23 | 8.547 | 2.809 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 10.526 | 8.259 | 2.715 | -0.288 | 3.37%
24 | 8.047 | 2.645 | 0.95 | I | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 10.526 | 7.752 | 2.548 | -0.295 | 3.666%
1 | 7.716 | 2.536 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.009 | -3.064 | 1.009 | -3.064 | 0.97 | -2.36 | 0.97 | -2.36 | -4.688 | 10.526 | 7.419 | 2.438 | -0.297 | 3.849%
2 | 7.517 | 2.471 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.257 | 0.97 | -2.257 | -4.828 | 10.526 | 7.219 | 2.373 | -0.298 | 3.964%
3 | 7.407 | 2.435 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.011 | -2.937 | 1.011 | -2.937 | 0.97 | -2.201 | 0.97 | -2.201 | -4.905 | 10.526 | 7.109 | 2.337 | -0.298 | 4.023%
4 | 7.398 | 2.432 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.011 | -2.933 | 1.011 | -2.933 | 0.97 | -2.196 | 0.97 | -2.196 | -4.911 | 10.526 | 7.1 | 2.334 | -0.298 | 4.028%
5 | 7.563 | 2.486 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.001 | 1.01 | -3.001 | 0.97 | -2.281 | 0.97 | -2.281 | -4.796 | 10.526 | 7.265 | 2.388 | -0.298 | 3.94%
6 | 7.986 | 2.625 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.175 | 1.007 | -3.175 | 0.97 | -2.5 | 0.97 | -2.5 | -4.497 | 10.526 | 7.691 | 2.528 | -0.295 | 3.694%
7 | 8.626 | 2.835 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.003 | -3.441 | 1.003 | -3.441 | 0.97 | -2.835 | 0.97 | -2.835 | -4.038 | 10.526 | 8.339 | 2.741 | -0.287 | 3.327%
8 | 9.059 | 2.978 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.001 | -3.622 | 1.001 | -3.622 | 0.97 | -3.063 | 0.97 | -3.063 | -3.723 | 10.526 | 8.781 | 2.886 | -0.278 | 3.069%
9 | 9.181 | 3.018 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -3.673 | 1 | -3.673 | 0.97 | -3.128 | 0.97 | -3.128 | -3.634 | 10.526 | 8.906 | 2.927 | -0.275 | 2.995%
10 | 9.23 | 3.034 | 0.95 | I | cloudy | 10.526 | 10.515 | 5 | 1 | -3.694 | 1 | -3.694 | 0.97 | -3.154 | 0.97 | -3.154 | -3.598 | 10.515 | 8.956 | 2.944 | -0.274 | 2.969%
11 | 9.261 | 3.044 | 0.95 | I | cloudy | 10.526 | 10.484 | 5 | 0.999 | -3.707 | 0.999 | -3.707 | 0.97 | -3.17 | 0.97 | -3.17 | -3.575 | 10.484 | 8.988 | 2.954 | -0.273 | 2.948%
12 | 9.292 | 3.054 | 0.95 | I | cloudy | 10.526 | 10.452 | 5 | 0.999 | -3.72 | 0.999 | -3.72 | 0.97 | -3.186 | 0.97 | -3.186 | -3.552 | 10.452 | 9.02 | 2.965 | -0.272 | 2.927%
13 | 9.322 | 3.064 | 0.95 | I | cloudy | 10.526 | 10.452 | 5 | 0.999 | -3.733 | 0.999 | -3.733 | 0.97 | -3.202 | 0.97 | -3.202 | -3.53 | 10.452 | 9.05 | 2.975 | -0.272 | 2.918%
14 | 9.338 | 3.069 | 0.95 | I | cloudy | 10.526 | 10.473 | 5 | 0.999 | -3.739 | 0.999 | -3.739 | 0.97 | -3.211 | 0.97 | -3.211 | -3.518 | 10.473 | 9.067 | 2.98 | -0.271 | 2.902%
15 | 9.404 | 3.091 | 0.95 | I | cloudy | 10.526 | 10.505 | 5 | 0.999 | -3.767 | 0.999 | -3.767 | 0.97 | -3.246 | 0.97 | -3.246 | -3.47 | 10.505 | 9.135 | 3.002 | -0.269 | 2.86%
16 | 9.594 | 3.153 | 0.95 | I | cloudy | 10.526 | 10.515 | 5 | 0.997 | -3.847 | 0.997 | -3.847 | 0.97 | -3.347 | 0.97 | -3.347 | -3.329 | 10.515 | 9.33 | 3.067 | -0.264 | 2.752%
17 | 9.883 | 3.248 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.97 | 0.996 | -3.97 | 0.97 | -3.502 | 0.97 | -3.502 | -3.113 | 10.526 | 9.629 | 3.165 | -0.254 | 2.57%
18 | 10 | 3.287 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.995 | -4.02 | 0.995 | -4.02 | 0.97 | -3.565 | 0.97 | -3.565 | -3.025 | 10.526 | 9.75 | 3.205 | -0.25 | 2.5%
19 | 9.966 | 3.276 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.995 | -4.005 | 0.995 | -4.005 | 0.97 | -3.547 | 0.97 | -3.547 | -3.051 | 10.526 | 9.714 | 3.193 | -0.252 | 2.529%
20 | 9.857 | 3.24 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.996 | -3.959 | 0.996 | -3.959 | 0.97 | -3.488 | 0.97 | -3.488 | -3.132 | 10.526 | 9.602 | 3.156 | -0.255 | 2.587%
21 | 9.62 | 3.162 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 0.997 | -3.858 | 0.997 | -3.858 | 0.97 | -3.361 | 0.97 | -3.361 | -3.309 | 10.526 | 9.357 | 3.075 | -0.263 | 2.734%
22 | 9.139 | 3.004 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1 | -3.656 | 1 | -3.656 | 0.97 | -3.105 | 0.97 | -3.105 | -3.665 | 10.526 | 8.863 | 2.913 | -0.276 | 3.02%
23 | 8.547 | 2.809 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.004 | -3.408 | 1.004 | -3.408 | 0.97 | -2.793 | 0.97 | -2.793 | -4.095 | 10.526 | 8.259 | 2.715 | -0.288 | 3.37%
24 | 8.047 | 2.645 | 0.95 | I | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.201 | 1.007 | -3.201 | 0.97 | -2.532 | 0.97 | -2.532 | -4.454 | 10.526 | 7.752 | 2.548 | -0.295 | 3.666%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.943 | 1.003 | -3.059 | -5.263 | 5.263 | 7.615 | 1.546 | -0.101 | 1.309%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.029 | -0.916 | 1.004 | -2.975 | -5.263 | 5.263 | 7.418 | 1.506 | -0.099 | 1.317%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.901 | 1.005 | -2.928 | -5.263 | 5.263 | 7.31 | 1.484 | -0.097 | 1.31%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.9 | 1.005 | -2.924 | -5.263 | 5.263 | 7.301 | 1.483 | -0.097 | 1.311%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.922 | 1.004 | -2.994 | -5.263 | 5.263 | 7.464 | 1.516 | -0.099 | 1.309%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.981 | 1.002 | -3.174 | -5.263 | 5.263 | 7.881 | 1.6 | -0.105 | 1.315%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 5.263 | 5.252 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.065 | 0.999 | -3.434 | -5.252 | 5.252 | 8.515 | 1.729 | -0.111 | 1.287%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 5.263 | 5.116 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.142 | 0.997 | -3.665 | -5.116 | 5.116 | 8.94 | 1.815 | -0.119 | 1.314%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 5.263 | 4.705 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.029 | -1.169 | 0.997 | -3.725 | -4.705 | 4.705 | 9.07 | 1.842 | -0.111 | 1.209%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 5.263 | 4.142 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.03 | -1.176 | 0.999 | -3.714 | -4.142 | 4.142 | 9.137 | 1.855 | -0.093 | 1.008%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 5.263 | 3.574 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.032 | -1.205 | 1 | -3.773 | -3.574 | 3.574 | 9.177 | 1.863 | -0.084 | 0.907%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 5.263 | 3.258 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.032 | -1.216 | 1.001 | -3.788 | -3.258 | 3.258 | 9.215 | 1.871 | -0.077 | 0.8287%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 5.263 | 3.353 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.032 | -1.221 | 1 | -3.81 | -3.353 | 3.353 | 9.242 | 1.877 | -0.08 | 0.8582%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 5.263 | 3.505 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.032 | -1.22 | 1 | -3.814 | -3.505 | 3.505 | 9.254 | 1.879 | -0.084 | 0.8996%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 5.263 | 3.942 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.03 | -1.218 | 0.998 | -3.836 | -3.942 | 3.942 | 9.309 | 1.89 | -0.095 | 1.01%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 5.263 | 4.458 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.029 | -1.233 | 0.996 | -3.909 | -4.458 | 4.458 | 9.484 | 1.926 | -0.11 | 1.147%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 5.263 | 4.921 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.027 | -1.251 | 0.994 | -3.991 | -4.921 | 4.921 | 9.762 | 1.982 | -0.121 | 1.224%
18 | 10 | 2.031 | 0.98 | I | very sunny | 5.263 | 5.189 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.262 | 0.992 | -4.04 | -5.189 | 5.189 | 9.87 | 2.004 | -0.13 | 1.3%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 5.263 | 5.258 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.255 | 0.992 | -4.025 | -5.258 | 5.258 | 9.835 | 1.997 | -0.131 | 1.314%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.026 | -1.24 | 0.993 | -3.978 | -5.263 | 5.263 | 9.727 | 1.975 | -0.13 | 1.319%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.207 | 0.994 | -3.875 | -5.263 | 5.263 | 9.493 | 1.928 | -0.127 | 1.32%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.14 | 0.997 | -3.667 | -5.263 | 5.263 | 9.019 | 1.831 | -0.12 | 1.313%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.058 | 0.999 | -3.413 | -5.263 | 5.263 | 8.435 | 1.713 | -0.112 | 1.31%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.989 | 1.002 | -3.2 | -5.263 | 5.263 | 7.941 | 1.613 | -0.106 | 1.317%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.943 | 1.003 | -3.059 | -5.263 | 5.263 | 7.615 | 1.546 | -0.101 | 1.309%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.029 | -0.916 | 1.004 | -2.975 | -5.263 | 5.263 | 7.418 | 1.506 | -0.099 | 1.317%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.901 | 1.005 | -2.928 | -5.263 | 5.263 | 7.31 | 1.484 | -0.097 | 1.31%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.9 | 1.005 | -2.924 | -5.263 | 5.263 | 7.301 | 1.483 | -0.097 | 1.311%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.922 | 1.004 | -2.994 | -5.263 | 5.263 | 7.464 | 1.516 | -0.099 | 1.309%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.981 | 1.002 | -3.174 | -5.263 | 5.263 | 7.881 | 1.6 | -0.105 | 1.315%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.069 | 0.999 | -3.447 | -5.263 | 5.263 | 8.513 | 1.729 | -0.113 | 1.31%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 5.263 | 5.258 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.129 | 0.997 | -3.633 | -5.258 | 5.258 | 8.94 | 1.815 | -0.119 | 1.314%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 5.263 | 5.205 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.027 | -1.147 | 0.996 | -3.686 | -5.205 | 5.205 | 9.062 | 1.84 | -0.119 | 1.296%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 5.263 | 5.095 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.028 | -1.166 | 0.996 | -3.74 | -5.095 | 5.095 | 9.109 | 1.85 | -0.121 | 1.311%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 5.263 | 4.979 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.028 | -1.173 | 0.996 | -3.755 | -4.979 | 4.979 | 9.142 | 1.856 | -0.119 | 1.285%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 5.263 | 4.916 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.028 | -1.179 | 0.996 | -3.77 | -4.916 | 4.916 | 9.174 | 1.863 | -0.118 | 1.27%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 5.263 | 4.984 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.028 | -1.182 | 0.996 | -3.782 | -4.984 | 4.984 | 9.202 | 1.869 | -0.12 | 1.287%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 5.263 | 5.016 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.028 | -1.183 | 0.996 | -3.788 | -5.016 | 5.016 | 9.217 | 1.872 | -0.121 | 1.296%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 5.263 | 5.147 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.027 | -1.189 | 0.995 | -3.815 | -5.147 | 5.147 | 9.279 | 1.884 | -0.125 | 1.329%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 5.263 | 5.237 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.027 | -1.214 | 0.994 | -3.896 | -5.237 | 5.237 | 9.464 | 1.922 | -0.13 | 1.355%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.026 | -1.244 | 0.993 | -3.989 | -5.263 | 5.263 | 9.753 | 1.98 | -0.13 | 1.315%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.26 | 0.992 | -4.04 | -5.263 | 5.263 | 9.868 | 2.004 | -0.132 | 1.32%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.255 | 0.992 | -4.025 | -5.263 | 5.263 | 9.834 | 1.997 | -0.132 | 1.324%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.026 | -1.24 | 0.993 | -3.978 | -5.263 | 5.263 | 9.727 | 1.975 | -0.13 | 1.319%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.207 | 0.994 | -3.875 | -5.263 | 5.263 | 9.493 | 1.928 | -0.127 | 1.32%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.14 | 0.997 | -3.667 | -5.263 | 5.263 | 9.019 | 1.831 | -0.12 | 1.313%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.058 | 0.999 | -3.413 | -5.263 | 5.263 | 8.435 | 1.713 | -0.112 | 1.31%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.989 | 1.002 | -3.2 | -5.263 | 5.263 | 7.941 | 1.613 | -0.106 | 1.317%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.029 | -0.943 | 1.003 | -3.059 | -5.263 | 5.263 | 7.615 | 1.546 | -0.101 | 1.309%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.029 | -0.916 | 1.004 | -2.975 | -5.263 | 5.263 | 7.418 | 1.506 | -0.099 | 1.317%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.03 | -0.901 | 1.005 | -2.928 | -5.263 | 5.263 | 7.31 | 1.484 | -0.097 | 1.31%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.03 | -0.9 | 1.005 | -2.924 | -5.263 | 5.263 | 7.301 | 1.483 | -0.097 | 1.311%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.029 | -0.922 | 1.004 | -2.994 | -5.263 | 5.263 | 7.464 | 1.516 | -0.099 | 1.309%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.029 | -0.981 | 1.002 | -3.174 | -5.263 | 5.263 | 7.881 | 1.6 | -0.105 | 1.315%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.028 | -1.069 | 0.999 | -3.447 | -5.263 | 5.263 | 8.513 | 1.729 | -0.113 | 1.31%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.028 | -1.129 | 0.997 | -3.633 | -5.263 | 5.263 | 8.94 | 1.815 | -0.119 | 1.314%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.027 | -1.146 | 0.996 | -3.685 | -5.263 | 5.263 | 9.06 | 1.84 | -0.121 | 1.318%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 5.263 | 5.258 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.027 | -1.153 | 0.996 | -3.707 | -5.258 | 5.258 | 9.109 | 1.85 | -0.121 | 1.311%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 5.263 | 5.242 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.027 | -1.158 | 0.996 | -3.72 | -5.242 | 5.242 | 9.139 | 1.856 | -0.122 | 1.317%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 5.263 | 5.226 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.027 | -1.162 | 0.996 | -3.734 | -5.226 | 5.226 | 9.17 | 1.862 | -0.122 | 1.313%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 5.263 | 5.226 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.027 | -1.166 | 0.996 | -3.746 | -5.226 | 5.226 | 9.2 | 1.868 | -0.122 | 1.309%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 5.263 | 5.237 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.027 | -1.178 | 0.995 | -3.784 | -5.237 | 5.237 | 9.212 | 1.871 | -0.126 | 1.349%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 5.263 | 5.252 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.027 | -1.187 | 0.995 | -3.813 | -5.252 | 5.252 | 9.277 | 1.884 | -0.127 | 1.35%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 5.263 | 5.258 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.027 | -1.203 | 0.994 | -3.864 | -5.258 | 5.258 | 9.468 | 1.922 | -0.126 | 1.313%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.026 | -1.244 | 0.993 | -3.989 | -5.263 | 5.263 | 9.753 | 1.98 | -0.13 | 1.315%
18 | 10 | 2.031 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.026 | -1.26 | 0.992 | -4.04 | -5.263 | 5.263 | 9.868 | 2.004 | -0.132 | 1.32%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.026 | -1.255 | 0.992 | -4.025 | -5.263 | 5.263 | 9.834 | 1.997 | -0.132 | 1.324%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.026 | -1.24 | 0.993 | -3.978 | -5.263 | 5.263 | 9.727 | 1.975 | -0.13 | 1.319%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.027 | -1.207 | 0.994 | -3.875 | -5.263 | 5.263 | 9.493 | 1.928 | -0.127 | 1.32%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.027 | -1.14 | 0.997 | -3.667 | -5.263 | 5.263 | 9.019 | 1.831 | -0.12 | 1.313%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.028 | -1.058 | 0.999 | -3.413 | -5.263 | 5.263 | 8.435 | 1.713 | -0.112 | 1.31%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 5.263 | 5.263 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.029 | -0.989 | 1.002 | -3.2 | -5.263 | 5.263 | 7.941 | 1.613 | -0.106 | 1.317%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.819 | 0.989 | -2.973 | -10.526 | 10.526 | 7.507 | 1.524 | -0.209 | 2.709%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.015 | -0.791 | 0.99 | -2.888 | -10.526 | 10.526 | 7.314 | 1.485 | -0.203 | 2.701%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.776 | 0.991 | -2.84 | -10.526 | 10.526 | 7.207 | 1.463 | -0.2 | 2.7%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.775 | 0.991 | -2.837 | -10.526 | 10.526 | 7.198 | 1.462 | -0.2 | 2.703%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.015 | -0.798 | 0.99 | -2.907 | -10.526 | 10.526 | 7.358 | 1.494 | -0.205 | 2.711%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.856 | 0.988 | -3.089 | -10.526 | 10.526 | 7.769 | 1.578 | -0.217 | 2.717%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 10.526 | 10.505 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.937 | 0.985 | -3.337 | -10.505 | 10.505 | 8.395 | 1.705 | -0.231 | 2.678%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 10.526 | 10.231 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.014 | -1.016 | 0.983 | -3.574 | -10.231 | 10.231 | 8.817 | 1.79 | -0.242 | 2.671%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 10.526 | 9.41 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.016 | -1.054 | 0.985 | -3.642 | -9.41 | 9.41 | 8.956 | 1.819 | -0.225 | 2.451%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 10.526 | 8.284 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.019 | -1.077 | 0.988 | -3.644 | -8.284 | 8.284 | 9.036 | 1.835 | -0.194 | 2.102%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 10.526 | 7.147 | 3 | 1.041 | -1.291 | 1.009 | -3.84 | 1.022 | -1.118 | 0.991 | -3.707 | -7.147 | 7.147 | 9.091 | 1.846 | -0.17 | 1.836%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 10.526 | 6.516 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.024 | -1.135 | 0.992 | -3.725 | -6.516 | 6.516 | 9.137 | 1.855 | -0.155 | 1.668%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 10.526 | 6.705 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.023 | -1.14 | 0.991 | -3.752 | -6.705 | 6.705 | 9.16 | 1.86 | -0.162 | 1.738%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 10.526 | 7.01 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.022 | -1.135 | 0.991 | -3.753 | -7.01 | 7.01 | 9.169 | 1.862 | -0.169 | 1.81%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 10.526 | 7.884 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.02 | -1.123 | 0.988 | -3.766 | -7.884 | 7.884 | 9.212 | 1.87 | -0.192 | 2.042%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 10.526 | 8.916 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.017 | -1.124 | 0.984 | -3.832 | -8.916 | 8.916 | 9.371 | 1.903 | -0.223 | 2.324%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 10.526 | 9.842 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.014 | -1.134 | 0.98 | -3.92 | -9.842 | 9.842 | 9.631 | 1.956 | -0.252 | 2.55%
18 | 10 | 2.031 | 0.98 | I | very sunny | 10.526 | 10.379 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.013 | -1.139 | 0.978 | -3.969 | -10.379 | 10.379 | 9.73 | 1.976 | -0.27 | 2.7%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 10.526 | 10.515 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.132 | 0.978 | -3.953 | -10.515 | 10.515 | 9.693 | 1.968 | -0.273 | 2.739%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.012 | -1.116 | 0.979 | -3.905 | -10.526 | 10.526 | 9.587 | 1.947 | -0.27 | 2.739%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.083 | 0.98 | -3.801 | -10.526 | 10.526 | 9.357 | 1.9 | -0.263 | 2.734%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.013 | -1.016 | 0.982 | -3.59 | -10.526 | 10.526 | 8.889 | 1.805 | -0.25 | 2.736%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.934 | 0.985 | -3.332 | -10.526 | 10.526 | 8.314 | 1.688 | -0.233 | 2.726%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.865 | 0.988 | -3.116 | -10.526 | 10.526 | 7.829 | 1.59 | -0.218 | 2.709%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.819 | 0.989 | -2.973 | -10.526 | 10.526 | 7.507 | 1.524 | -0.209 | 2.709%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.015 | -0.791 | 0.99 | -2.888 | -10.526 | 10.526 | 7.314 | 1.485 | -0.203 | 2.701%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.776 | 0.991 | -2.84 | -10.526 | 10.526 | 7.207 | 1.463 | -0.2 | 2.7%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.775 | 0.991 | -2.837 | -10.526 | 10.526 | 7.198 | 1.462 | -0.2 | 2.703%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.015 | -0.798 | 0.99 | -2.907 | -10.526 | 10.526 | 7.358 | 1.494 | -0.205 | 2.711%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.856 | 0.988 | -3.089 | -10.526 | 10.526 | 7.769 | 1.578 | -0.217 | 2.717%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.945 | 0.985 | -3.366 | -10.526 | 10.526 | 8.391 | 1.704 | -0.235 | 2.724%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 10.526 | 10.515 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.013 | -1.005 | 0.983 | -3.555 | -10.515 | 10.515 | 8.812 | 1.789 | -0.247 | 2.727%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 10.526 | 10.41 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.014 | -1.024 | 0.982 | -3.609 | -10.41 | 10.41 | 8.933 | 1.814 | -0.248 | 2.701%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 10.526 | 10.189 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.014 | -1.041 | 0.983 | -3.649 | -10.189 | 10.189 | 8.985 | 1.824 | -0.245 | 2.654%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 10.526 | 9.958 | 3 | 1.041 | -1.291 | 1.009 | -3.839 | 1.015 | -1.052 | 0.983 | -3.667 | -9.958 | 9.958 | 9.021 | 1.832 | -0.24 | 2.592%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 10.526 | 9.831 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.015 | -1.059 | 0.983 | -3.683 | -9.831 | 9.831 | 9.054 | 1.838 | -0.238 | 2.561%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 10.526 | 9.968 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.014 | -1.06 | 0.983 | -3.694 | -9.968 | 9.968 | 9.08 | 1.844 | -0.242 | 2.596%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 10.526 | 10.031 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.014 | -1.06 | 0.982 | -3.7 | -10.031 | 10.031 | 9.094 | 1.847 | -0.244 | 2.613%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 10.526 | 10.294 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.014 | -1.063 | 0.981 | -3.724 | -10.294 | 10.294 | 9.151 | 1.858 | -0.253 | 2.69%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 10.526 | 10.473 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.013 | -1.085 | 0.98 | -3.805 | -10.473 | 10.473 | 9.331 | 1.895 | -0.263 | 2.741%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.012 | -1.12 | 0.978 | -3.916 | -10.526 | 10.526 | 9.612 | 1.952 | -0.271 | 2.742%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.012 | -1.136 | 0.978 | -3.968 | -10.526 | 10.526 | 9.726 | 1.975 | -0.274 | 2.74%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.132 | 0.978 | -3.953 | -10.526 | 10.526 | 9.693 | 1.968 | -0.273 | 2.739%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.012 | -1.116 | 0.979 | -3.905 | -10.526 | 10.526 | 9.587 | 1.947 | -0.27 | 2.739%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.083 | 0.98 | -3.801 | -10.526 | 10.526 | 9.357 | 1.9 | -0.263 | 2.734%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.013 | -1.016 | 0.982 | -3.59 | -10.526 | 10.526 | 8.889 | 1.805 | -0.25 | 2.736%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.934 | 0.985 | -3.332 | -10.526 | 10.526 | 8.314 | 1.688 | -0.233 | 2.726%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.865 | 0.988 | -3.116 | -10.526 | 10.526 | 7.829 | 1.59 | -0.218 | 2.709%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.075 | 1.017 | -3.179 | 1.015 | -0.819 | 0.989 | -2.973 | -10.526 | 10.526 | 7.507 | 1.524 | -0.209 | 2.709%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.048 | 1.018 | -3.095 | 1.015 | -0.791 | 0.99 | -2.888 | -10.526 | 10.526 | 7.314 | 1.485 | -0.203 | 2.701%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.032 | 1.018 | -3.048 | 1.016 | -0.776 | 0.991 | -2.84 | -10.526 | 10.526 | 7.207 | 1.463 | -0.2 | 2.7%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.031 | 1.018 | -3.044 | 1.016 | -0.775 | 0.991 | -2.837 | -10.526 | 10.526 | 7.198 | 1.462 | -0.2 | 2.703%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.054 | 1.018 | -3.114 | 1.015 | -0.798 | 0.99 | -2.907 | -10.526 | 10.526 | 7.358 | 1.494 | -0.205 | 2.711%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.113 | 1.016 | -3.293 | 1.015 | -0.856 | 0.988 | -3.089 | -10.526 | 10.526 | 7.769 | 1.578 | -0.217 | 2.717%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.202 | 1.012 | -3.567 | 1.014 | -0.945 | 0.985 | -3.366 | -10.526 | 10.526 | 8.391 | 1.704 | -0.235 | 2.724%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.263 | 1.01 | -3.752 | 1.013 | -1.005 | 0.983 | -3.555 | -10.526 | 10.526 | 8.812 | 1.789 | -0.247 | 2.727%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.28 | 1.01 | -3.805 | 1.013 | -1.022 | 0.982 | -3.608 | -10.526 | 10.526 | 8.93 | 1.813 | -0.251 | 2.734%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 10.526 | 10.515 | 3 | 1.041 | -1.287 | 1.009 | -3.826 | 1.013 | -1.029 | 0.982 | -3.63 | -10.515 | 10.515 | 8.978 | 1.823 | -0.252 | 2.73%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 10.526 | 10.484 | 3 | 1.041 | -1.291 | 1.009 | -3.839 | 1.013 | -1.034 | 0.982 | -3.644 | -10.484 | 10.484 | 9.009 | 1.829 | -0.252 | 2.721%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 10.526 | 10.452 | 3 | 1.041 | -1.296 | 1.009 | -3.853 | 1.013 | -1.039 | 0.982 | -3.657 | -10.452 | 10.452 | 9.04 | 1.836 | -0.252 | 2.712%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 10.526 | 10.452 | 3 | 1.041 | -1.3 | 1.009 | -3.866 | 1.013 | -1.043 | 0.982 | -3.67 | -10.452 | 10.452 | 9.069 | 1.842 | -0.253 | 2.714%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 10.526 | 10.473 | 3 | 1.041 | -1.302 | 1.009 | -3.873 | 1.013 | -1.05 | 0.981 | -3.692 | -10.473 | 10.473 | 9.083 | 1.844 | -0.255 | 2.731%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 10.526 | 10.505 | 3 | 1.041 | -1.311 | 1.008 | -3.901 | 1.013 | -1.058 | 0.981 | -3.72 | -10.505 | 10.505 | 9.146 | 1.857 | -0.258 | 2.744%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 10.526 | 10.515 | 3 | 1.04 | -1.338 | 1.008 | -3.983 | 1.013 | -1.08 | 0.98 | -3.789 | -10.515 | 10.515 | 9.332 | 1.895 | -0.262 | 2.731%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.379 | 1.006 | -4.109 | 1.012 | -1.12 | 0.978 | -3.916 | -10.526 | 10.526 | 9.612 | 1.952 | -0.271 | 2.742%
18 | 10 | 2.031 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.395 | 1.005 | -4.16 | 1.012 | -1.136 | 0.978 | -3.968 | -10.526 | 10.526 | 9.726 | 1.975 | -0.274 | 2.74%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.39 | 1.006 | -4.145 | 1.012 | -1.132 | 0.978 | -3.953 | -10.526 | 10.526 | 9.693 | 1.968 | -0.273 | 2.739%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.375 | 1.006 | -4.097 | 1.012 | -1.116 | 0.979 | -3.905 | -10.526 | 10.526 | 9.587 | 1.947 | -0.27 | 2.739%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.342 | 1.007 | -3.995 | 1.013 | -1.083 | 0.98 | -3.801 | -10.526 | 10.526 | 9.357 | 1.9 | -0.263 | 2.734%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.274 | 1.01 | -3.787 | 1.013 | -1.016 | 0.982 | -3.59 | -10.526 | 10.526 | 8.889 | 1.805 | -0.25 | 2.736%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.191 | 1.013 | -3.533 | 1.014 | -0.934 | 0.985 | -3.332 | -10.526 | 10.526 | 8.314 | 1.688 | -0.233 | 2.726%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 10.526 | 10.526 | 3 | 1.042 | -1.121 | 1.015 | -3.319 | 1.015 | -0.865 | 0.988 | -3.116 | -10.526 | 10.526 | 7.829 | 1.59 | -0.218 | 2.709%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.001 | -1.663 | 0.989 | -2.755 | -5.263 | 5.263 | 7.502 | 1.523 | -0.214 | 2.773%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.002 | -1.608 | 0.99 | -2.67 | -5.263 | 5.263 | 7.309 | 1.484 | -0.208 | 2.767%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.002 | -1.578 | 0.99 | -2.624 | -5.263 | 5.263 | 7.202 | 1.463 | -0.205 | 2.768%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.002 | -1.575 | 0.99 | -2.62 | -5.263 | 5.263 | 7.194 | 1.461 | -0.204 | 2.757%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.002 | -1.621 | 0.989 | -2.69 | -5.263 | 5.263 | 7.354 | 1.493 | -0.209 | 2.763%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.737 | 0.987 | -2.87 | -5.263 | 5.263 | 7.765 | 1.577 | -0.221 | 2.767%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 5.263 | 5.252 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.897 | 0.985 | -3.116 | -5.252 | 5.252 | 8.39 | 1.704 | -0.236 | 2.736%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 5.263 | 5.116 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.998 | -2.054 | 0.983 | -3.353 | -5.116 | 5.116 | 8.812 | 1.789 | -0.247 | 2.727%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 5.263 | 4.705 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 1 | -2.124 | 0.984 | -3.439 | -4.705 | 4.705 | 8.951 | 1.818 | -0.23 | 2.505%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 5.263 | 4.142 | 4 | 1.025 | -2.537 | 1.009 | -3.826 | 1.003 | -2.165 | 0.988 | -3.47 | -4.142 | 4.142 | 9.032 | 1.834 | -0.198 | 2.145%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 5.263 | 3.574 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 1.006 | -2.241 | 0.99 | -3.557 | -3.574 | 3.574 | 9.087 | 1.845 | -0.174 | 1.879%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 5.263 | 3.258 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 1.007 | -2.272 | 0.992 | -3.588 | -3.258 | 3.258 | 9.134 | 1.855 | -0.158 | 1.7%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 5.263 | 3.353 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 1.007 | -2.281 | 0.991 | -3.608 | -3.353 | 3.353 | 9.157 | 1.859 | -0.165 | 1.77%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 5.263 | 3.505 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 1.006 | -2.273 | 0.99 | -3.603 | -3.505 | 3.505 | 9.165 | 1.861 | -0.173 | 1.853%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 5.263 | 3.942 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 1.004 | -2.228 | 0.988 | -3.556 | -3.942 | 3.942 | 9.213 | 1.871 | -0.191 | 2.031%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 5.263 | 4.458 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 1 | -2.262 | 0.984 | -3.638 | -4.458 | 4.458 | 9.366 | 1.902 | -0.228 | 2.376%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 5.263 | 4.921 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.996 | -2.29 | 0.98 | -3.708 | -4.921 | 4.921 | 9.625 | 1.954 | -0.258 | 2.611%
18 | 10 | 2.031 | 0.98 | I | very sunny | 5.263 | 5.189 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.994 | -2.303 | 0.978 | -3.744 | -5.189 | 5.189 | 9.723 | 1.974 | -0.277 | 2.77%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 5.263 | 5.258 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.994 | -2.289 | 0.977 | -3.726 | -5.258 | 5.258 | 9.686 | 1.967 | -0.28 | 2.81%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.258 | 0.978 | -3.678 | -5.263 | 5.263 | 9.58 | 1.945 | -0.277 | 2.81%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.995 | -2.192 | 0.979 | -3.574 | -5.263 | 5.263 | 9.35 | 1.899 | -0.27 | 2.807%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.997 | -2.057 | 0.982 | -3.366 | -5.263 | 5.263 | 8.884 | 1.804 | -0.255 | 2.79%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.893 | 0.985 | -3.111 | -5.263 | 5.263 | 8.309 | 1.687 | -0.238 | 2.785%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1 | -1.754 | 0.987 | -2.896 | -5.263 | 5.263 | 7.824 | 1.589 | -0.223 | 2.771%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.001 | -1.663 | 0.989 | -2.755 | -5.263 | 5.263 | 7.502 | 1.523 | -0.214 | 2.773%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.002 | -1.608 | 0.99 | -2.67 | -5.263 | 5.263 | 7.309 | 1.484 | -0.208 | 2.767%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.002 | -1.578 | 0.99 | -2.624 | -5.263 | 5.263 | 7.202 | 1.463 | -0.205 | 2.768%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.002 | -1.575 | 0.99 | -2.62 | -5.263 | 5.263 | 7.194 | 1.461 | -0.204 | 2.757%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.002 | -1.621 | 0.989 | -2.69 | -5.263 | 5.263 | 7.354 | 1.493 | -0.209 | 2.763%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.737 | 0.987 | -2.87 | -5.263 | 5.263 | 7.765 | 1.577 | -0.221 | 2.767%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.915 | 0.984 | -3.145 | -5.263 | 5.263 | 8.386 | 1.703 | -0.24 | 2.782%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 5.263 | 5.258 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.997 | -2.035 | 0.982 | -3.332 | -5.258 | 5.258 | 8.806 | 1.788 | -0.253 | 2.793%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 5.263 | 5.205 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.997 | -2.073 | 0.982 | -3.387 | -5.205 | 5.205 | 8.928 | 1.813 | -0.253 | 2.756%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 5.263 | 5.095 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.997 | -2.104 | 0.982 | -3.429 | -5.095 | 5.095 | 8.979 | 1.823 | -0.251 | 2.719%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 5.263 | 4.979 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.998 | -2.123 | 0.982 | -3.452 | -4.979 | 4.979 | 9.015 | 1.831 | -0.246 | 2.656%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 5.263 | 4.916 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.998 | -2.137 | 0.983 | -3.47 | -4.916 | 4.916 | 9.049 | 1.837 | -0.243 | 2.615%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 5.263 | 4.984 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.998 | -2.139 | 0.982 | -3.478 | -4.984 | 4.984 | 9.074 | 1.843 | -0.248 | 2.66%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 5.263 | 5.016 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.998 | -2.141 | 0.982 | -3.482 | -5.016 | 5.016 | 9.088 | 1.845 | -0.25 | 2.677%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 5.263 | 5.147 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.997 | -2.148 | 0.981 | -3.5 | -5.147 | 5.147 | 9.146 | 1.857 | -0.258 | 2.744%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 5.263 | 5.237 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.996 | -2.186 | 0.979 | -3.565 | -5.237 | 5.237 | 9.327 | 1.894 | -0.267 | 2.783%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.994 | -2.265 | 0.978 | -3.689 | -5.263 | 5.263 | 9.605 | 1.95 | -0.278 | 2.813%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.994 | -2.298 | 0.977 | -3.74 | -5.263 | 5.263 | 9.719 | 1.974 | -0.281 | 2.81%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.994 | -2.289 | 0.977 | -3.725 | -5.263 | 5.263 | 9.686 | 1.967 | -0.28 | 2.81%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.258 | 0.978 | -3.678 | -5.263 | 5.263 | 9.58 | 1.945 | -0.277 | 2.81%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.995 | -2.192 | 0.979 | -3.574 | -5.263 | 5.263 | 9.35 | 1.899 | -0.27 | 2.807%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.997 | -2.057 | 0.982 | -3.366 | -5.263 | 5.263 | 8.884 | 1.804 | -0.255 | 2.79%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.893 | 0.985 | -3.111 | -5.263 | 5.263 | 8.309 | 1.687 | -0.238 | 2.785%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1 | -1.754 | 0.987 | -2.896 | -5.263 | 5.263 | 7.824 | 1.589 | -0.223 | 2.771%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 1.001 | -1.663 | 0.989 | -2.755 | -5.263 | 5.263 | 7.502 | 1.523 | -0.214 | 2.773%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 1.002 | -1.608 | 0.99 | -2.67 | -5.263 | 5.263 | 7.309 | 1.484 | -0.208 | 2.767%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 1.002 | -1.578 | 0.99 | -2.624 | -5.263 | 5.263 | 7.202 | 1.463 | -0.205 | 2.768%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 1.002 | -1.575 | 0.99 | -2.62 | -5.263 | 5.263 | 7.194 | 1.461 | -0.204 | 2.757%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 1.002 | -1.621 | 0.989 | -2.69 | -5.263 | 5.263 | 7.354 | 1.493 | -0.209 | 2.763%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.029 | -2.189 | 1.016 | -3.293 | 1.001 | -1.737 | 0.987 | -2.87 | -5.263 | 5.263 | 7.765 | 1.577 | -0.221 | 2.767%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.999 | -1.915 | 0.984 | -3.145 | -5.263 | 5.263 | 8.386 | 1.703 | -0.24 | 2.782%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.489 | 1.01 | -3.752 | 0.997 | -2.035 | 0.982 | -3.331 | -5.263 | 5.263 | 8.806 | 1.788 | -0.253 | 2.793%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.997 | -2.069 | 0.981 | -3.384 | -5.263 | 5.263 | 8.924 | 1.812 | -0.257 | 2.799%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 5.263 | 5.258 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.997 | -2.083 | 0.981 | -3.405 | -5.258 | 5.258 | 8.972 | 1.822 | -0.258 | 2.795%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 5.263 | 5.242 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.997 | -2.093 | 0.981 | -3.42 | -5.242 | 5.242 | 9.003 | 1.828 | -0.258 | 2.786%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 5.263 | 5.226 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.997 | -2.103 | 0.981 | -3.434 | -5.226 | 5.226 | 9.034 | 1.834 | -0.258 | 2.777%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 5.263 | 5.226 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.997 | -2.111 | 0.981 | -3.447 | -5.226 | 5.226 | 9.063 | 1.84 | -0.259 | 2.778%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 5.263 | 5.237 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.996 | -2.122 | 0.981 | -3.464 | -5.237 | 5.237 | 9.077 | 1.843 | -0.261 | 2.795%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 5.263 | 5.252 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.996 | -2.139 | 0.98 | -3.492 | -5.252 | 5.252 | 9.14 | 1.856 | -0.264 | 2.807%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 5.263 | 5.258 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.995 | -2.185 | 0.979 | -3.563 | -5.258 | 5.258 | 9.325 | 1.894 | -0.269 | 2.804%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.994 | -2.265 | 0.978 | -3.689 | -5.263 | 5.263 | 9.605 | 1.95 | -0.278 | 2.813%
18 | 10 | 2.031 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.994 | -2.298 | 0.977 | -3.74 | -5.263 | 5.263 | 9.719 | 1.974 | -0.281 | 2.81%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.994 | -2.289 | 0.977 | -3.725 | -5.263 | 5.263 | 9.686 | 1.967 | -0.28 | 2.81%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.995 | -2.258 | 0.978 | -3.678 | -5.263 | 5.263 | 9.58 | 1.945 | -0.277 | 2.81%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.995 | -2.192 | 0.979 | -3.574 | -5.263 | 5.263 | 9.35 | 1.899 | -0.27 | 2.807%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.997 | -2.057 | 0.982 | -3.366 | -5.263 | 5.263 | 8.884 | 1.804 | -0.255 | 2.79%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.999 | -1.893 | 0.985 | -3.111 | -5.263 | 5.263 | 8.309 | 1.687 | -0.238 | 2.785%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 5.263 | 5.263 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 1 | -1.754 | 0.987 | -2.896 | -5.263 | 5.263 | 7.824 | 1.589 | -0.223 | 2.771%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.48 | 0.977 | -2.588 | -7.371 | 10.526 | 7.412 | 1.505 | -0.304 | 3.94%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.425 | 0.978 | -2.502 | -7.373 | 10.526 | 7.222 | 1.466 | -0.295 | 3.924%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.395 | 0.978 | -2.455 | -7.374 | 10.526 | 7.116 | 1.445 | -0.291 | 3.929%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.392 | 0.978 | -2.452 | -7.374 | 10.526 | 7.107 | 1.443 | -0.291 | 3.933%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.438 | 0.978 | -2.522 | -7.372 | 10.526 | 7.266 | 1.475 | -0.297 | 3.927%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.555 | 0.976 | -2.704 | -7.366 | 10.526 | 7.671 | 1.558 | -0.315 | 3.944%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 10.526 | 10.505 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.733 | 0.972 | -2.98 | -7.357 | 10.505 | 8.285 | 1.682 | -0.341 | 3.953%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 10.526 | 10.231 | 4 | 1.025 | -2.489 | 1.01 | -3.753 | 0.985 | -1.854 | 0.97 | -3.168 | -7.351 | 10.231 | 8.7 | 1.767 | -0.359 | 3.963%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 10.526 | 9.41 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.995 | -2.046 | 0.98 | -3.366 | -5.57 | 9.41 | 8.908 | 1.809 | -0.273 | 2.974%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 10.526 | 8.284 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -2.06 | 0.979 | -3.387 | -5.57 | 8.284 | 8.956 | 1.819 | -0.274 | 2.969%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 10.526 | 7.147 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -2.069 | 0.979 | -3.401 | -5.57 | 7.147 | 8.986 | 1.825 | -0.275 | 2.969%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 10.526 | 6.516 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -2.078 | 0.979 | -3.414 | -5.569 | 6.516 | 9.016 | 1.831 | -0.276 | 2.97%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 10.526 | 6.705 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2.086 | 0.979 | -3.427 | -5.569 | 6.705 | 9.045 | 1.837 | -0.277 | 2.971%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 10.526 | 7.01 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.09 | 0.979 | -3.434 | -5.569 | 7.01 | 9.06 | 1.84 | -0.278 | 2.977%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 10.526 | 7.884 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.109 | 0.978 | -3.463 | -5.568 | 7.884 | 9.124 | 1.853 | -0.28 | 2.977%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 10.526 | 8.916 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.162 | 0.978 | -3.546 | -5.566 | 8.916 | 9.308 | 1.89 | -0.286 | 2.981%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 10.526 | 9.842 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.244 | 0.976 | -3.672 | -5.563 | 9.842 | 9.588 | 1.947 | -0.295 | 2.985%
18 | 10 | 2.031 | 0.98 | I | very sunny | 10.526 | 10.379 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.277 | 0.975 | -3.724 | -5.561 | 10.379 | 9.702 | 1.97 | -0.298 | 2.98%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 10.526 | 10.515 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.267 | 0.976 | -3.709 | -5.562 | 10.515 | 9.669 | 1.963 | -0.297 | 2.98%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.236 | 0.976 | -3.661 | -5.563 | 10.526 | 9.563 | 1.942 | -0.294 | 2.983%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.17 | 0.977 | -3.557 | -5.565 | 10.526 | 9.333 | 1.895 | -0.287 | 2.983%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.995 | -2.035 | 0.98 | -3.348 | -5.571 | 10.526 | 8.867 | 1.801 | -0.272 | 2.976%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.711 | 0.973 | -2.946 | -7.359 | 10.526 | 8.209 | 1.667 | -0.338 | 3.955%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.572 | 0.975 | -2.73 | -7.365 | 10.526 | 7.73 | 1.57 | -0.317 | 3.939%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.48 | 0.977 | -2.588 | -7.37 | 10.526 | 7.412 | 1.505 | -0.304 | 3.94%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.425 | 0.978 | -2.502 | -7.373 | 10.526 | 7.222 | 1.466 | -0.295 | 3.924%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.395 | 0.978 | -2.455 | -7.374 | 10.526 | 7.116 | 1.445 | -0.291 | 3.929%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.392 | 0.978 | -2.452 | -7.374 | 10.526 | 7.107 | 1.443 | -0.291 | 3.933%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.438 | 0.978 | -2.522 | -7.372 | 10.526 | 7.266 | 1.475 | -0.297 | 3.927%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.555 | 0.976 | -2.704 | -7.366 | 10.526 | 7.671 | 1.558 | -0.315 | 3.944%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.733 | 0.972 | -2.98 | -7.357 | 10.526 | 8.285 | 1.682 | -0.341 | 3.953%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 10.526 | 10.515 | 4 | 1.025 | -2.489 | 1.01 | -3.753 | 0.985 | -1.854 | 0.97 | -3.168 | -7.351 | 10.515 | 8.7 | 1.767 | -0.359 | 3.963%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 10.526 | 10.41 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.995 | -2.046 | 0.98 | -3.366 | -5.57 | 10.41 | 8.908 | 1.809 | -0.273 | 2.974%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 10.526 | 10.189 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -2.06 | 0.979 | -3.387 | -5.57 | 10.189 | 8.956 | 1.819 | -0.274 | 2.969%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 10.526 | 9.958 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -2.069 | 0.979 | -3.401 | -5.57 | 9.958 | 8.986 | 1.825 | -0.275 | 2.969%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 10.526 | 9.831 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -2.078 | 0.979 | -3.414 | -5.569 | 9.831 | 9.016 | 1.831 | -0.276 | 2.97%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 10.526 | 9.968 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2.086 | 0.979 | -3.427 | -5.569 | 9.968 | 9.045 | 1.837 | -0.277 | 2.971%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 10.526 | 10.031 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.09 | 0.979 | -3.434 | -5.569 | 10.031 | 9.06 | 1.84 | -0.278 | 2.977%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 10.526 | 10.294 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.109 | 0.978 | -3.463 | -5.568 | 10.294 | 9.124 | 1.853 | -0.28 | 2.977%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 10.526 | 10.473 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.162 | 0.978 | -3.546 | -5.566 | 10.473 | 9.308 | 1.89 | -0.286 | 2.981%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.244 | 0.976 | -3.672 | -5.563 | 10.526 | 9.588 | 1.947 | -0.295 | 2.985%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.277 | 0.975 | -3.724 | -5.561 | 10.526 | 9.702 | 1.97 | -0.298 | 2.98%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.267 | 0.976 | -3.709 | -5.562 | 10.526 | 9.669 | 1.963 | -0.297 | 2.98%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.236 | 0.976 | -3.661 | -5.563 | 10.526 | 9.563 | 1.942 | -0.294 | 2.983%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.17 | 0.977 | -3.557 | -5.565 | 10.526 | 9.333 | 1.895 | -0.287 | 2.983%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.995 | -2.035 | 0.98 | -3.348 | -5.571 | 10.526 | 8.867 | 1.801 | -0.272 | 2.976%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.711 | 0.973 | -2.946 | -7.359 | 10.526 | 8.209 | 1.667 | -0.338 | 3.955%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.572 | 0.975 | -2.73 | -7.365 | 10.526 | 7.73 | 1.57 | -0.317 | 3.939%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.114 | 1.017 | -3.179 | 0.99 | -1.48 | 0.977 | -2.588 | -7.37 | 10.526 | 7.412 | 1.505 | -0.304 | 3.94%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.059 | 1.018 | -3.095 | 0.99 | -1.425 | 0.978 | -2.502 | -7.373 | 10.526 | 7.222 | 1.466 | -0.295 | 3.924%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.031 | -2.029 | 1.018 | -3.048 | 0.991 | -1.395 | 0.978 | -2.455 | -7.374 | 10.526 | 7.116 | 1.445 | -0.291 | 3.929%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.031 | -2.026 | 1.018 | -3.044 | 0.991 | -1.392 | 0.978 | -2.452 | -7.374 | 10.526 | 7.107 | 1.443 | -0.291 | 3.933%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.03 | -2.072 | 1.018 | -3.114 | 0.99 | -1.438 | 0.978 | -2.522 | -7.372 | 10.526 | 7.266 | 1.475 | -0.297 | 3.927%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.029 | -2.19 | 1.016 | -3.294 | 0.989 | -1.555 | 0.976 | -2.704 | -7.366 | 10.526 | 7.671 | 1.558 | -0.315 | 3.944%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.368 | 1.012 | -3.567 | 0.987 | -1.733 | 0.972 | -2.98 | -7.357 | 10.526 | 8.285 | 1.682 | -0.341 | 3.953%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.489 | 1.01 | -3.753 | 0.985 | -1.854 | 0.97 | -3.168 | -7.351 | 10.526 | 8.7 | 1.767 | -0.359 | 3.963%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.524 | 1.01 | -3.805 | 0.995 | -2.046 | 0.98 | -3.366 | -5.57 | 10.526 | 8.908 | 1.809 | -0.273 | 2.974%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 10.526 | 10.515 | 4 | 1.025 | -2.538 | 1.009 | -3.826 | 0.995 | -2.06 | 0.979 | -3.387 | -5.57 | 10.515 | 8.956 | 1.819 | -0.274 | 2.969%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 10.526 | 10.484 | 4 | 1.025 | -2.546 | 1.009 | -3.84 | 0.995 | -2.069 | 0.979 | -3.401 | -5.57 | 10.484 | 8.986 | 1.825 | -0.275 | 2.969%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 10.526 | 10.452 | 4 | 1.025 | -2.555 | 1.009 | -3.853 | 0.995 | -2.078 | 0.979 | -3.414 | -5.569 | 10.452 | 9.016 | 1.831 | -0.276 | 2.97%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 10.526 | 10.452 | 4 | 1.025 | -2.563 | 1.009 | -3.866 | 0.995 | -2.086 | 0.979 | -3.427 | -5.569 | 10.452 | 9.045 | 1.837 | -0.277 | 2.971%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 10.526 | 10.473 | 4 | 1.025 | -2.568 | 1.009 | -3.873 | 0.995 | -2.09 | 0.979 | -3.434 | -5.569 | 10.473 | 9.06 | 1.84 | -0.278 | 2.977%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 10.526 | 10.505 | 4 | 1.024 | -2.586 | 1.008 | -3.901 | 0.994 | -2.109 | 0.978 | -3.463 | -5.568 | 10.505 | 9.124 | 1.853 | -0.28 | 2.977%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 10.526 | 10.515 | 4 | 1.024 | -2.64 | 1.008 | -3.983 | 0.994 | -2.162 | 0.978 | -3.546 | -5.566 | 10.515 | 9.308 | 1.89 | -0.286 | 2.981%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.722 | 1.006 | -4.109 | 0.993 | -2.244 | 0.976 | -3.672 | -5.563 | 10.526 | 9.588 | 1.947 | -0.295 | 2.985%
18 | 10 | 2.031 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.022 | -2.755 | 1.005 | -4.16 | 0.992 | -2.277 | 0.975 | -3.724 | -5.561 | 10.526 | 9.702 | 1.97 | -0.298 | 2.98%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.022 | -2.745 | 1.006 | -4.145 | 0.992 | -2.267 | 0.976 | -3.709 | -5.562 | 10.526 | 9.669 | 1.963 | -0.297 | 2.98%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.023 | -2.714 | 1.006 | -4.097 | 0.993 | -2.236 | 0.976 | -3.661 | -5.563 | 10.526 | 9.563 | 1.942 | -0.294 | 2.983%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.024 | -2.647 | 1.007 | -3.995 | 0.994 | -2.17 | 0.977 | -3.557 | -5.565 | 10.526 | 9.333 | 1.895 | -0.287 | 2.983%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.512 | 1.01 | -3.787 | 0.995 | -2.035 | 0.98 | -3.348 | -5.571 | 10.526 | 8.867 | 1.801 | -0.272 | 2.976%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.013 | -3.533 | 0.987 | -1.711 | 0.973 | -2.946 | -7.359 | 10.526 | 8.209 | 1.667 | -0.338 | 3.955%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 10.526 | 10.526 | 4 | 1.029 | -2.206 | 1.015 | -3.319 | 0.989 | -1.572 | 0.975 | -2.73 | -7.365 | 10.526 | 7.73 | 1.57 | -0.317 | 3.939%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.974 | -2.38 | 0.974 | -2.38 | -5.263 | 5.263 | 7.388 | 1.5 | -0.328 | 4.251%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.975 | -2.293 | 0.975 | -2.293 | -5.263 | 5.263 | 7.198 | 1.462 | -0.319 | 4.244%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.975 | -2.246 | 0.975 | -2.246 | -5.263 | 5.263 | 7.093 | 1.44 | -0.314 | 4.239%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.975 | -2.242 | 0.975 | -2.242 | -5.263 | 5.263 | 7.084 | 1.439 | -0.314 | 4.244%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.974 | -2.313 | 0.974 | -2.313 | -5.263 | 5.263 | 7.242 | 1.47 | -0.321 | 4.244%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.972 | -2.497 | 0.972 | -2.497 | -5.263 | 5.263 | 7.645 | 1.552 | -0.341 | 4.27%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 5.263 | 5.252 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 5.252 | 8.265 | 1.678 | -0.361 | 4.185%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 5.263 | 5.116 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 5.116 | 8.698 | 1.766 | -0.361 | 3.985%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 5.263 | 4.705 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.705 | 4.705 | 8.821 | 1.791 | -0.36 | 3.921%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 5.263 | 4.142 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.976 | -3.185 | 0.976 | -3.185 | -4.142 | 4.142 | 8.922 | 1.812 | -0.308 | 3.337%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 5.263 | 3.574 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.98 | -3.311 | 0.98 | -3.311 | -3.574 | 3.574 | 8.993 | 1.826 | -0.268 | 2.894%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 5.263 | 3.258 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.983 | -3.373 | 0.983 | -3.373 | -3.258 | 3.258 | 9.048 | 1.837 | -0.244 | 2.626%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 5.263 | 3.353 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.982 | -3.371 | 0.982 | -3.371 | -3.353 | 3.353 | 9.069 | 1.842 | -0.253 | 2.714%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 5.263 | 3.505 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.98 | -3.354 | 0.98 | -3.354 | -3.505 | 3.505 | 9.073 | 1.842 | -0.265 | 2.838%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 5.263 | 3.942 | 5 | 1.008 | -3.901 | 1.008 | -3.901 | 0.977 | -3.286 | 0.977 | -3.286 | -3.942 | 3.942 | 9.106 | 1.849 | -0.298 | 3.169%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 5.263 | 4.458 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.458 | 4.458 | 9.237 | 1.876 | -0.357 | 3.721%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 5.263 | 4.921 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 4.921 | 9.529 | 1.935 | -0.354 | 3.582%
18 | 10 | 2.031 | 0.98 | I | very sunny | 5.263 | 5.189 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 5.189 | 9.647 | 1.959 | -0.353 | 3.53%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 5.263 | 5.258 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 5.258 | 9.613 | 1.952 | -0.353 | 3.542%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 5.263 | 9.502 | 1.93 | -0.355 | 3.602%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 5.263 | 9.263 | 1.881 | -0.357 | 3.711%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 5.263 | 8.779 | 1.783 | -0.36 | 3.939%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 5.263 | 8.186 | 1.662 | -0.361 | 4.224%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.972 | -2.524 | 0.972 | -2.524 | -5.263 | 5.263 | 7.703 | 1.564 | -0.344 | 4.275%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.974 | -2.38 | 0.974 | -2.38 | -5.263 | 5.263 | 7.388 | 1.5 | -0.328 | 4.251%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.975 | -2.293 | 0.975 | -2.293 | -5.263 | 5.263 | 7.198 | 1.462 | -0.319 | 4.244%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.975 | -2.246 | 0.975 | -2.246 | -5.263 | 5.263 | 7.093 | 1.44 | -0.314 | 4.239%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.975 | -2.242 | 0.975 | -2.242 | -5.263 | 5.263 | 7.084 | 1.439 | -0.314 | 4.244%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.974 | -2.313 | 0.974 | -2.313 | -5.263 | 5.263 | 7.242 | 1.47 | -0.321 | 4.244%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.972 | -2.497 | 0.972 | -2.497 | -5.263 | 5.263 | 7.645 | 1.552 | -0.341 | 4.27%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 5.263 | 8.265 | 1.678 | -0.361 | 4.185%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 5.263 | 5.258 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 5.258 | 8.698 | 1.766 | -0.361 | 3.985%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 5.263 | 5.205 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 5.205 | 8.821 | 1.791 | -0.36 | 3.921%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 5.263 | 5.095 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 5.095 | 8.87 | 1.801 | -0.36 | 3.9%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 5.263 | 4.979 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 4.979 | 8.901 | 1.807 | -0.36 | 3.887%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 5.263 | 4.916 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 4.916 | 8.932 | 1.814 | -0.36 | 3.874%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 5.263 | 4.984 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 4.984 | 8.962 | 1.82 | -0.36 | 3.862%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 5.263 | 5.016 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 5.016 | 8.979 | 1.823 | -0.359 | 3.845%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 5.263 | 5.147 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 5.147 | 9.045 | 1.837 | -0.359 | 3.818%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 5.263 | 5.237 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 5.237 | 9.237 | 1.876 | -0.357 | 3.721%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 5.263 | 9.529 | 1.935 | -0.354 | 3.582%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 5.263 | 9.647 | 1.959 | -0.353 | 3.53%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 5.263 | 9.613 | 1.952 | -0.353 | 3.542%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 5.263 | 9.502 | 1.93 | -0.355 | 3.602%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 5.263 | 9.263 | 1.881 | -0.357 | 3.711%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 5.263 | 8.779 | 1.783 | -0.36 | 3.939%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 5.263 | 8.186 | 1.662 | -0.361 | 4.224%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.972 | -2.524 | 0.972 | -2.524 | -5.263 | 5.263 | 7.703 | 1.564 | -0.344 | 4.275%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.974 | -2.38 | 0.974 | -2.38 | -5.263 | 5.263 | 7.388 | 1.5 | -0.328 | 4.251%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.975 | -2.293 | 0.975 | -2.293 | -5.263 | 5.263 | 7.198 | 1.462 | -0.319 | 4.244%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.975 | -2.246 | 0.975 | -2.246 | -5.263 | 5.263 | 7.093 | 1.44 | -0.314 | 4.239%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.975 | -2.242 | 0.975 | -2.242 | -5.263 | 5.263 | 7.084 | 1.439 | -0.314 | 4.244%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.974 | -2.313 | 0.974 | -2.313 | -5.263 | 5.263 | 7.242 | 1.47 | -0.321 | 4.244%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.972 | -2.497 | 0.972 | -2.497 | -5.263 | 5.263 | 7.645 | 1.552 | -0.341 | 4.27%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 5.263 | 8.265 | 1.678 | -0.361 | 4.185%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 5.263 | 8.698 | 1.766 | -0.361 | 3.985%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 5.263 | 8.821 | 1.791 | -0.36 | 3.921%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 5.263 | 5.258 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 5.258 | 8.87 | 1.801 | -0.36 | 3.9%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 5.263 | 5.242 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 5.242 | 8.901 | 1.807 | -0.36 | 3.887%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 5.263 | 5.226 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 5.226 | 8.932 | 1.814 | -0.36 | 3.874%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 5.263 | 5.226 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 5.226 | 8.962 | 1.82 | -0.36 | 3.862%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 5.263 | 5.237 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 5.237 | 8.979 | 1.823 | -0.359 | 3.845%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 5.263 | 5.252 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 5.252 | 9.045 | 1.837 | -0.359 | 3.818%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 5.263 | 5.258 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 5.258 | 9.237 | 1.876 | -0.357 | 3.721%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 5.263 | 9.529 | 1.935 | -0.354 | 3.582%
18 | 10 | 2.031 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 5.263 | 9.647 | 1.959 | -0.353 | 3.53%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 5.263 | 9.613 | 1.952 | -0.353 | 3.542%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 5.263 | 9.502 | 1.93 | -0.355 | 3.602%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 5.263 | 9.263 | 1.881 | -0.357 | 3.711%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 5.263 | 8.779 | 1.783 | -0.36 | 3.939%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 5.263 | 8.186 | 1.662 | -0.361 | 4.224%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 5.263 | 5.263 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.972 | -2.524 | 0.972 | -2.524 | -5.263 | 5.263 | 7.703 | 1.564 | -0.344 | 4.275%
1 | 7.716 | 1.567 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.33 | 0.97 | -2.33 | -5.654 | 10.526 | 7.361 | 1.495 | -0.355 | 4.601%
2 | 7.517 | 1.526 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.229 | 0.97 | -2.229 | -5.767 | 10.526 | 7.164 | 1.455 | -0.353 | 4.696%
3 | 7.407 | 1.504 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.173 | 0.97 | -2.173 | -5.829 | 10.526 | 7.056 | 1.433 | -0.351 | 4.739%
4 | 7.398 | 1.502 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -2.169 | 0.97 | -2.169 | -5.834 | 10.526 | 7.047 | 1.431 | -0.351 | 4.745%
5 | 7.563 | 1.536 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.252 | 0.97 | -2.252 | -5.741 | 10.526 | 7.209 | 1.464 | -0.354 | 4.681%
6 | 7.986 | 1.622 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.468 | 0.97 | -2.468 | -5.5 | 10.526 | 7.628 | 1.549 | -0.358 | 4.483%
7 | 8.626 | 1.752 | 0.98 | I | very sunny | 10.526 | 10.505 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 10.505 | 8.265 | 1.678 | -0.361 | 4.185%
8 | 9.059 | 1.84 | 0.98 | I | very sunny | 10.526 | 10.231 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 10.231 | 8.698 | 1.766 | -0.361 | 3.985%
9 | 9.181 | 1.864 | 0.98 | I | very sunny | 10.526 | 9.41 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 9.41 | 8.821 | 1.791 | -0.36 | 3.921%
10 | 9.23 | 1.874 | 0.98 | I | very sunny | 10.526 | 8.284 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 8.284 | 8.87 | 1.801 | -0.36 | 3.9%
11 | 9.261 | 1.881 | 0.98 | I | very sunny | 10.526 | 7.147 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 7.147 | 8.901 | 1.807 | -0.36 | 3.887%
12 | 9.292 | 1.887 | 0.98 | I | very sunny | 10.526 | 6.516 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 6.516 | 8.932 | 1.814 | -0.36 | 3.874%
13 | 9.322 | 1.893 | 0.98 | I | very sunny | 10.526 | 6.705 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 6.705 | 8.962 | 1.82 | -0.36 | 3.862%
14 | 9.338 | 1.896 | 0.98 | I | very sunny | 10.526 | 7.01 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 7.01 | 8.979 | 1.823 | -0.359 | 3.845%
15 | 9.404 | 1.91 | 0.98 | I | very sunny | 10.526 | 7.884 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 7.884 | 9.045 | 1.837 | -0.359 | 3.818%
16 | 9.594 | 1.948 | 0.98 | I | very sunny | 10.526 | 8.916 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 8.916 | 9.237 | 1.876 | -0.357 | 3.721%
17 | 9.883 | 2.007 | 0.98 | I | very sunny | 10.526 | 9.842 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 9.842 | 9.529 | 1.935 | -0.354 | 3.582%
18 | 10 | 2.031 | 0.98 | I | very sunny | 10.526 | 10.379 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 10.379 | 9.647 | 1.959 | -0.353 | 3.53%
19 | 9.966 | 2.024 | 0.98 | I | very sunny | 10.526 | 10.515 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 10.515 | 9.613 | 1.952 | -0.353 | 3.542%
20 | 9.857 | 2.002 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 10.526 | 9.502 | 1.93 | -0.355 | 3.602%
21 | 9.62 | 1.953 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 10.526 | 9.263 | 1.881 | -0.357 | 3.711%
22 | 9.139 | 1.856 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 10.526 | 8.779 | 1.783 | -0.36 | 3.939%
23 | 8.547 | 1.736 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 10.526 | 8.186 | 1.662 | -0.361 | 4.224%
24 | 8.047 | 1.634 | 0.98 | I | very sunny | 10.526 | 10.526 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.97 | -2.499 | 0.97 | -2.499 | -5.465 | 10.526 | 7.689 | 1.561 | -0.358 | 4.449%
1 | 7.716 | 1.567 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.33 | 0.97 | -2.33 | -5.654 | 10.526 | 7.361 | 1.495 | -0.355 | 4.601%
2 | 7.517 | 1.526 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.229 | 0.97 | -2.229 | -5.767 | 10.526 | 7.164 | 1.455 | -0.353 | 4.696%
3 | 7.407 | 1.504 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.173 | 0.97 | -2.173 | -5.829 | 10.526 | 7.056 | 1.433 | -0.351 | 4.739%
4 | 7.398 | 1.502 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -2.169 | 0.97 | -2.169 | -5.834 | 10.526 | 7.047 | 1.431 | -0.351 | 4.745%
5 | 7.563 | 1.536 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.252 | 0.97 | -2.252 | -5.741 | 10.526 | 7.209 | 1.464 | -0.354 | 4.681%
6 | 7.986 | 1.622 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.468 | 0.97 | -2.468 | -5.5 | 10.526 | 7.628 | 1.549 | -0.358 | 4.483%
7 | 8.626 | 1.752 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 10.526 | 8.265 | 1.678 | -0.361 | 4.185%
8 | 9.059 | 1.84 | 0.98 | I | moderate sun | 10.526 | 10.515 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 10.515 | 8.698 | 1.766 | -0.361 | 3.985%
9 | 9.181 | 1.864 | 0.98 | I | moderate sun | 10.526 | 10.41 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 10.41 | 8.821 | 1.791 | -0.36 | 3.921%
10 | 9.23 | 1.874 | 0.98 | I | moderate sun | 10.526 | 10.189 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 10.189 | 8.87 | 1.801 | -0.36 | 3.9%
11 | 9.261 | 1.881 | 0.98 | I | moderate sun | 10.526 | 9.958 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 9.958 | 8.901 | 1.807 | -0.36 | 3.887%
12 | 9.292 | 1.887 | 0.98 | I | moderate sun | 10.526 | 9.831 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 9.831 | 8.932 | 1.814 | -0.36 | 3.874%
13 | 9.322 | 1.893 | 0.98 | I | moderate sun | 10.526 | 9.968 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 9.968 | 8.962 | 1.82 | -0.36 | 3.862%
14 | 9.338 | 1.896 | 0.98 | I | moderate sun | 10.526 | 10.031 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 10.031 | 8.979 | 1.823 | -0.359 | 3.845%
15 | 9.404 | 1.91 | 0.98 | I | moderate sun | 10.526 | 10.294 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 10.294 | 9.045 | 1.837 | -0.359 | 3.818%
16 | 9.594 | 1.948 | 0.98 | I | moderate sun | 10.526 | 10.473 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 10.473 | 9.237 | 1.876 | -0.357 | 3.721%
17 | 9.883 | 2.007 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 10.526 | 9.529 | 1.935 | -0.354 | 3.582%
18 | 10 | 2.031 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 10.526 | 9.647 | 1.959 | -0.353 | 3.53%
19 | 9.966 | 2.024 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 10.526 | 9.613 | 1.952 | -0.353 | 3.542%
20 | 9.857 | 2.002 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 10.526 | 9.502 | 1.93 | -0.355 | 3.602%
21 | 9.62 | 1.953 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 10.526 | 9.263 | 1.881 | -0.357 | 3.711%
22 | 9.139 | 1.856 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 10.526 | 8.779 | 1.783 | -0.36 | 3.939%
23 | 8.547 | 1.736 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 10.526 | 8.186 | 1.662 | -0.361 | 4.224%
24 | 8.047 | 1.634 | 0.98 | I | moderate sun | 10.526 | 10.526 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.97 | -2.499 | 0.97 | -2.499 | -5.465 | 10.526 | 7.689 | 1.561 | -0.358 | 4.449%
1 | 7.716 | 1.567 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.017 | -3.179 | 1.017 | -3.179 | 0.97 | -2.33 | 0.97 | -2.33 | -5.654 | 10.526 | 7.361 | 1.495 | -0.355 | 4.601%
2 | 7.517 | 1.526 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.095 | 1.018 | -3.095 | 0.97 | -2.229 | 0.97 | -2.229 | -5.767 | 10.526 | 7.164 | 1.455 | -0.353 | 4.696%
3 | 7.407 | 1.504 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.048 | 1.018 | -3.048 | 0.97 | -2.173 | 0.97 | -2.173 | -5.829 | 10.526 | 7.056 | 1.433 | -0.351 | 4.739%
4 | 7.398 | 1.502 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.044 | 1.018 | -3.044 | 0.97 | -2.169 | 0.97 | -2.169 | -5.834 | 10.526 | 7.047 | 1.431 | -0.351 | 4.745%
5 | 7.563 | 1.536 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.018 | -3.114 | 1.018 | -3.114 | 0.97 | -2.252 | 0.97 | -2.252 | -5.741 | 10.526 | 7.209 | 1.464 | -0.354 | 4.681%
6 | 7.986 | 1.622 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.016 | -3.294 | 1.016 | -3.294 | 0.97 | -2.468 | 0.97 | -2.468 | -5.5 | 10.526 | 7.628 | 1.549 | -0.358 | 4.483%
7 | 8.626 | 1.752 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.012 | -3.567 | 1.012 | -3.567 | 0.97 | -2.796 | 0.97 | -2.796 | -5.129 | 10.526 | 8.265 | 1.678 | -0.361 | 4.185%
8 | 9.059 | 1.84 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.753 | 1.01 | -3.753 | 0.97 | -3.02 | 0.97 | -3.02 | -4.875 | 10.526 | 8.698 | 1.766 | -0.361 | 3.985%
9 | 9.181 | 1.864 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.805 | 1.01 | -3.805 | 0.97 | -3.083 | 0.97 | -3.083 | -4.803 | 10.526 | 8.821 | 1.791 | -0.36 | 3.921%
10 | 9.23 | 1.874 | 0.98 | I | cloudy | 10.526 | 10.515 | 5 | 1.009 | -3.826 | 1.009 | -3.826 | 0.97 | -3.109 | 0.97 | -3.109 | -4.774 | 10.515 | 8.87 | 1.801 | -0.36 | 3.9%
11 | 9.261 | 1.881 | 0.98 | I | cloudy | 10.526 | 10.484 | 5 | 1.009 | -3.84 | 1.009 | -3.84 | 0.97 | -3.125 | 0.97 | -3.125 | -4.756 | 10.484 | 8.901 | 1.807 | -0.36 | 3.887%
12 | 9.292 | 1.887 | 0.98 | I | cloudy | 10.526 | 10.452 | 5 | 1.009 | -3.853 | 1.009 | -3.853 | 0.97 | -3.141 | 0.97 | -3.141 | -4.737 | 10.452 | 8.932 | 1.814 | -0.36 | 3.874%
13 | 9.322 | 1.893 | 0.98 | I | cloudy | 10.526 | 10.452 | 5 | 1.009 | -3.866 | 1.009 | -3.866 | 0.97 | -3.157 | 0.97 | -3.157 | -4.719 | 10.452 | 8.962 | 1.82 | -0.36 | 3.862%
14 | 9.338 | 1.896 | 0.98 | I | cloudy | 10.526 | 10.473 | 5 | 1.009 | -3.873 | 1.009 | -3.873 | 0.97 | -3.165 | 0.97 | -3.165 | -4.71 | 10.473 | 8.979 | 1.823 | -0.359 | 3.845%
15 | 9.404 | 1.91 | 0.98 | I | cloudy | 10.526 | 10.505 | 5 | 1.009 | -3.901 | 1.009 | -3.901 | 0.97 | -3.2 | 0.97 | -3.2 | -4.67 | 10.505 | 9.045 | 1.837 | -0.359 | 3.818%
16 | 9.594 | 1.948 | 0.98 | I | cloudy | 10.526 | 10.515 | 5 | 1.008 | -3.983 | 1.008 | -3.983 | 0.97 | -3.299 | 0.97 | -3.299 | -4.557 | 10.515 | 9.237 | 1.876 | -0.357 | 3.721%
17 | 9.883 | 2.007 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.109 | 1.006 | -4.109 | 0.97 | -3.45 | 0.97 | -3.45 | -4.383 | 10.526 | 9.529 | 1.935 | -0.354 | 3.582%
18 | 10 | 2.031 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.005 | -4.16 | 1.005 | -4.16 | 0.97 | -3.512 | 0.97 | -3.512 | -4.312 | 10.526 | 9.647 | 1.959 | -0.353 | 3.53%
19 | 9.966 | 2.024 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.145 | 1.006 | -4.145 | 0.97 | -3.494 | 0.97 | -3.494 | -4.332 | 10.526 | 9.613 | 1.952 | -0.353 | 3.542%
20 | 9.857 | 2.002 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.006 | -4.097 | 1.006 | -4.097 | 0.97 | -3.436 | 0.97 | -3.436 | -4.398 | 10.526 | 9.502 | 1.93 | -0.355 | 3.602%
21 | 9.62 | 1.953 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.007 | -3.995 | 1.007 | -3.995 | 0.97 | -3.312 | 0.97 | -3.312 | -4.541 | 10.526 | 9.263 | 1.881 | -0.357 | 3.711%
22 | 9.139 | 1.856 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.01 | -3.787 | 1.01 | -3.787 | 0.97 | -3.062 | 0.97 | -3.062 | -4.828 | 10.526 | 8.779 | 1.783 | -0.36 | 3.939%
23 | 8.547 | 1.736 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.013 | -3.533 | 1.013 | -3.533 | 0.97 | -2.756 | 0.97 | -2.756 | -5.176 | 10.526 | 8.186 | 1.662 | -0.361 | 4.224%
24 | 8.047 | 1.634 | 0.98 | I | cloudy | 10.526 | 10.526 | 5 | 1.015 | -3.319 | 1.015 | -3.319 | 0.97 | -2.499 | 0.97 | -2.499 | -5.465 | 10.526 | 7.689 | 1.561 | -0.358 | 4.449%

## Residential ZIP Parameters
hour | load MW | load Mvar | PF | load type | sun rating | PV_size (MVA) | Q limit (MVar) | PV bus # | PV bus V pu (no CVR) | PV bus angle (no CVR) | Load bus (5) pu (no CVR) | Load bus (5) angle (no CVR) | PV bus V pu (CVR) | PV bus angle (CVR) | Load bus (5) pu (CVR) | Load bus (5) angle (CVR) | PV bus Q (MVar) | PV bus Q limit (MVar) | load MW CVR | load MVar CVR | MW reduction in P | % reduction in P
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0369 | -1.0325 | 0.99876 | -2.9186 | 1.0237 | -0.90306 | 0.98634 | -2.8137 | -5.263 | 5.263 | 7.6148 | 3.5573 | -0.10121 | -1.312%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0241 | -0.87646 | 0.98777 | -2.7344 | -5.263 | 5.263 | 7.4184 | 3.4661 | -0.098585 | -1.311%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0243 | -0.86177 | 0.98855 | -2.6906 | -5.263 | 5.263 | 7.3098 | 3.4155 | -0.097206 | -1.312%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0243 | -0.86057 | 0.98862 | -2.6871 | -5.263 | 5.263 | 7.3009 | 3.4114 | -0.097093 | -1.312%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.024 | -0.88261 | 0.98744 | -2.7527 | -5.263 | 5.263 | 7.4638 | 3.4872 | -0.09916 | -1.311%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0231 | -0.93925 | 0.98438 | -2.9217 | -5.263 | 5.263 | 7.8816 | 3.6816 | -0.10444 | -1.308%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2525 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0218 | -1.0256 | 0.97973 | -3.1798 | -5.2525 | 5.2525 | 8.5139 | 3.976 | -0.11211 | -1.3%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1156 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 5.1156 | 8.969 | 4.2242 | -0.090001 | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.7051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 4.7051 | 9.0898 | 4.2808 | -0.091187 | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.142 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 4.142 | 9.1383 | 4.3036 | -0.091662 | -0.9931% | -2.1779 | -0.010629
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5736 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0247 | -1.1577 | 0.97881 | -3.4856 | -3.5736 | 3.5736 | 9.1786 | 4.3353 | -0.082375 | -0.8895%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.2578 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0254 | -1.1683 | 0.97934 | -3.4995 | -3.2578 | 3.2578 | 9.217 | 4.3636 | -0.075031 | -0.8075%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.3525 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0251 | -1.1705 | 0.97889 | -3.5115 | -3.3525 | 3.3525 | 9.2445 | 4.3735 | -0.077549 | -0.8319%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5052 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0247 | -1.1696 | 0.9784 | -3.5175 | -3.5052 | 3.5052 | 9.2566 | 4.3743 | -0.081369 | -0.8714%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.942 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1698 | 0.97684 | -3.5431 | -3.942 | 3.942 | 9.3114 | 4.3858 | -0.09256 | -0.9843%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.4578 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 4.4578 | 9.4988 | 4.4725 | -0.095187 | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.9209 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 4.9209 | 9.785 | 4.6065 | -0.09798 | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1893 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 5.1893 | 9.9009 | 4.6607 | -0.09911 | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2577 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 5.2577 | 9.8672 | 4.645 | -0.098782 | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 5.263 | 9.7593 | 4.5944 | -0.097732 | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 5.263 | 9.5246 | 4.4845 | -0.09544 | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 5.263 | 9.0482 | 4.2613 | -0.09078 | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0219 | -1.0147 | 0.98028 | -3.1478 | -5.263 | 5.263 | 8.4356 | 3.9393 | -0.11137 | -1.303%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.023 | -0.94743 | 0.98394 | -2.9462 | -5.263 | 5.263 | 7.9418 | 3.7097 | -0.10519 | -1.307%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0236 | -0.90307 | 0.98633 | -2.8137 | -5.263 | 5.263 | 7.6149 | 3.5576 | -0.10107 | -1.31%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0241 | -0.87646 | 0.98777 | -2.7344 | -5.263 | 5.263 | 7.4184 | 3.4661 | -0.098585 | -1.311%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0243 | -0.86177 | 0.98855 | -2.6906 | -5.263 | 5.263 | 7.3098 | 3.4155 | -0.097206 | -1.312%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0243 | -0.86057 | 0.98862 | -2.6871 | -5.263 | 5.263 | 7.3009 | 3.4114 | -0.097093 | -1.312%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.024 | -0.88261 | 0.98744 | -2.7527 | -5.263 | 5.263 | 7.4638 | 3.4872 | -0.09916 | -1.311%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0231 | -0.93925 | 0.98438 | -2.9217 | -5.263 | 5.263 | 7.8816 | 3.6816 | -0.10444 | -1.308%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0218 | -1.0253 | 0.9797 | -3.1798 | -5.263 | 5.263 | 8.5137 | 3.9756 | -0.11235 | -1.302%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 5.2577 | 8.969 | 4.2242 | -0.090001 | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 5.2051 | 9.0898 | 4.2808 | -0.091187 | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 5.0946 | 9.1383 | 4.3036 | -0.091662 | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 4.9788 | 9.169 | 4.318 | -0.091965 | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 4.9156 | 9.1997 | 4.3324 | -0.092264 | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 4.9841 | 9.2294 | 4.3463 | -0.092556 | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 5.0156 | 9.2453 | 4.3537 | -0.09271 | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 5.1472 | 9.3106 | 4.3843 | -0.093351 | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 5.2367 | 9.4988 | 4.4725 | -0.095187 | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 5.263 | 9.785 | 4.6065 | -0.09798 | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 5.263 | 9.9009 | 4.6607 | -0.09911 | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 5.263 | 9.8672 | 4.645 | -0.098782 | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 5.263 | 9.7593 | 4.5944 | -0.097732 | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 5.263 | 9.5246 | 4.4845 | -0.09544 | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 5.263 | 9.0482 | 4.2613 | -0.09078 | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0219 | -1.0147 | 0.98028 | -3.1478 | -5.263 | 5.263 | 8.4356 | 3.9393 | -0.11137 | -1.303%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.023 | -0.94743 | 0.98394 | -2.9462 | -5.263 | 5.263 | 7.9418 | 3.7097 | -0.10519 | -1.307%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0236 | -0.90307 | 0.98633 | -2.8137 | -5.263 | 5.263 | 7.6149 | 3.5576 | -0.10107 | -1.31%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0241 | -0.87646 | 0.98777 | -2.7344 | -5.263 | 5.263 | 7.4184 | 3.4661 | -0.098585 | -1.311%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0243 | -0.86177 | 0.98855 | -2.6906 | -5.263 | 5.263 | 7.3098 | 3.4155 | -0.097206 | -1.312%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0243 | -0.86057 | 0.98862 | -2.6871 | -5.263 | 5.263 | 7.3009 | 3.4114 | -0.097093 | -1.312%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.024 | -0.88261 | 0.98744 | -2.7527 | -5.263 | 5.263 | 7.4638 | 3.4872 | -0.09916 | -1.311%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0231 | -0.93925 | 0.98438 | -2.9217 | -5.263 | 5.263 | 7.8816 | 3.6816 | -0.10444 | -1.308%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0218 | -1.0253 | 0.9797 | -3.1798 | -5.263 | 5.263 | 8.5137 | 3.9756 | -0.11235 | -1.302%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 5.263 | 8.969 | 4.2242 | -0.090001 | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 5.263 | 9.0898 | 4.2808 | -0.091187 | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 5.2577 | 9.1383 | 4.3036 | -0.091662 | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2419 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 5.2419 | 9.169 | 4.318 | -0.091965 | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 5.2262 | 9.1997 | 4.3324 | -0.092264 | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 5.2262 | 9.2294 | 4.3463 | -0.092556 | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2367 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 5.2367 | 9.2453 | 4.3537 | -0.09271 | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2525 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 5.2525 | 9.3106 | 4.3843 | -0.093351 | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 5.2577 | 9.4988 | 4.4725 | -0.095187 | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 5.263 | 9.785 | 4.6065 | -0.09798 | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 5.263 | 9.9009 | 4.6607 | -0.09911 | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 5.263 | 9.8672 | 4.645 | -0.098782 | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 5.263 | 9.7593 | 4.5944 | -0.097732 | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 5.263 | 9.5246 | 4.4845 | -0.09544 | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 5.263 | 9.0482 | 4.2613 | -0.09078 | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0219 | -1.0147 | 0.98028 | -3.1478 | -5.263 | 5.263 | 8.4356 | 3.9393 | -0.11137 | -1.303%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.023 | -0.94743 | 0.98394 | -2.9462 | -5.263 | 5.263 | 7.9418 | 3.7097 | -0.10519 | -1.307%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84817 | 0.97987 | -2.7949 | -7.8399 | 10.526 | 7.5623 | 3.4649 | -0.1537 | -1.992%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0103 | -0.75359 | 0.9747 | -2.661 | -10.526 | 10.526 | 7.315 | 3.2851 | -0.20199 | -2.687%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0105 | -0.73882 | 0.97547 | -2.6164 | -10.526 | 10.526 | 7.2079 | 3.2374 | -0.19914 | -2.689%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0105 | -0.73761 | 0.97554 | -2.6128 | -10.526 | 10.526 | 7.1991 | 3.2335 | -0.1989 | -2.689%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0102 | -0.75977 | 0.97437 | -2.6797 | -10.526 | 10.526 | 7.3598 | 3.3051 | -0.20319 | -2.687%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88453 | 0.97792 | -2.9046 | -7.8445 | 10.526 | 7.827 | 3.5852 | -0.15899 | -1.991%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5049 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97104 | 0.97324 | -3.1666 | -7.8559 | 10.5049 | 8.4545 | 3.8701 | -0.17149 | -1.988%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.2313 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 10.2313 | 8.969 | 4.2242 | -0.090001 | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 9.4102 | 9.0898 | 4.2808 | -0.091187 | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.284 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 8.284 | 9.1383 | 4.3036 | -0.091662 | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.1472 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 7.1472 | 9.169 | 4.318 | -0.091965 | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.5156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 6.5156 | 9.1997 | 4.3324 | -0.092264 | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.7051 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 6.7051 | 9.2294 | 4.3463 | -0.092556 | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.0103 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 7.0103 | 9.2453 | 4.3537 | -0.09271 | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.884 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 7.884 | 9.3106 | 4.3843 | -0.093351 | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.9155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 8.9155 | 9.4988 | 4.4725 | -0.095187 | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.8418 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 9.8418 | 9.785 | 4.6065 | -0.09798 | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.3786 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 10.3786 | 9.9009 | 4.6607 | -0.09911 | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5155 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 10.5155 | 9.8672 | 4.645 | -0.098782 | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 10.526 | 9.7593 | 4.5944 | -0.097732 | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 10.526 | 9.5246 | 4.4845 | -0.09544 | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 10.526 | 9.0482 | 4.2613 | -0.09078 | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96033 | 0.97382 | -3.1341 | -7.8546 | 10.526 | 8.377 | 3.8349 | -0.16995 | -1.988%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.89275 | 0.97747 | -2.9295 | -7.8456 | 10.526 | 7.8868 | 3.6124 | -0.16018 | -1.991%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84817 | 0.97987 | -2.7949 | -7.8399 | 10.526 | 7.5623 | 3.4649 | -0.1537 | -1.992%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0103 | -0.75359 | 0.9747 | -2.661 | -10.526 | 10.526 | 7.315 | 3.2851 | -0.20199 | -2.687%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0105 | -0.73882 | 0.97547 | -2.6164 | -10.526 | 10.526 | 7.2079 | 3.2374 | -0.19914 | -2.689%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0105 | -0.73761 | 0.97554 | -2.6128 | -10.526 | 10.526 | 7.1991 | 3.2335 | -0.1989 | -2.689%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0102 | -0.75977 | 0.97437 | -2.6797 | -10.526 | 10.526 | 7.3598 | 3.3051 | -0.20319 | -2.687%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88453 | 0.97792 | -2.9046 | -7.8445 | 10.526 | 7.827 | 3.5852 | -0.15899 | -1.991%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97104 | 0.97324 | -3.1666 | -7.8559 | 10.526 | 8.4545 | 3.8701 | -0.17149 | -1.988%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 10.5155 | 8.969 | 4.2242 | -0.090001 | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 10.4102 | 9.0898 | 4.2808 | -0.091187 | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 10.1892 | 9.1383 | 4.3036 | -0.091662 | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 9.9576 | 9.169 | 4.318 | -0.091965 | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 9.8313 | 9.1997 | 4.3324 | -0.092264 | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 9.9681 | 9.2294 | 4.3463 | -0.092556 | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 10.0313 | 9.2453 | 4.3537 | -0.09271 | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 10.2944 | 9.3106 | 4.3843 | -0.093351 | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 10.4734 | 9.4988 | 4.4725 | -0.095187 | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 10.526 | 9.785 | 4.6065 | -0.09798 | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 10.526 | 9.9009 | 4.6607 | -0.09911 | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 10.526 | 9.8672 | 4.645 | -0.098782 | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 10.526 | 9.7593 | 4.5944 | -0.097732 | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 10.526 | 9.5246 | 4.4845 | -0.09544 | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 10.526 | 9.0482 | 4.2613 | -0.09078 | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96033 | 0.97382 | -3.1341 | -7.8546 | 10.526 | 8.377 | 3.8349 | -0.16995 | -1.988%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.89275 | 0.97747 | -2.9295 | -7.8456 | 10.526 | 7.8868 | 3.6124 | -0.16018 | -1.991%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84817 | 0.97987 | -2.7949 | -7.8399 | 10.526 | 7.5623 | 3.4649 | -0.1537 | -1.992%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0103 | -0.75359 | 0.9747 | -2.661 | -10.526 | 10.526 | 7.315 | 3.2851 | -0.20199 | -2.687%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0105 | -0.73882 | 0.97547 | -2.6164 | -10.526 | 10.526 | 7.2079 | 3.2374 | -0.19914 | -2.689%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0105 | -0.73761 | 0.97554 | -2.6128 | -10.526 | 10.526 | 7.1991 | 3.2335 | -0.1989 | -2.689%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0102 | -0.75977 | 0.97437 | -2.6797 | -10.526 | 10.526 | 7.3598 | 3.3051 | -0.20319 | -2.687%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88453 | 0.97792 | -2.9046 | -7.8445 | 10.526 | 7.827 | 3.5852 | -0.15899 | -1.991%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97104 | 0.97324 | -3.1666 | -7.8559 | 10.526 | 8.4545 | 3.8701 | -0.17149 | -1.988%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1221 | 0.97936 | -3.4011 | -3.9711 | 10.526 | 8.969 | 4.2242 | -0.090001 | -0.9935%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1387 | 0.97844 | -3.4512 | -3.9723 | 10.526 | 9.0898 | 4.2808 | -0.091187 | -0.9932%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1454 | 0.97808 | -3.4713 | -3.9727 | 10.5155 | 9.1383 | 4.3036 | -0.091662 | -0.9931%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4839 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1496 | 0.97784 | -3.4841 | -3.9731 | 10.4839 | 9.169 | 4.318 | -0.091965 | -0.993%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1538 | 0.97761 | -3.4968 | -3.9733 | 10.4523 | 9.1997 | 4.3324 | -0.092264 | -0.9929%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1579 | 0.97738 | -3.5092 | -3.9736 | 10.4523 | 9.2294 | 4.3463 | -0.092556 | -0.9929%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4734 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.1601 | 0.97726 | -3.5158 | -3.9738 | 10.4734 | 9.2453 | 4.3537 | -0.09271 | -0.9928%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5049 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.1691 | 0.97676 | -3.543 | -3.9744 | 10.5049 | 9.3106 | 4.3843 | -0.093351 | -0.9927%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1951 | 0.97532 | -3.6216 | -3.9762 | 10.5155 | 9.4988 | 4.4725 | -0.095187 | -0.9922%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2347 | 0.97311 | -3.7416 | -3.979 | 10.526 | 9.785 | 4.6065 | -0.09798 | -0.9914%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2507 | 0.97221 | -3.7903 | -3.9802 | 10.526 | 9.9009 | 4.6607 | -0.09911 | -0.9911%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2461 | 0.97247 | -3.7761 | -3.9798 | 10.526 | 9.8672 | 4.645 | -0.098782 | -0.9912%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2311 | 0.97331 | -3.7307 | -3.9787 | 10.526 | 9.7593 | 4.5944 | -0.097732 | -0.9915%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1986 | 0.97512 | -3.6323 | -3.9764 | 10.526 | 9.5246 | 4.4845 | -0.09544 | -0.9921%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.133 | 0.97876 | -3.4339 | -3.9719 | 10.526 | 9.0482 | 4.2613 | -0.09078 | -0.9933%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96033 | 0.97382 | -3.1341 | -7.8546 | 10.526 | 8.377 | 3.8349 | -0.16995 | -1.988%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.89275 | 0.97747 | -2.9295 | -7.8456 | 10.526 | 7.8868 | 3.6124 | -0.16018 | -1.991%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 5.263 | 7.5579 | 3.4572 | -0.15809 | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99168 | -1.4701 | 0.97402 | -2.4415 | -5.263 | 5.263 | 7.3096 | 3.2758 | -0.20735 | -2.758%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99218 | -1.4415 | 0.9748 | -2.3975 | -5.263 | 5.263 | 7.2026 | 3.2283 | -0.20439 | -2.759%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99222 | -1.4392 | 0.97486 | -2.3939 | -5.263 | 5.263 | 7.1939 | 3.2244 | -0.20415 | -2.759%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99147 | -1.4821 | 0.97369 | -2.46 | -5.263 | 5.263 | 7.3544 | 3.2957 | -0.20859 | -2.758%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 5.263 | 7.8223 | 3.5769 | -0.16372 | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2525 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 5.2525 | 8.4489 | 3.8601 | -0.1771 | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1156 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 5.1156 | 8.9659 | 4.2186 | -0.093133 | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.7051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 4.7051 | 9.0866 | 4.275 | -0.094413 | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.142 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 4.142 | 9.1351 | 4.2977 | -0.094928 | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5736 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 3.5736 | 9.1657 | 4.312 | -0.095252 | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.2578 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 3.2578 | 9.1964 | 4.3263 | -0.095577 | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.3525 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 3.3525 | 9.2261 | 4.3402 | -0.095893 | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5052 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 3.5052 | 9.2419 | 4.3476 | -0.096062 | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.942 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 3.942 | 9.3072 | 4.3781 | -0.096754 | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.4578 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 4.4578 | 9.4953 | 4.466 | -0.098747 | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.9209 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 4.9209 | 9.7812 | 4.5995 | -0.10178 | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1893 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 5.1893 | 9.897 | 4.6536 | -0.10301 | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2577 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 5.2577 | 9.8633 | 4.6379 | -0.10266 | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 5.263 | 9.7555 | 4.5875 | -0.10151 | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 5.263 | 9.521 | 4.478 | -0.099021 | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 5.263 | 9.045 | 4.2556 | -0.093972 | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 5.263 | 8.3716 | 3.8252 | -0.17544 | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 5.263 | 7.882 | 3.6039 | -0.16499 | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 5.263 | 7.5579 | 3.4572 | -0.15809 | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99168 | -1.4701 | 0.97402 | -2.4415 | -5.263 | 5.263 | 7.3096 | 3.2758 | -0.20735 | -2.758%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99218 | -1.4415 | 0.9748 | -2.3975 | -5.263 | 5.263 | 7.2026 | 3.2283 | -0.20439 | -2.759%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99222 | -1.4392 | 0.97486 | -2.3939 | -5.263 | 5.263 | 7.1939 | 3.2244 | -0.20415 | -2.759%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99147 | -1.4821 | 0.97369 | -2.46 | -5.263 | 5.263 | 7.3544 | 3.2957 | -0.20859 | -2.758%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 5.263 | 7.8223 | 3.5769 | -0.16372 | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 5.263 | 8.4489 | 3.8601 | -0.1771 | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 5.2577 | 8.9659 | 4.2186 | -0.093133 | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 5.2051 | 9.0866 | 4.275 | -0.094413 | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 5.0946 | 9.1351 | 4.2977 | -0.094928 | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 4.9788 | 9.1657 | 4.312 | -0.095252 | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 4.9156 | 9.1964 | 4.3263 | -0.095577 | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 4.9841 | 9.2261 | 4.3402 | -0.095893 | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 5.0156 | 9.2419 | 4.3476 | -0.096062 | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 5.1472 | 9.3072 | 4.3781 | -0.096754 | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 5.2367 | 9.4953 | 4.466 | -0.098747 | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 5.263 | 9.7812 | 4.5995 | -0.10178 | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 5.263 | 9.897 | 4.6536 | -0.10301 | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 5.263 | 9.8633 | 4.6379 | -0.10266 | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 5.263 | 9.7555 | 4.5875 | -0.10151 | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 5.263 | 9.521 | 4.478 | -0.099021 | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 5.263 | 9.045 | 4.2556 | -0.093972 | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 5.263 | 8.3716 | 3.8252 | -0.17544 | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 5.263 | 7.882 | 3.6039 | -0.16499 | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 5.263 | 7.5579 | 3.4572 | -0.15809 | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99168 | -1.4701 | 0.97402 | -2.4415 | -5.263 | 5.263 | 7.3096 | 3.2758 | -0.20735 | -2.758%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99218 | -1.4415 | 0.9748 | -2.3975 | -5.263 | 5.263 | 7.2026 | 3.2283 | -0.20439 | -2.759%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99222 | -1.4392 | 0.97486 | -2.3939 | -5.263 | 5.263 | 7.1939 | 3.2244 | -0.20415 | -2.759%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99147 | -1.4821 | 0.97369 | -2.46 | -5.263 | 5.263 | 7.3544 | 3.2957 | -0.20859 | -2.758%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 5.263 | 7.8223 | 3.5769 | -0.16372 | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 5.263 | 8.4489 | 3.8601 | -0.1771 | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 5.263 | 8.9659 | 4.2186 | -0.093133 | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 5.263 | 9.0866 | 4.275 | -0.094413 | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 5.2577 | 9.1351 | 4.2977 | -0.094928 | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2419 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 5.2419 | 9.1657 | 4.312 | -0.095252 | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 5.2262 | 9.1964 | 4.3263 | -0.095577 | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 5.2262 | 9.2261 | 4.3402 | -0.095893 | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2367 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 5.2367 | 9.2419 | 4.3476 | -0.096062 | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2525 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 5.2525 | 9.3072 | 4.3781 | -0.096754 | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 5.2577 | 9.4953 | 4.466 | -0.098747 | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 5.263 | 9.7812 | 4.5995 | -0.10178 | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 5.263 | 9.897 | 4.6536 | -0.10301 | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 5.263 | 9.8633 | 4.6379 | -0.10266 | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 5.263 | 9.7555 | 4.5875 | -0.10151 | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 5.263 | 9.521 | 4.478 | -0.099021 | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 5.263 | 9.045 | 4.2556 | -0.093972 | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 5.263 | 8.3716 | 3.8252 | -0.17544 | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 5.263 | 7.882 | 3.6039 | -0.16499 | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 10.526 | 7.5579 | 3.4572 | -0.15809 | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.429 | 0.97106 | -2.4088 | -5.8247 | 10.526 | 7.2862 | 3.2351 | -0.23077 | -3.07%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4005 | 0.97185 | -2.3646 | -5.8215 | 10.526 | 7.1797 | 3.1885 | -0.22734 | -3.069%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.3982 | 0.97192 | -2.361 | -5.8213 | 10.526 | 7.1709 | 3.1847 | -0.22705 | -3.069%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4409 | 0.97073 | -2.4272 | -5.8258 | 10.526 | 7.3308 | 3.2546 | -0.23221 | -3.07%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 10.526 | 7.8223 | 3.5769 | -0.16372 | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5049 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 10.5049 | 8.4489 | 3.8601 | -0.1771 | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.2313 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 10.2313 | 8.9659 | 4.2186 | -0.093133 | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 9.4102 | 9.0866 | 4.275 | -0.094413 | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.284 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 8.284 | 9.1351 | 4.2977 | -0.094928 | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.1472 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 7.1472 | 9.1657 | 4.312 | -0.095252 | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.5156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 6.5156 | 9.1964 | 4.3263 | -0.095577 | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.7051 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 6.7051 | 9.2261 | 4.3402 | -0.095893 | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.0103 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 7.0103 | 9.2419 | 4.3476 | -0.096062 | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.884 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 7.884 | 9.3072 | 4.3781 | -0.096754 | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.9155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 8.9155 | 9.4953 | 4.466 | -0.098747 | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.8418 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 9.8418 | 9.7812 | 4.5995 | -0.10178 | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.3786 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 10.3786 | 9.897 | 4.6536 | -0.10301 | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5155 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 10.5155 | 9.8633 | 4.6379 | -0.10266 | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 10.526 | 9.7555 | 4.5875 | -0.10151 | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 10.526 | 9.521 | 4.478 | -0.099021 | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 10.526 | 9.045 | 4.2556 | -0.093972 | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 10.526 | 8.3716 | 3.8252 | -0.17544 | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 10.526 | 7.882 | 3.6039 | -0.16499 | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 10.526 | 7.5579 | 3.4572 | -0.15809 | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.429 | 0.97106 | -2.4088 | -5.8247 | 10.526 | 7.2862 | 3.2351 | -0.23077 | -3.07%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4005 | 0.97185 | -2.3646 | -5.8215 | 10.526 | 7.1797 | 3.1885 | -0.22734 | -3.069%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.3982 | 0.97192 | -2.361 | -5.8213 | 10.526 | 7.1709 | 3.1847 | -0.22705 | -3.069%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4409 | 0.97073 | -2.4272 | -5.8258 | 10.526 | 7.3308 | 3.2546 | -0.23221 | -3.07%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 10.526 | 7.8223 | 3.5769 | -0.16372 | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 10.526 | 8.4489 | 3.8601 | -0.1771 | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 10.5155 | 8.9659 | 4.2186 | -0.093133 | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 10.4102 | 9.0866 | 4.275 | -0.094413 | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 10.1892 | 9.1351 | 4.2977 | -0.094928 | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 9.9576 | 9.1657 | 4.312 | -0.095252 | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 9.8313 | 9.1964 | 4.3263 | -0.095577 | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 9.9681 | 9.2261 | 4.3402 | -0.095893 | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 10.0313 | 9.2419 | 4.3476 | -0.096062 | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 10.2944 | 9.3072 | 4.3781 | -0.096754 | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 10.4734 | 9.4953 | 4.466 | -0.098747 | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 10.526 | 9.7812 | 4.5995 | -0.10178 | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 10.526 | 9.897 | 4.6536 | -0.10301 | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 10.526 | 9.8633 | 4.6379 | -0.10266 | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 10.526 | 9.7555 | 4.5875 | -0.10151 | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 10.526 | 9.521 | 4.478 | -0.099021 | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 10.526 | 9.045 | 4.2556 | -0.093972 | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 10.526 | 8.3716 | 3.8252 | -0.17544 | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 10.526 | 7.882 | 3.6039 | -0.16499 | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6398 | 0.97933 | -2.6317 | -3.9271 | 10.526 | 7.5579 | 3.4572 | -0.15809 | -2.049%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.429 | 0.97106 | -2.4088 | -5.8247 | 10.526 | 7.2862 | 3.2351 | -0.23077 | -3.07%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4005 | 0.97185 | -2.3646 | -5.8215 | 10.526 | 7.1797 | 3.1885 | -0.22734 | -3.069%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.3982 | 0.97192 | -2.361 | -5.8213 | 10.526 | 7.1709 | 3.1847 | -0.22705 | -3.069%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4409 | 0.97073 | -2.4272 | -5.8258 | 10.526 | 7.3308 | 3.2546 | -0.23221 | -3.07%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7101 | 0.97736 | -2.7402 | -3.9321 | 10.526 | 7.8223 | 3.5769 | -0.16372 | -2.05%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8776 | 0.97263 | -2.9993 | -3.9446 | 10.526 | 8.4489 | 3.8601 | -0.1771 | -2.053%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1514 | 0.97904 | -3.3167 | -1.9971 | 10.526 | 8.9659 | 4.2186 | -0.093133 | -1.028%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1837 | 0.97812 | -3.3665 | -1.9984 | 10.526 | 9.0866 | 4.275 | -0.094413 | -1.028%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1967 | 0.97774 | -3.3865 | -1.999 | 10.5155 | 9.1351 | 4.2977 | -0.094928 | -1.028%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4839 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2049 | 0.97751 | -3.3992 | -1.9993 | 10.4839 | 9.1657 | 4.312 | -0.095252 | -1.029%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2131 | 0.97727 | -3.4119 | -1.9996 | 10.4523 | 9.1964 | 4.3263 | -0.095577 | -1.029%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2211 | 0.97704 | -3.4242 | -1.9999 | 10.4523 | 9.2261 | 4.3402 | -0.095893 | -1.029%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4734 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2253 | 0.97692 | -3.4308 | -2.0001 | 10.4734 | 9.2419 | 4.3476 | -0.096062 | -1.029%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5049 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2428 | 0.97642 | -3.4578 | -2.0008 | 10.5049 | 9.3072 | 4.3781 | -0.096754 | -1.029%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2934 | 0.97497 | -3.5359 | -2.0028 | 10.5155 | 9.4953 | 4.466 | -0.098747 | -1.029%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3704 | 0.97275 | -3.6553 | -2.0059 | 10.526 | 9.7812 | 4.5995 | -0.10178 | -1.03%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.4017 | 0.97184 | -3.7038 | -2.0072 | 10.526 | 9.897 | 4.6536 | -0.10301 | -1.03%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3926 | 0.97211 | -3.6897 | -2.0068 | 10.526 | 9.8633 | 4.6379 | -0.10266 | -1.03%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3635 | 0.97295 | -3.6445 | -2.0056 | 10.526 | 9.7555 | 4.5875 | -0.10151 | -1.03%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3003 | 0.97477 | -3.5467 | -2.003 | 10.526 | 9.521 | 4.478 | -0.099021 | -1.029%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1726 | 0.97843 | -3.3493 | -1.998 | 10.526 | 9.045 | 4.2556 | -0.093972 | -1.028%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8568 | 0.97322 | -2.9671 | -3.9431 | 10.526 | 8.3716 | 3.8252 | -0.17544 | -2.053%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.726 | 0.97691 | -2.7648 | -3.9334 | 10.526 | 7.882 | 3.6039 | -0.16499 | -2.05%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 5.263 | 7.4821 | 3.3248 | -0.23391 | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 5.263 | 7.2779 | 3.2206 | -0.23914 | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 5.263 | 7.1653 | 3.1636 | -0.24174 | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 5.263 | 7.1561 | 3.1589 | -0.24194 | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 5.263 | 7.325 | 3.2446 | -0.238 | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 5.263 | 7.7603 | 3.468 | -0.22573 | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2525 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 5.2525 | 8.4248 | 3.8173 | -0.20117 | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1156 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 5.1156 | 8.8787 | 4.0618 | -0.18034 | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.7051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 4.7051 | 9.0072 | 4.1319 | -0.17383 | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.142 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 4.142 | 9.0589 | 4.1602 | -0.17114 | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5736 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 3.5736 | 9.0916 | 4.1781 | -0.16942 | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.2578 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 3.2578 | 9.1243 | 4.1961 | -0.16767 | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.3525 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 3.3525 | 9.156 | 4.2136 | -0.16597 | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.5052 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 3.5052 | 9.1729 | 4.2229 | -0.16505 | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 5.263 | 3.942 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 3.942 | 9.2428 | 4.2614 | -0.16122 | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.4578 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 4.4578 | 9.4443 | 4.3734 | -0.14972 | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 5.263 | 4.9209 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 4.9209 | 9.7521 | 4.5463 | -0.13089 | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.1893 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 5.1893 | 9.8772 | 4.6173 | -0.1228 | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.2577 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 5.2577 | 9.8408 | 4.5966 | -0.12518 | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 5.263 | 9.7243 | 4.5306 | -0.13265 | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 5.263 | 9.4719 | 4.3888 | -0.1481 | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 5.263 | 8.9629 | 4.1077 | -0.1761 | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 5.263 | 8.3424 | 3.7735 | -0.2046 | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 5.263 | 7.8233 | 3.5007 | -0.2237 | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 5.263 | 7.4821 | 3.3248 | -0.23392 | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 5.263 | 7.2779 | 3.2206 | -0.23914 | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 5.263 | 7.1653 | 3.1636 | -0.24174 | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 5.263 | 7.1561 | 3.1589 | -0.24194 | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 5.263 | 7.325 | 3.2446 | -0.238 | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 5.263 | 7.7603 | 3.468 | -0.22573 | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 5.263 | 8.4248 | 3.8173 | -0.20117 | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 5.2577 | 8.8787 | 4.0618 | -0.18034 | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 5.2051 | 9.0072 | 4.1319 | -0.17383 | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 5.0946 | 9.0589 | 4.1602 | -0.17114 | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 4.9788 | 9.0916 | 4.1781 | -0.16942 | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 4.9156 | 9.1243 | 4.1961 | -0.16767 | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 4.9841 | 9.156 | 4.2136 | -0.16597 | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 5.0156 | 9.1729 | 4.2229 | -0.16505 | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 5.1472 | 9.2428 | 4.2614 | -0.16122 | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 5.2367 | 9.4443 | 4.3734 | -0.14972 | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 5.263 | 9.7521 | 4.5463 | -0.13089 | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 5.263 | 9.8772 | 4.6173 | -0.1228 | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 5.263 | 9.8408 | 4.5966 | -0.12518 | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 5.263 | 9.7243 | 4.5306 | -0.13265 | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 5.263 | 9.4719 | 4.3888 | -0.1481 | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 5.263 | 8.9629 | 4.1077 | -0.1761 | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 5.263 | 8.3424 | 3.7735 | -0.2046 | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 5.263 | 7.8233 | 3.5007 | -0.2237 | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 5.263 | 7.4821 | 3.3248 | -0.23392 | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 5.263 | 7.2779 | 3.2206 | -0.23914 | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 5.263 | 7.1653 | 3.1636 | -0.24174 | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 5.263 | 7.1561 | 3.1589 | -0.24194 | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 5.263 | 7.325 | 3.2446 | -0.238 | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 5.263 | 7.7603 | 3.468 | -0.22573 | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 5.263 | 8.4248 | 3.8173 | -0.20117 | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 5.263 | 8.8787 | 4.0618 | -0.18034 | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 5.263 | 9.0072 | 4.1319 | -0.17383 | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 5.2577 | 9.0589 | 4.1602 | -0.17114 | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2419 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 5.2419 | 9.0916 | 4.1781 | -0.16942 | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 5.2262 | 9.1243 | 4.1961 | -0.16767 | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 5.2262 | 9.156 | 4.2136 | -0.16597 | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2367 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 5.2367 | 9.1729 | 4.2229 | -0.16505 | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2525 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 5.2525 | 9.2428 | 4.2614 | -0.16122 | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 5.2577 | 9.4443 | 4.3734 | -0.14972 | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 5.263 | 9.7521 | 4.5463 | -0.13089 | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 5.263 | 9.8772 | 4.6173 | -0.1228 | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 5.263 | 9.8408 | 4.5966 | -0.12518 | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 5.263 | 9.7243 | 4.5306 | -0.13265 | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 5.263 | 9.4719 | 4.3888 | -0.1481 | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 5.263 | 8.9629 | 4.1077 | -0.1761 | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 5.263 | 8.3424 | 3.7735 | -0.2046 | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 5.263 | 7.8233 | 3.5007 | -0.2237 | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 10.526 | 7.4821 | 3.3248 | -0.23392 | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 10.526 | 7.2779 | 3.2206 | -0.23914 | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 10.526 | 7.1653 | 3.1636 | -0.24174 | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 10.526 | 7.1561 | 3.1589 | -0.24194 | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 10.526 | 7.325 | 3.2446 | -0.238 | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 10.526 | 7.7603 | 3.468 | -0.22573 | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5049 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 10.5049 | 8.4248 | 3.8173 | -0.20117 | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.2313 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 10.2313 | 8.8787 | 4.0618 | -0.18034 | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 9.4102 | 9.0072 | 4.1319 | -0.17383 | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.284 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 8.284 | 9.0589 | 4.1602 | -0.17114 | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.1472 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 7.1472 | 9.0916 | 4.1781 | -0.16942 | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.5156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 6.5156 | 9.1243 | 4.1961 | -0.16767 | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | very sunny | 10.526 | 6.7051 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 6.7051 | 9.156 | 4.2136 | -0.16597 | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.0103 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 7.0103 | 9.1729 | 4.2229 | -0.16505 | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | very sunny | 10.526 | 7.884 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 7.884 | 9.2428 | 4.2614 | -0.16122 | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | very sunny | 10.526 | 8.9155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 8.9155 | 9.4443 | 4.3734 | -0.14972 | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | very sunny | 10.526 | 9.8418 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 9.8418 | 9.7521 | 4.5463 | -0.13089 | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.3786 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 10.3786 | 9.8772 | 4.6173 | -0.1228 | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.5155 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 10.5155 | 9.8408 | 4.5966 | -0.12518 | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 10.526 | 9.7243 | 4.5306 | -0.13265 | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 10.526 | 9.4719 | 4.3888 | -0.1481 | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 10.526 | 8.9629 | 4.1077 | -0.1761 | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 10.526 | 8.3424 | 3.7735 | -0.2046 | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 10.526 | 7.8233 | 3.5007 | -0.2237 | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 10.526 | 7.4821 | 3.3248 | -0.23392 | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 10.526 | 7.2779 | 3.2206 | -0.23914 | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 10.526 | 7.1653 | 3.1636 | -0.24174 | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 10.526 | 7.1561 | 3.1589 | -0.24194 | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 10.526 | 7.325 | 3.2446 | -0.238 | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 10.526 | 7.7603 | 3.468 | -0.22573 | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 10.526 | 8.4248 | 3.8173 | -0.20117 | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 10.5155 | 8.8787 | 4.0618 | -0.18034 | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 10.4102 | 9.0072 | 4.1319 | -0.17383 | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 10.1892 | 9.0589 | 4.1602 | -0.17114 | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 9.9576 | 9.0916 | 4.1781 | -0.16942 | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 9.8313 | 9.1243 | 4.1961 | -0.16767 | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 9.9681 | 9.156 | 4.2136 | -0.16597 | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 10.0313 | 9.1729 | 4.2229 | -0.16505 | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 10.2944 | 9.2428 | 4.2614 | -0.16122 | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 10.4734 | 9.4443 | 4.3734 | -0.14972 | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 10.526 | 9.7521 | 4.5463 | -0.13089 | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 10.526 | 9.8772 | 4.6173 | -0.1228 | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 10.526 | 9.8408 | 4.5966 | -0.12518 | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 10.526 | 9.7243 | 4.5306 | -0.13265 | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 10.526 | 9.4719 | 4.3888 | -0.1481 | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 10.526 | 8.9629 | 4.1077 | -0.1761 | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 10.526 | 8.3424 | 3.7735 | -0.2046 | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 10.526 | 7.8233 | 3.5007 | -0.2237 | -2.78%
1 | 7.716 | 3.737 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.3926 | 0.97 | -2.3926 | -3.778 | 10.526 | 7.4821 | 3.3248 | -0.23392 | -3.032%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2875 | 0.97 | -2.2875 | -3.9581 | 10.526 | 7.2779 | 3.2206 | -0.23914 | -3.181%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.2296 | 0.97 | -2.2296 | -4.0569 | 10.526 | 7.1653 | 3.1636 | -0.24174 | -3.264%
4 | 7.398 | 3.583 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2248 | 0.97 | -2.2248 | -4.065 | 10.526 | 7.1561 | 3.1589 | -0.24194 | -3.27%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3118 | 0.97 | -2.3118 | -3.9167 | 10.526 | 7.325 | 3.2446 | -0.238 | -3.147%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.536 | 0.97 | -2.536 | -3.5304 | 10.526 | 7.7603 | 3.468 | -0.22573 | -2.827%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8789 | 0.97 | -2.8789 | -2.9288 | 10.526 | 8.4248 | 3.8173 | -0.20117 | -2.332%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1136 | 0.97 | -3.1136 | -2.5094 | 10.526 | 8.8787 | 4.0618 | -0.18034 | -1.991%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1801 | 0.97 | -3.1801 | -2.3894 | 10.526 | 9.0072 | 4.1319 | -0.17383 | -1.893%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2068 | 0.97 | -3.2068 | -2.341 | 10.5155 | 9.0589 | 4.1602 | -0.17114 | -1.854%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4839 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2238 | 0.97 | -3.2238 | -2.3102 | 10.4839 | 9.0916 | 4.1781 | -0.16942 | -1.829%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2407 | 0.97 | -3.2407 | -2.2795 | 10.4523 | 9.1243 | 4.1961 | -0.16767 | -1.804%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2572 | 0.97 | -3.2572 | -2.2496 | 10.4523 | 9.156 | 4.2136 | -0.16597 | -1.78%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.4734 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2659 | 0.97 | -3.2659 | -2.2337 | 10.4734 | 9.1729 | 4.2229 | -0.16505 | -1.768%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5049 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3021 | 0.97 | -3.3021 | -2.1678 | 10.5049 | 9.2428 | 4.2614 | -0.16122 | -1.714%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4065 | 0.97 | -3.4065 | -1.9768 | 10.5155 | 9.4443 | 4.3734 | -0.14972 | -1.561%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5662 | 0.97 | -3.5662 | -1.6821 | 10.526 | 9.7521 | 4.5463 | -0.13089 | -1.324%
18 | 10 | 4.8432 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6312 | 0.97 | -3.6312 | -1.5614 | 10.526 | 9.8772 | 4.6173 | -0.1228 | -1.228%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6123 | 0.97 | -3.6123 | -1.5966 | 10.526 | 9.8408 | 4.5966 | -0.12518 | -1.256%
20 | 9.857 | 4.774 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5518 | 0.97 | -3.5518 | -1.7088 | 10.526 | 9.7243 | 4.5306 | -0.13265 | -1.346%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4208 | 0.97 | -3.4208 | -1.9505 | 10.526 | 9.4719 | 4.3888 | -0.1481 | -1.539%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.1572 | 0.97 | -3.1572 | -2.4308 | 10.526 | 8.9629 | 4.1077 | -0.1761 | -1.927%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.8363 | 0.97 | -2.8363 | -3.0042 | 10.526 | 8.3424 | 3.7735 | -0.2046 | -2.394%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5685 | 0.97 | -2.5685 | -3.474 | 10.526 | 7.8233 | 3.5007 | -0.2237 | -2.78%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0268 | -0.9258 | 0.9961 | -2.9536 | -5.263 | 5.263 | 7.6133 | 2.4147 | -0.10274 | -1.331%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0271 | -0.89874 | 0.99726 | -2.8714 | -5.263 | 5.263 | 7.4169 | 2.3526 | -0.10013 | -1.332%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0273 | -0.8838 | 0.9979 | -2.826 | -5.263 | 5.263 | 7.3083 | 2.3183 | -0.098697 | -1.332%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0273 | -0.88258 | 0.99795 | -2.8223 | -5.263 | 5.263 | 7.2994 | 2.3155 | -0.098578 | -1.332%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0271 | -0.90499 | 0.99699 | -2.8904 | -5.263 | 5.263 | 7.4623 | 2.367 | -0.10072 | -1.332%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0264 | -0.96257 | 0.99452 | -3.0655 | -5.263 | 5.263 | 7.8798 | 2.4989 | -0.10621 | -1.33%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2525 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0255 | -1.0469 | 0.9909 | -3.3202 | -5.2525 | 5.2525 | 8.513 | 2.7002 | -0.11304 | -1.31%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1156 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0251 | -1.1093 | 0.98865 | -3.5035 | -5.1156 | 5.1156 | 8.9437 | 2.8391 | -0.11528 | -1.273%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.7051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.026 | -1.1358 | 0.98892 | -3.5611 | -4.7051 | 4.7051 | 9.074 | 2.8889 | -0.10702 | -1.166%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.142 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0273 | -1.1563 | 0.98999 | -3.5918 | -4.142 | 4.142 | 9.1357 | 2.9202 | -0.094298 | -1.022%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5736 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0286 | -1.1839 | 0.99088 | -3.6483 | -3.5736 | 3.5736 | 9.1769 | 2.9426 | -0.084109 | -0.9082%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.2578 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0293 | -1.1947 | 0.99148 | -3.663 | -3.2578 | 3.2578 | 9.2154 | 2.9617 | -0.076616 | -0.8245%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.3525 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0292 | -1.1872 | 0.99138 | -3.6411 | -3.3525 | 3.3525 | 9.2459 | 2.9722 | -0.076101 | -0.8164%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5052 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0288 | -1.1858 | 0.99091 | -3.6455 | -3.5052 | 3.5052 | 9.2581 | 2.9729 | -0.079887 | -0.8555%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.942 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0274 | -1.1961 | 0.98907 | -3.7072 | -3.942 | 3.942 | 9.3094 | 2.9767 | -0.094642 | -1.006%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.4578 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0259 | -1.1984 | 0.98703 | -3.7388 | -4.4578 | 4.4578 | 9.4885 | 3.0259 | -0.10548 | -1.099%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.9209 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0242 | -1.23 | 0.98403 | -3.8646 | -4.9209 | 4.9209 | 9.7616 | 3.1011 | -0.12144 | -1.229%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1893 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0233 | -1.2406 | 0.98262 | -3.9137 | -5.1893 | 5.1893 | 9.8699 | 3.1289 | -0.13007 | -1.301%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2577 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0232 | -1.2345 | 0.98266 | -3.899 | -5.2577 | 5.2577 | 9.8345 | 3.1161 | -0.13149 | -1.319%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0233 | -1.2193 | 0.98331 | -3.8525 | -5.263 | 5.263 | 9.7268 | 3.082 | -0.13025 | -1.321%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0237 | -1.1866 | 0.98476 | -3.7516 | -5.263 | 5.263 | 9.4928 | 3.0082 | -0.12723 | -1.323%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0245 | -1.1204 | 0.98767 | -3.548 | -5.263 | 5.263 | 9.0179 | 2.8584 | -0.12108 | -1.325%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0255 | -1.0392 | 0.99121 | -3.2994 | -5.263 | 5.263 | 8.4335 | 2.6739 | -0.11346 | -1.328%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0263 | -0.97089 | 0.99416 | -3.0909 | -5.263 | 5.263 | 7.94 | 2.518 | -0.107 | -1.33%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0268 | -0.9258 | 0.9961 | -2.9536 | -5.263 | 5.263 | 7.6133 | 2.4147 | -0.10271 | -1.331%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0271 | -0.89874 | 0.99726 | -2.8714 | -5.263 | 5.263 | 7.4169 | 2.3526 | -0.10013 | -1.332%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0273 | -0.8838 | 0.9979 | -2.826 | -5.263 | 5.263 | 7.3083 | 2.3183 | -0.098697 | -1.332%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0273 | -0.88258 | 0.99795 | -2.8223 | -5.263 | 5.263 | 7.2994 | 2.3155 | -0.098578 | -1.332%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0271 | -0.90499 | 0.99699 | -2.8904 | -5.263 | 5.263 | 7.4623 | 2.367 | -0.10072 | -1.332%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0264 | -0.96257 | 0.99452 | -3.0655 | -5.263 | 5.263 | 7.8798 | 2.4989 | -0.10621 | -1.33%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0254 | -1.05 | 0.99074 | -3.3324 | -5.263 | 5.263 | 8.5115 | 2.6985 | -0.11448 | -1.327%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0247 | -1.1095 | 0.98816 | -3.5143 | -5.2577 | 5.2577 | 8.9391 | 2.8336 | -0.11992 | -1.324%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0246 | -1.1274 | 0.98756 | -3.5661 | -5.2051 | 5.2051 | 9.0608 | 2.8732 | -0.12018 | -1.309%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0249 | -1.1333 | 0.98767 | -3.5757 | -5.0946 | 5.0946 | 9.1131 | 2.8932 | -0.11686 | -1.266%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0251 | -1.1403 | 0.98777 | -3.5905 | -4.9788 | 4.9788 | 9.1465 | 2.9062 | -0.11446 | -1.236%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0252 | -1.146 | 0.98774 | -3.6045 | -4.9156 | 4.9156 | 9.1787 | 2.9177 | -0.11331 | -1.219%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.025 | -1.1485 | 0.98739 | -3.6161 | -4.9841 | 4.9841 | 9.2067 | 2.9251 | -0.11531 | -1.237%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0249 | -1.15 | 0.98721 | -3.6224 | -5.0156 | 5.0156 | 9.2217 | 2.9292 | -0.11626 | -1.245%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0245 | -1.1559 | 0.98649 | -3.6482 | -5.1472 | 5.1472 | 9.2837 | 2.946 | -0.12025 | -1.279%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0239 | -1.1799 | 0.98512 | -3.727 | -5.2367 | 5.2367 | 9.4692 | 3.0026 | -0.1248 | -1.301%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0233 | -1.2229 | 0.98315 | -3.8635 | -5.263 | 5.263 | 9.7524 | 3.0901 | -0.13058 | -1.321%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.2391 | 0.98243 | -3.9135 | -5.263 | 5.263 | 9.8679 | 3.1265 | -0.13206 | -1.321%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0231 | -1.2344 | 0.98264 | -3.8989 | -5.263 | 5.263 | 9.8344 | 3.1159 | -0.13163 | -1.321%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0233 | -1.2193 | 0.98331 | -3.8525 | -5.263 | 5.263 | 9.7268 | 3.082 | -0.13025 | -1.321%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0237 | -1.1866 | 0.98476 | -3.7516 | -5.263 | 5.263 | 9.4928 | 3.0082 | -0.12723 | -1.323%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0245 | -1.1204 | 0.98767 | -3.548 | -5.263 | 5.263 | 9.0179 | 2.8584 | -0.12108 | -1.325%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0255 | -1.0392 | 0.99121 | -3.2994 | -5.263 | 5.263 | 8.4335 | 2.6739 | -0.11346 | -1.328%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0263 | -0.97089 | 0.99416 | -3.0909 | -5.263 | 5.263 | 7.94 | 2.518 | -0.107 | -1.33%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0268 | -0.9258 | 0.9961 | -2.9536 | -5.263 | 5.263 | 7.6133 | 2.4147 | -0.10271 | -1.331%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0271 | -0.89874 | 0.99726 | -2.8714 | -5.263 | 5.263 | 7.4169 | 2.3526 | -0.10013 | -1.332%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0273 | -0.8838 | 0.9979 | -2.826 | -5.263 | 5.263 | 7.3083 | 2.3183 | -0.098697 | -1.332%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0273 | -0.88258 | 0.99795 | -2.8223 | -5.263 | 5.263 | 7.2994 | 2.3155 | -0.098578 | -1.332%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0271 | -0.90499 | 0.99699 | -2.8904 | -5.263 | 5.263 | 7.4623 | 2.367 | -0.10072 | -1.332%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0264 | -0.96257 | 0.99452 | -3.0655 | -5.263 | 5.263 | 7.8798 | 2.4989 | -0.10621 | -1.33%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0254 | -1.05 | 0.99074 | -3.3324 | -5.263 | 5.263 | 8.5115 | 2.6985 | -0.11448 | -1.327%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0247 | -1.1094 | 0.98815 | -3.5143 | -5.263 | 5.263 | 8.939 | 2.8335 | -0.12005 | -1.325%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0245 | -1.1262 | 0.98742 | -3.5658 | -5.263 | 5.263 | 9.0594 | 2.8715 | -0.12161 | -1.325%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0244 | -1.133 | 0.98713 | -3.5865 | -5.2577 | 5.2577 | 9.1079 | 2.8869 | -0.12211 | -1.323%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2419 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0244 | -1.1376 | 0.98699 | -3.5997 | -5.2419 | 5.2419 | 9.1389 | 2.897 | -0.12211 | -1.319%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0244 | -1.1422 | 0.98684 | -3.6128 | -5.2262 | 5.2262 | 9.1699 | 2.9071 | -0.12211 | -1.314%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0243 | -1.1463 | 0.98666 | -3.6255 | -5.2262 | 5.2262 | 9.1995 | 2.9165 | -0.12249 | -1.314%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2367 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0243 | -1.1447 | 0.98667 | -3.619 | -5.2367 | 5.2367 | 9.2164 | 2.9228 | -0.12161 | -1.302%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2525 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0242 | -1.1534 | 0.98623 | -3.6466 | -5.2525 | 5.2525 | 9.2812 | 2.9429 | -0.12282 | -1.306%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0238 | -1.1831 | 0.98493 | -3.7406 | -5.2577 | 5.2577 | 9.4672 | 3.0003 | -0.12676 | -1.321%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0233 | -1.2229 | 0.98315 | -3.8635 | -5.263 | 5.263 | 9.7524 | 3.0901 | -0.13058 | -1.321%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.2391 | 0.98243 | -3.9135 | -5.263 | 5.263 | 9.8679 | 3.1265 | -0.13206 | -1.321%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0231 | -1.2344 | 0.98264 | -3.8989 | -5.263 | 5.263 | 9.8344 | 3.1159 | -0.13163 | -1.321%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0233 | -1.2193 | 0.98331 | -3.8525 | -5.263 | 5.263 | 9.7268 | 3.082 | -0.13025 | -1.321%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0237 | -1.1866 | 0.98476 | -3.7516 | -5.263 | 5.263 | 9.4928 | 3.0082 | -0.12723 | -1.323%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0245 | -1.1204 | 0.98767 | -3.548 | -5.263 | 5.263 | 9.0179 | 2.8584 | -0.12108 | -1.325%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0255 | -1.0392 | 0.99121 | -3.2994 | -5.263 | 5.263 | 8.4335 | 2.6739 | -0.11346 | -1.328%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0263 | -0.97089 | 0.99416 | -3.0909 | -5.263 | 5.263 | 7.94 | 2.518 | -0.107 | -1.33%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.013 | -0.80234 | 0.98272 | -2.8768 | -10.526 | 10.526 | 7.5055 | 2.2887 | -0.21055 | -2.729%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0133 | -0.77517 | 0.98386 | -2.7932 | -10.526 | 10.526 | 7.3118 | 2.2301 | -0.20519 | -2.73%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0135 | -0.76016 | 0.98449 | -2.747 | -10.526 | 10.526 | 7.2048 | 2.1977 | -0.20223 | -2.73%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0135 | -0.75894 | 0.98454 | -2.7433 | -10.526 | 10.526 | 7.196 | 2.1951 | -0.20198 | -2.73%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0132 | -0.78145 | 0.98359 | -2.8125 | -10.526 | 10.526 | 7.3566 | 2.2437 | -0.20643 | -2.729%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0126 | -0.83927 | 0.98116 | -2.9907 | -10.526 | 10.526 | 7.7682 | 2.3682 | -0.21781 | -2.727%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5049 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0116 | -0.92754 | 0.97748 | -3.2624 | -10.5049 | 10.5049 | 8.3915 | 2.5569 | -0.23449 | -2.718%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.2313 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0116 | -0.99302 | 0.97565 | -3.4488 | -10.2313 | 10.2313 | 8.8198 | 2.692 | -0.23923 | -2.641%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0136 | -1.0273 | 0.97707 | -3.5049 | -9.4102 | 9.4102 | 8.9594 | 2.7525 | -0.22164 | -2.414%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.284 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0166 | -1.058 | 0.97972 | -3.5309 | -8.284 | 8.284 | 9.0358 | 2.801 | -0.19417 | -2.104%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.1472 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0194 | -1.0979 | 0.98211 | -3.5907 | -7.1472 | 7.1472 | 9.0913 | 2.8402 | -0.16974 | -1.833%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.5156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.021 | -1.1153 | 0.98354 | -3.6068 | -6.5156 | 6.5156 | 9.1375 | 2.8685 | -0.15446 | -1.662%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.7051 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0206 | -1.1074 | 0.98315 | -3.5897 | -6.7051 | 6.7051 | 9.165 | 2.8752 | -0.157 | -1.684%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.0103 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0198 | -1.1023 | 0.98229 | -3.5917 | -7.0103 | 7.0103 | 9.1733 | 2.8713 | -0.16471 | -1.764%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.884 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1039 | 0.97954 | -3.6489 | -7.8127 | 7.884 | 9.2148 | 2.8636 | -0.18921 | -2.012%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.9155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1302 | 0.97839 | -3.7306 | -7.8146 | 8.9155 | 9.401 | 2.9209 | -0.19302 | -2.012%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.8418 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1703 | 0.97662 | -3.8552 | -7.8176 | 9.8418 | 9.6842 | 3.0081 | -0.19882 | -2.012%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.3786 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1866 | 0.97591 | -3.9059 | -7.8188 | 10.3786 | 9.7988 | 3.0433 | -0.20117 | -2.012%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5155 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1818 | 0.97611 | -3.8912 | -7.8185 | 10.5155 | 9.7655 | 3.0331 | -0.20048 | -2.012%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1667 | 0.97678 | -3.844 | -7.8173 | 10.526 | 9.6587 | 3.0002 | -0.1983 | -2.012%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1338 | 0.97823 | -3.7418 | -7.8148 | 10.526 | 9.4265 | 2.9288 | -0.19354 | -2.012%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0107 | -0.99778 | 0.9744 | -3.4817 | -10.526 | 10.526 | 8.8903 | 2.7068 | -0.24871 | -2.721%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0117 | -0.91623 | 0.97789 | -3.2286 | -10.526 | 10.526 | 8.3141 | 2.5331 | -0.23287 | -2.725%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0125 | -0.84762 | 0.9808 | -3.0165 | -10.526 | 10.526 | 7.8275 | 2.3861 | -0.21945 | -2.727%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.013 | -0.80234 | 0.98272 | -2.8768 | -10.526 | 10.526 | 7.5055 | 2.2887 | -0.21055 | -2.729%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0133 | -0.77517 | 0.98386 | -2.7932 | -10.526 | 10.526 | 7.3118 | 2.2301 | -0.20519 | -2.73%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0135 | -0.76016 | 0.98449 | -2.747 | -10.526 | 10.526 | 7.2048 | 2.1977 | -0.20223 | -2.73%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0135 | -0.75894 | 0.98454 | -2.7433 | -10.526 | 10.526 | 7.196 | 2.1951 | -0.20198 | -2.73%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0132 | -0.78145 | 0.98359 | -2.8125 | -10.526 | 10.526 | 7.3566 | 2.2437 | -0.20643 | -2.729%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0126 | -0.83927 | 0.98116 | -2.9907 | -10.526 | 10.526 | 7.7682 | 2.3682 | -0.21781 | -2.727%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0115 | -0.92709 | 0.97743 | -3.2623 | -10.526 | 10.526 | 8.391 | 2.5563 | -0.23498 | -2.724%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0109 | -0.98696 | 0.9749 | -3.4474 | -10.5155 | 10.5155 | 8.8127 | 2.6837 | -0.24631 | -2.719%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.011 | -1.006 | 0.97445 | -3.5003 | -10.4102 | 10.4102 | 8.9341 | 2.7226 | -0.24691 | -2.689%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0115 | -1.0175 | 0.97474 | -3.5223 | -10.1892 | 10.1892 | 8.9874 | 2.7436 | -0.24259 | -2.628%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.012 | -1.0267 | 0.97516 | -3.5366 | -9.9576 | 9.9576 | 9.0235 | 2.7597 | -0.23748 | -2.564%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0123 | -1.0336 | 0.97531 | -3.5505 | -9.8313 | 9.8313 | 9.057 | 2.7727 | -0.23503 | -2.529%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0119 | -1.0349 | 0.97477 | -3.5627 | -9.9681 | 9.9681 | 9.0827 | 2.7774 | -0.23928 | -2.567%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0947 | 0.97994 | -3.6206 | -7.8118 | 10.0313 | 9.1501 | 2.8437 | -0.18788 | -2.012%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1039 | 0.97954 | -3.6489 | -7.8127 | 10.2944 | 9.2148 | 2.8636 | -0.18921 | -2.012%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1302 | 0.97839 | -3.7306 | -7.8146 | 10.4734 | 9.401 | 2.9209 | -0.19302 | -2.012%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1703 | 0.97662 | -3.8552 | -7.8176 | 10.526 | 9.6842 | 3.0081 | -0.19882 | -2.012%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1866 | 0.97591 | -3.9059 | -7.8188 | 10.526 | 9.7988 | 3.0433 | -0.20117 | -2.012%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1818 | 0.97611 | -3.8912 | -7.8185 | 10.526 | 9.7655 | 3.0331 | -0.20048 | -2.012%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1667 | 0.97678 | -3.844 | -7.8173 | 10.526 | 9.6587 | 3.0002 | -0.1983 | -2.012%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1338 | 0.97823 | -3.7418 | -7.8148 | 10.526 | 9.4265 | 2.9288 | -0.19354 | -2.012%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0107 | -0.99778 | 0.9744 | -3.4817 | -10.526 | 10.526 | 8.8903 | 2.7068 | -0.24871 | -2.721%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0117 | -0.91623 | 0.97789 | -3.2286 | -10.526 | 10.526 | 8.3141 | 2.5331 | -0.23287 | -2.725%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0125 | -0.84762 | 0.9808 | -3.0165 | -10.526 | 10.526 | 7.8275 | 2.3861 | -0.21945 | -2.727%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.013 | -0.80234 | 0.98272 | -2.8768 | -10.526 | 10.526 | 7.5055 | 2.2887 | -0.21055 | -2.729%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0133 | -0.77517 | 0.98386 | -2.7932 | -10.526 | 10.526 | 7.3118 | 2.2301 | -0.20519 | -2.73%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0135 | -0.76016 | 0.98449 | -2.747 | -10.526 | 10.526 | 7.2048 | 2.1977 | -0.20223 | -2.73%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0135 | -0.75894 | 0.98454 | -2.7433 | -10.526 | 10.526 | 7.196 | 2.1951 | -0.20198 | -2.73%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0132 | -0.78145 | 0.98359 | -2.8125 | -10.526 | 10.526 | 7.3566 | 2.2437 | -0.20643 | -2.729%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0126 | -0.83927 | 0.98116 | -2.9907 | -10.526 | 10.526 | 7.7682 | 2.3682 | -0.21781 | -2.727%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0115 | -0.92709 | 0.97743 | -3.2623 | -10.526 | 10.526 | 8.391 | 2.5563 | -0.23498 | -2.724%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0108 | -0.98674 | 0.97488 | -3.4474 | -10.526 | 10.526 | 8.8124 | 2.6834 | -0.24657 | -2.722%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0106 | -1.0036 | 0.97415 | -3.4997 | -10.526 | 10.526 | 8.9312 | 2.7191 | -0.24983 | -2.721%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0106 | -1.0106 | 0.97389 | -3.5208 | -10.5155 | 10.5155 | 8.9791 | 2.7338 | -0.25088 | -2.718%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4839 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0106 | -1.0155 | 0.97379 | -3.5343 | -10.4839 | 10.4839 | 9.0101 | 2.7439 | -0.2509 | -2.709%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0107 | -1.0205 | 0.97368 | -3.5478 | -10.4523 | 10.4523 | 9.0411 | 2.7539 | -0.25091 | -2.7%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0106 | -1.0246 | 0.97351 | -3.5607 | -10.4523 | 10.4523 | 9.0703 | 2.7627 | -0.25171 | -2.7%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4734 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0947 | 0.97994 | -3.6206 | -7.8118 | 10.4734 | 9.1501 | 2.8437 | -0.18788 | -2.012%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5049 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1039 | 0.97954 | -3.6489 | -7.8127 | 10.5049 | 9.2148 | 2.8636 | -0.18921 | -2.012%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1302 | 0.97839 | -3.7306 | -7.8146 | 10.5155 | 9.401 | 2.9209 | -0.19302 | -2.012%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1703 | 0.97662 | -3.8552 | -7.8176 | 10.526 | 9.6842 | 3.0081 | -0.19882 | -2.012%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1866 | 0.97591 | -3.9059 | -7.8188 | 10.526 | 9.7988 | 3.0433 | -0.20117 | -2.012%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1818 | 0.97611 | -3.8912 | -7.8185 | 10.526 | 9.7655 | 3.0331 | -0.20048 | -2.012%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1667 | 0.97678 | -3.844 | -7.8173 | 10.526 | 9.6587 | 3.0002 | -0.1983 | -2.012%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1338 | 0.97823 | -3.7418 | -7.8148 | 10.526 | 9.4265 | 2.9288 | -0.19354 | -2.012%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0107 | -0.99778 | 0.9744 | -3.4817 | -10.526 | 10.526 | 8.8903 | 2.7068 | -0.24871 | -2.721%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0117 | -0.91623 | 0.97789 | -3.2286 | -10.526 | 10.526 | 8.3141 | 2.5331 | -0.23287 | -2.725%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0125 | -0.84762 | 0.9808 | -3.0165 | -10.526 | 10.526 | 7.8275 | 2.3861 | -0.21945 | -2.727%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99709 | -1.6035 | 0.98211 | -2.6571 | -5.263 | 5.263 | 7.5006 | 2.283 | -0.21545 | -2.792%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99783 | -1.5499 | 0.98325 | -2.5744 | -5.263 | 5.263 | 7.3071 | 2.2247 | -0.20992 | -2.793%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.99824 | -1.5204 | 0.98389 | -2.5288 | -5.263 | 5.263 | 7.2001 | 2.1924 | -0.20687 | -2.793%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99827 | -1.5179 | 0.98394 | -2.525 | -5.263 | 5.263 | 7.1914 | 2.1897 | -0.20661 | -2.793%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99766 | -1.5623 | 0.98299 | -2.5935 | -5.263 | 5.263 | 7.3518 | 2.2382 | -0.2112 | -2.793%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99608 | -1.6763 | 0.98054 | -2.7696 | -5.263 | 5.263 | 7.7631 | 2.3622 | -0.22295 | -2.792%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2525 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99371 | -1.8505 | 0.97685 | -3.0387 | -5.2525 | 5.2525 | 8.3858 | 2.5502 | -0.24018 | -2.784%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1156 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.9928 | -1.9782 | 0.97502 | -3.229 | -5.1156 | 5.1156 | 8.8138 | 2.685 | -0.24515 | -2.706%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.7051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99456 | -2.0408 | 0.9765 | -3.3029 | -4.7051 | 4.7051 | 8.9539 | 2.746 | -0.22714 | -2.474%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.142 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99743 | -2.0943 | 0.97923 | -3.3538 | -4.142 | 4.142 | 9.031 | 2.7953 | -0.19897 | -2.156%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5736 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 1.0001 | -2.168 | 0.98168 | -3.438 | -3.5736 | 3.5736 | 9.0871 | 2.8352 | -0.17393 | -1.878%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.2578 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 1.0016 | -2.1985 | 0.98315 | -3.4678 | -3.2578 | 3.2578 | 9.1337 | 2.8639 | -0.15827 | -1.703%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.3525 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 1.0012 | -2.1829 | 0.98275 | -3.4474 | -3.3525 | 3.3525 | 9.1611 | 2.8706 | -0.1609 | -1.726%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5052 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 1.0004 | -2.1745 | 0.98188 | -3.4428 | -3.5052 | 3.5052 | 9.1692 | 2.8664 | -0.16881 | -1.808%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.942 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9015 | 3.942 | 9.2103 | 2.8583 | -0.19366 | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.4578 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 4.4578 | 9.3963 | 2.9154 | -0.19767 | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.9209 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 4.9209 | 9.6792 | 3.0021 | -0.20378 | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1893 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 5.1893 | 9.7937 | 3.0372 | -0.20626 | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2577 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 5.2577 | 9.7605 | 3.027 | -0.20554 | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 5.263 | 9.6538 | 2.9943 | -0.20323 | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 5.263 | 9.4218 | 2.9232 | -0.19822 | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99169 | -1.9895 | 0.97376 | -3.2549 | -5.263 | 5.263 | 8.8841 | 2.6995 | -0.2549 | -2.789%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99396 | -1.8283 | 0.97726 | -3.0048 | -5.263 | 5.263 | 8.3085 | 2.5265 | -0.23851 | -2.791%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99585 | -1.6928 | 0.98019 | -2.7951 | -5.263 | 5.263 | 7.8224 | 2.3801 | -0.22464 | -2.792%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99709 | -1.6035 | 0.98211 | -2.6571 | -5.263 | 5.263 | 7.5005 | 2.283 | -0.21545 | -2.792%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99783 | -1.5499 | 0.98325 | -2.5744 | -5.263 | 5.263 | 7.3071 | 2.2247 | -0.20992 | -2.793%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.99824 | -1.5204 | 0.98389 | -2.5288 | -5.263 | 5.263 | 7.2001 | 2.1924 | -0.20687 | -2.793%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99827 | -1.5179 | 0.98394 | -2.525 | -5.263 | 5.263 | 7.1914 | 2.1897 | -0.20661 | -2.793%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99766 | -1.5623 | 0.98299 | -2.5935 | -5.263 | 5.263 | 7.3518 | 2.2382 | -0.2112 | -2.793%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99608 | -1.6763 | 0.98054 | -2.7696 | -5.263 | 5.263 | 7.7631 | 2.3622 | -0.22295 | -2.792%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99366 | -1.8497 | 0.9768 | -3.0381 | -5.263 | 5.263 | 8.3853 | 2.5496 | -0.2407 | -2.79%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99202 | -1.968 | 0.97426 | -3.2213 | -5.2577 | 5.2577 | 8.8066 | 2.6765 | -0.25242 | -2.786%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99184 | -2.0051 | 0.97382 | -3.2759 | -5.2051 | 5.2051 | 8.9279 | 2.7153 | -0.25306 | -2.756%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99225 | -2.0263 | 0.97412 | -3.3026 | -5.0946 | 5.0946 | 8.9814 | 2.7365 | -0.24864 | -2.694%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97996 | -3.4207 | -3.8997 | 4.9788 | 9.0704 | 2.8153 | -0.19064 | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 4.9156 | 9.1007 | 2.8246 | -0.1913 | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 4.9841 | 9.1301 | 2.8336 | -0.19193 | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 5.0156 | 9.1457 | 2.8384 | -0.19227 | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 5.1472 | 9.2103 | 2.8583 | -0.19366 | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 5.2367 | 9.3963 | 2.9154 | -0.19767 | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 5.263 | 9.6792 | 3.0021 | -0.20378 | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 5.263 | 9.7937 | 3.0372 | -0.20626 | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 5.263 | 9.7605 | 3.027 | -0.20554 | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 5.263 | 9.6538 | 2.9943 | -0.20323 | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 5.263 | 9.4218 | 2.9232 | -0.19822 | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99169 | -1.9895 | 0.97376 | -3.2549 | -5.263 | 5.263 | 8.8841 | 2.6995 | -0.2549 | -2.789%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99396 | -1.8283 | 0.97726 | -3.0048 | -5.263 | 5.263 | 8.3085 | 2.5265 | -0.23851 | -2.791%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99585 | -1.6928 | 0.98019 | -2.7951 | -5.263 | 5.263 | 7.8224 | 2.3801 | -0.22464 | -2.792%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99709 | -1.6035 | 0.98211 | -2.6571 | -5.263 | 5.263 | 7.5005 | 2.283 | -0.21545 | -2.792%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99783 | -1.5499 | 0.98325 | -2.5744 | -5.263 | 5.263 | 7.3071 | 2.2247 | -0.20992 | -2.793%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.99824 | -1.5204 | 0.98389 | -2.5288 | -5.263 | 5.263 | 7.2001 | 2.1924 | -0.20687 | -2.793%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99827 | -1.5179 | 0.98394 | -2.525 | -5.263 | 5.263 | 7.1914 | 2.1897 | -0.20661 | -2.793%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99766 | -1.5623 | 0.98299 | -2.5935 | -5.263 | 5.263 | 7.3518 | 2.2382 | -0.2112 | -2.793%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99608 | -1.6763 | 0.98054 | -2.7696 | -5.263 | 5.263 | 7.7631 | 2.3622 | -0.22295 | -2.792%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99366 | -1.8497 | 0.9768 | -3.0381 | -5.263 | 5.263 | 8.3853 | 2.5496 | -0.2407 | -2.79%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99199 | -1.9676 | 0.97423 | -3.221 | -5.263 | 5.263 | 8.8063 | 2.6761 | -0.25269 | -2.789%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99152 | -2.0009 | 0.97351 | -3.2728 | -5.263 | 5.263 | 8.9249 | 2.7118 | -0.25606 | -2.789%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99136 | -2.0147 | 0.97324 | -3.2939 | -5.2577 | 5.2577 | 8.9729 | 2.7264 | -0.25714 | -2.786%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2419 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97996 | -3.4207 | -3.8997 | 5.2419 | 9.0704 | 2.8153 | -0.19064 | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 5.2262 | 9.1007 | 2.8246 | -0.1913 | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 5.2262 | 9.1301 | 2.8336 | -0.19193 | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2367 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 5.2367 | 9.1457 | 2.8384 | -0.19227 | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2525 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 5.2525 | 9.2103 | 2.8583 | -0.19366 | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 5.2577 | 9.3963 | 2.9154 | -0.19767 | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 5.263 | 9.6792 | 3.0021 | -0.20378 | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 5.263 | 9.7937 | 3.0372 | -0.20626 | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 5.263 | 9.7605 | 3.027 | -0.20554 | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 5.263 | 9.6538 | 2.9943 | -0.20323 | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 5.263 | 9.4218 | 2.9232 | -0.19822 | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99169 | -1.9895 | 0.97376 | -3.2549 | -5.263 | 5.263 | 8.8841 | 2.6995 | -0.2549 | -2.789%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99396 | -1.8283 | 0.97726 | -3.0048 | -5.263 | 5.263 | 8.3085 | 2.5265 | -0.23851 | -2.791%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99585 | -1.6928 | 0.98019 | -2.7951 | -5.263 | 5.263 | 7.8224 | 2.3801 | -0.22464 | -2.792%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5665 | 0.97941 | -2.6273 | -5.7636 | 10.526 | 7.4788 | 2.2579 | -0.23715 | -3.073%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3539 | 0.97076 | -2.3995 | -7.6011 | 10.526 | 7.2093 | 2.1121 | -0.30771 | -4.094%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3245 | 0.9714 | -2.3536 | -7.5983 | 10.526 | 7.1039 | 2.0817 | -0.30312 | -4.092%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3221 | 0.97146 | -2.3499 | -7.5981 | 10.526 | 7.0953 | 2.0792 | -0.30274 | -4.092%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3663 | 0.9705 | -2.4188 | -7.6016 | 10.526 | 7.2534 | 2.1248 | -0.30963 | -4.094%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6393 | 0.97783 | -2.7401 | -5.7676 | 10.526 | 7.7404 | 2.3358 | -0.24562 | -3.076%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5049 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8124 | 0.97403 | -3.0091 | -5.7786 | 10.5049 | 8.3602 | 2.5202 | -0.26576 | -3.081%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.2313 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9302 | 0.97143 | -3.1926 | -5.7858 | 10.2313 | 8.7796 | 2.6447 | -0.27942 | -3.084%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9634 | 0.97069 | -3.2445 | -5.7879 | 9.4102 | 8.8977 | 2.6797 | -0.28327 | -3.085%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.284 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.9768 | 0.97039 | -3.2653 | -5.7887 | 8.284 | 8.9452 | 2.6938 | -0.28482 | -3.086%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.1472 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97997 | -3.4207 | -3.8996 | 7.1472 | 9.0704 | 2.8153 | -0.19064 | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.5156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 6.5156 | 9.1007 | 2.8246 | -0.1913 | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.7051 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 6.7051 | 9.1301 | 2.8336 | -0.19193 | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.0103 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 7.0103 | 9.1457 | 2.8384 | -0.19227 | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.884 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 7.884 | 9.2103 | 2.8583 | -0.19366 | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.9155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 8.9155 | 9.3963 | 2.9154 | -0.19767 | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.8418 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 9.8418 | 9.6792 | 3.0021 | -0.20378 | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.3786 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 10.3786 | 9.7937 | 3.0372 | -0.20626 | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5155 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 10.5155 | 9.7605 | 3.027 | -0.20554 | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 10.526 | 9.6538 | 2.9943 | -0.20323 | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 10.526 | 9.4218 | 2.9232 | -0.19822 | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.952 | 0.97094 | -3.2266 | -5.7873 | 10.526 | 8.8571 | 2.6677 | -0.28195 | -3.085%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.791 | 0.9745 | -2.9758 | -5.7772 | 10.526 | 8.2837 | 2.4975 | -0.26327 | -3.08%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6557 | 0.97747 | -2.7656 | -5.7689 | 10.526 | 7.7995 | 2.3534 | -0.24754 | -3.076%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5665 | 0.97941 | -2.6273 | -5.7635 | 10.526 | 7.4788 | 2.2579 | -0.23715 | -3.073%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3539 | 0.97076 | -2.3995 | -7.6011 | 10.526 | 7.2093 | 2.1121 | -0.30771 | -4.094%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3245 | 0.9714 | -2.3536 | -7.5983 | 10.526 | 7.1039 | 2.0817 | -0.30312 | -4.092%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3221 | 0.97146 | -2.3499 | -7.5981 | 10.526 | 7.0953 | 2.0792 | -0.30274 | -4.092%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3663 | 0.9705 | -2.4188 | -7.6016 | 10.526 | 7.2534 | 2.1248 | -0.30963 | -4.094%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6393 | 0.97783 | -2.7401 | -5.7676 | 10.526 | 7.7404 | 2.3358 | -0.24562 | -3.076%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8124 | 0.97403 | -3.0091 | -5.7786 | 10.526 | 8.3602 | 2.5202 | -0.26576 | -3.081%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9302 | 0.97143 | -3.1926 | -5.7858 | 10.5155 | 8.7796 | 2.6447 | -0.27942 | -3.084%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9634 | 0.97069 | -3.2445 | -5.7879 | 10.4102 | 8.8977 | 2.6797 | -0.28327 | -3.085%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.9768 | 0.97039 | -3.2653 | -5.7887 | 10.1892 | 8.9452 | 2.6938 | -0.28482 | -3.086%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97997 | -3.4207 | -3.8996 | 9.9576 | 9.0704 | 2.8153 | -0.19064 | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 9.8313 | 9.1007 | 2.8246 | -0.1913 | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 9.9681 | 9.1301 | 2.8336 | -0.19193 | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 10.0313 | 9.1457 | 2.8384 | -0.19227 | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 10.2944 | 9.2103 | 2.8583 | -0.19366 | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 10.4734 | 9.3963 | 2.9154 | -0.19767 | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 10.526 | 9.6792 | 3.0021 | -0.20378 | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 10.526 | 9.7937 | 3.0372 | -0.20626 | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 10.526 | 9.7605 | 3.027 | -0.20554 | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 10.526 | 9.6538 | 2.9943 | -0.20323 | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 10.526 | 9.4218 | 2.9232 | -0.19822 | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.952 | 0.97094 | -3.2266 | -5.7873 | 10.526 | 8.8571 | 2.6677 | -0.28195 | -3.085%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.791 | 0.9745 | -2.9758 | -5.7772 | 10.526 | 8.2837 | 2.4975 | -0.26327 | -3.08%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6557 | 0.97747 | -2.7656 | -5.7689 | 10.526 | 7.7995 | 2.3534 | -0.24754 | -3.076%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5665 | 0.97941 | -2.6273 | -5.7635 | 10.526 | 7.4788 | 2.2579 | -0.23715 | -3.073%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3539 | 0.97076 | -2.3995 | -7.6011 | 10.526 | 7.2093 | 2.1121 | -0.30771 | -4.094%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3245 | 0.9714 | -2.3536 | -7.5983 | 10.526 | 7.1039 | 2.0817 | -0.30312 | -4.092%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3221 | 0.97146 | -2.3499 | -7.5981 | 10.526 | 7.0953 | 2.0792 | -0.30274 | -4.092%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3663 | 0.9705 | -2.4188 | -7.6016 | 10.526 | 7.2534 | 2.1248 | -0.30963 | -4.094%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6393 | 0.97783 | -2.7401 | -5.7676 | 10.526 | 7.7404 | 2.3358 | -0.24562 | -3.076%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8124 | 0.97403 | -3.0091 | -5.7786 | 10.526 | 8.3602 | 2.5202 | -0.26576 | -3.081%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9302 | 0.97143 | -3.1926 | -5.7858 | 10.526 | 8.7796 | 2.6447 | -0.27942 | -3.084%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9634 | 0.97069 | -3.2445 | -5.7879 | 10.526 | 8.8977 | 2.6797 | -0.28327 | -3.085%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.98847 | -1.9768 | 0.97039 | -3.2653 | -5.7887 | 10.5155 | 8.9452 | 2.6938 | -0.28482 | -3.086%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4839 | 4 | 1.0184 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1451 | 0.97997 | -3.4207 | -3.8996 | 10.4839 | 9.0704 | 2.8153 | -0.19064 | -2.059%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1536 | 0.97978 | -3.4338 | -3.9002 | 10.4523 | 9.1007 | 2.8246 | -0.1913 | -2.059%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1618 | 0.97959 | -3.4465 | -3.9005 | 10.4523 | 9.1301 | 2.8336 | -0.19193 | -2.059%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4734 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1662 | 0.97949 | -3.4533 | -3.9007 | 10.4734 | 9.1457 | 2.8384 | -0.19227 | -2.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5049 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1843 | 0.97909 | -3.4814 | -3.9014 | 10.5049 | 9.2103 | 2.8583 | -0.19366 | -2.059%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2363 | 0.97793 | -3.5623 | -3.9037 | 10.5155 | 9.3963 | 2.9154 | -0.19767 | -2.06%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3157 | 0.97615 | -3.6857 | -3.9071 | 10.526 | 9.6792 | 3.0021 | -0.20378 | -2.062%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.3479 | 0.97542 | -3.7359 | -3.9085 | 10.526 | 9.7937 | 3.0372 | -0.20626 | -2.063%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3386 | 0.97563 | -3.7213 | -3.9081 | 10.526 | 9.7605 | 3.027 | -0.20554 | -2.062%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3086 | 0.97631 | -3.6746 | -3.9068 | 10.526 | 9.6538 | 2.9943 | -0.20323 | -2.062%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2435 | 0.97777 | -3.5734 | -3.904 | 10.526 | 9.4218 | 2.9232 | -0.19822 | -2.061%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.952 | 0.97094 | -3.2266 | -5.7873 | 10.526 | 8.8571 | 2.6677 | -0.28195 | -3.085%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.791 | 0.9745 | -2.9758 | -5.7772 | 10.526 | 8.2837 | 2.4975 | -0.26327 | -3.08%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6557 | 0.97747 | -2.7656 | -5.7689 | 10.526 | 7.7995 | 2.3534 | -0.24754 | -3.076%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0088 | -3.0638 | 1.0088 | -3.0638 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9616 | 5.263 | 7.4031 | 2.1706 | -0.31285 | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 5.263 | 7.2033 | 2.1052 | -0.3137 | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 5.263 | 7.0931 | 2.0693 | -0.31393 | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 5.263 | 7.0841 | 2.0664 | -0.31395 | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 5.263 | 7.2494 | 2.1203 | -0.31356 | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 5.263 | 7.6751 | 2.2603 | -0.31089 | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2525 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 5.2525 | 8.3238 | 2.4777 | -0.30218 | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1156 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 5.1156 | 8.766 | 2.6287 | -0.29301 | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.7051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 4.7051 | 8.8911 | 2.6719 | -0.28994 | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.142 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 4.142 | 8.9414 | 2.6893 | -0.28864 | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5736 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97213 | -3.1917 | 0.97213 | -3.1917 | -3.5736 | 3.5736 | 8.9939 | 2.7247 | -0.26707 | -2.884%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.2578 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97451 | -3.241 | 0.97451 | -3.241 | -3.2578 | 3.2578 | 9.0492 | 2.7634 | -0.24285 | -2.614%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.3525 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97355 | -3.2437 | 0.97355 | -3.2437 | -3.3525 | 3.3525 | 9.0707 | 2.7632 | -0.25127 | -2.695%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.5052 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97221 | -3.2337 | 0.97221 | -3.2337 | -3.5052 | 3.5052 | 9.074 | 2.7534 | -0.26396 | -2.827%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 5.263 | 3.942 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 3.942 | 9.1202 | 2.7514 | -0.28376 | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.4578 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 4.4578 | 9.3161 | 2.8199 | -0.27792 | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 5.263 | 4.9209 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 4.9209 | 9.615 | 2.9254 | -0.26801 | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.1893 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 5.1893 | 9.7364 | 2.9686 | -0.26364 | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.2577 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 5.2577 | 9.7011 | 2.956 | -0.26493 | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 5.263 | 9.588 | 2.9159 | -0.26895 | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 5.263 | 9.3429 | 2.8294 | -0.27708 | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 5.263 | 8.848 | 2.657 | -0.29102 | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 5.263 | 8.2434 | 2.4505 | -0.30356 | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 5.263 | 7.7367 | 2.2808 | -0.3103 | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 5.263 | 7.4031 | 2.1706 | -0.31287 | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 5.263 | 7.2033 | 2.1052 | -0.3137 | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 5.263 | 7.0931 | 2.0693 | -0.31393 | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 5.263 | 7.0841 | 2.0664 | -0.31395 | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 5.263 | 7.2494 | 2.1203 | -0.31356 | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 5.263 | 7.6751 | 2.2603 | -0.31089 | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 5.263 | 8.3238 | 2.4777 | -0.30218 | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 5.2577 | 8.766 | 2.6287 | -0.29301 | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 5.2051 | 8.8911 | 2.6719 | -0.28994 | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 5.0946 | 8.9414 | 2.6893 | -0.28864 | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 4.9788 | 8.9732 | 2.7003 | -0.2878 | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 4.9156 | 9.005 | 2.7114 | -0.28695 | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 4.9841 | 9.0359 | 2.7221 | -0.28612 | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 5.0156 | 9.0523 | 2.7278 | -0.28566 | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 5.1472 | 9.1202 | 2.7514 | -0.28376 | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 5.2367 | 9.3161 | 2.8199 | -0.27792 | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 5.263 | 9.615 | 2.9254 | -0.26801 | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 5.263 | 9.7364 | 2.9686 | -0.26364 | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 5.263 | 9.7011 | 2.956 | -0.26493 | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 5.263 | 9.588 | 2.9159 | -0.26895 | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 5.263 | 9.3429 | 2.8294 | -0.27708 | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 5.263 | 8.848 | 2.657 | -0.29102 | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 5.263 | 8.2434 | 2.4505 | -0.30356 | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 5.263 | 7.7367 | 2.2808 | -0.3103 | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 5.263 | 7.4031 | 2.1706 | -0.31287 | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 5.263 | 7.2033 | 2.1052 | -0.3137 | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 5.263 | 7.0931 | 2.0693 | -0.31393 | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 5.263 | 7.0841 | 2.0664 | -0.31395 | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 5.263 | 7.2494 | 2.1203 | -0.31356 | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 5.263 | 7.6751 | 2.2603 | -0.31089 | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 5.263 | 8.3238 | 2.4777 | -0.30218 | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 5.263 | 8.766 | 2.6287 | -0.29301 | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 5.263 | 8.8911 | 2.6719 | -0.28994 | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 5.2577 | 8.9414 | 2.6893 | -0.28864 | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2419 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 5.2419 | 8.9732 | 2.7003 | -0.2878 | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 5.2262 | 9.005 | 2.7114 | -0.28695 | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 5.2262 | 9.0359 | 2.7221 | -0.28612 | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2367 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 5.2367 | 9.0523 | 2.7278 | -0.28566 | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2525 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 5.2525 | 9.1202 | 2.7514 | -0.28376 | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 5.2577 | 9.3161 | 2.8199 | -0.27792 | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 5.263 | 9.615 | 2.9254 | -0.26801 | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 5.263 | 9.7364 | 2.9686 | -0.26364 | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 5.263 | 9.7011 | 2.956 | -0.26493 | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 5.263 | 9.588 | 2.9159 | -0.26895 | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 5.263 | 9.3429 | 2.8294 | -0.27708 | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 5.263 | 8.848 | 2.657 | -0.29102 | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 5.263 | 8.2434 | 2.4505 | -0.30356 | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 5.263 | 7.7367 | 2.2808 | -0.3103 | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 10.526 | 7.4031 | 2.1706 | -0.31287 | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 10.526 | 7.2033 | 2.1052 | -0.3137 | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 10.526 | 7.0931 | 2.0693 | -0.31393 | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 10.526 | 7.0841 | 2.0664 | -0.31395 | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 10.526 | 7.2494 | 2.1203 | -0.31356 | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 10.526 | 7.6751 | 2.2603 | -0.31089 | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5049 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 10.5049 | 8.3238 | 2.4777 | -0.30218 | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.2313 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 10.2313 | 8.766 | 2.6287 | -0.29301 | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 9.4102 | 8.8911 | 2.6719 | -0.28994 | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.284 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 8.284 | 8.9414 | 2.6893 | -0.28864 | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.1472 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 7.1472 | 8.9732 | 2.7003 | -0.2878 | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.5156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 6.5156 | 9.005 | 2.7114 | -0.28695 | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | very sunny | 10.526 | 6.7051 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 6.7051 | 9.0359 | 2.7221 | -0.28612 | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.0103 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 7.0103 | 9.0523 | 2.7278 | -0.28566 | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | very sunny | 10.526 | 7.884 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 7.884 | 9.1202 | 2.7514 | -0.28376 | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | very sunny | 10.526 | 8.9155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 8.9155 | 9.3161 | 2.8199 | -0.27792 | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | very sunny | 10.526 | 9.8418 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 9.8418 | 9.615 | 2.9254 | -0.26801 | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.3786 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 10.3786 | 9.7364 | 2.9686 | -0.26364 | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.5155 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 10.5155 | 9.7011 | 2.956 | -0.26493 | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 10.526 | 9.588 | 2.9159 | -0.26895 | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 10.526 | 9.3429 | 2.8294 | -0.27708 | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 10.526 | 8.848 | 2.657 | -0.29102 | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 10.526 | 8.2434 | 2.4505 | -0.30356 | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 10.526 | 7.7367 | 2.2808 | -0.3103 | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 10.526 | 7.4031 | 2.1706 | -0.31287 | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 10.526 | 7.2033 | 2.1052 | -0.3137 | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 10.526 | 7.0931 | 2.0693 | -0.31393 | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 10.526 | 7.0841 | 2.0664 | -0.31395 | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 10.526 | 7.2494 | 2.1203 | -0.31356 | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 10.526 | 7.6751 | 2.2603 | -0.31089 | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 10.526 | 8.3238 | 2.4777 | -0.30218 | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 10.5155 | 8.766 | 2.6287 | -0.29301 | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 10.4102 | 8.8911 | 2.6719 | -0.28994 | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 10.1892 | 8.9414 | 2.6893 | -0.28864 | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 9.9576 | 8.9732 | 2.7003 | -0.2878 | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 9.8313 | 9.005 | 2.7114 | -0.28695 | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 9.9681 | 9.0359 | 2.7221 | -0.28612 | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 10.0313 | 9.0523 | 2.7278 | -0.28566 | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 10.2944 | 9.1202 | 2.7514 | -0.28376 | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 10.4734 | 9.3161 | 2.8199 | -0.27792 | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 10.526 | 9.615 | 2.9254 | -0.26801 | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 10.526 | 9.7364 | 2.9686 | -0.26364 | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 10.526 | 9.7011 | 2.956 | -0.26493 | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 10.526 | 9.588 | 2.9159 | -0.26895 | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 10.526 | 9.3429 | 2.8294 | -0.27708 | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 10.526 | 8.848 | 2.657 | -0.29102 | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 10.526 | 8.2434 | 2.4505 | -0.30356 | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 10.526 | 7.7367 | 2.2808 | -0.3103 | -3.856%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.352 | 0.97 | -2.352 | -4.9617 | 10.526 | 7.4031 | 2.1706 | -0.31287 | -4.055%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2491 | 0.97 | -2.2491 | -5.1013 | 10.526 | 7.2033 | 2.1052 | -0.3137 | -4.173%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.1924 | 0.97 | -2.1924 | -5.178 | 10.526 | 7.0931 | 2.0693 | -0.31393 | -4.238%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.1878 | 0.97 | -2.1878 | -5.1842 | 10.526 | 7.0841 | 2.0664 | -0.31395 | -4.244%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2729 | 0.97 | -2.2729 | -5.0691 | 10.526 | 7.2494 | 2.1203 | -0.31356 | -4.146%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.492 | 0.97 | -2.492 | -4.7702 | 10.526 | 7.6751 | 2.2603 | -0.31089 | -3.893%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.8267 | 0.97 | -2.8267 | -4.3072 | 10.526 | 8.3238 | 2.4777 | -0.30218 | -3.503%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0552 | 0.97 | -3.0552 | -3.9862 | 10.526 | 8.766 | 2.6287 | -0.29301 | -3.234%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.1199 | 0.97 | -3.1199 | -3.8946 | 10.526 | 8.8911 | 2.6719 | -0.28994 | -3.158%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.146 | 0.97 | -3.146 | -3.8577 | 10.5155 | 8.9414 | 2.6893 | -0.28864 | -3.127%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4839 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1624 | 0.97 | -3.1624 | -3.8343 | 10.4839 | 8.9732 | 2.7003 | -0.2878 | -3.108%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1789 | 0.97 | -3.1789 | -3.8108 | 10.4523 | 9.005 | 2.7114 | -0.28695 | -3.088%
13 | 9.322 | 3.064 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.1949 | 0.97 | -3.1949 | -3.7881 | 10.4523 | 9.0359 | 2.7221 | -0.28612 | -3.069%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.4734 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2034 | 0.97 | -3.2034 | -3.776 | 10.4734 | 9.0523 | 2.7278 | -0.28566 | -3.059%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5049 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2386 | 0.97 | -3.2386 | -3.7259 | 10.5049 | 9.1202 | 2.7514 | -0.28376 | -3.017%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.34 | 0.97 | -3.34 | -3.5808 | 10.5155 | 9.3161 | 2.8199 | -0.27792 | -2.897%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.495 | 0.97 | -3.495 | -3.3575 | 10.526 | 9.615 | 2.9254 | -0.26801 | -2.712%
18 | 10 | 3.2868 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.558 | 0.97 | -3.558 | -3.2663 | 10.526 | 9.7364 | 2.9686 | -0.26364 | -2.636%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5397 | 0.97 | -3.5397 | -3.2928 | 10.526 | 9.7011 | 2.956 | -0.26493 | -2.658%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.481 | 0.97 | -3.481 | -3.3777 | 10.526 | 9.588 | 2.9159 | -0.26895 | -2.729%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3539 | 0.97 | -3.3539 | -3.5608 | 10.526 | 9.3429 | 2.8294 | -0.27708 | -2.88%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.0976 | 0.97 | -3.0976 | -3.9262 | 10.526 | 8.848 | 2.657 | -0.29102 | -3.184%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7852 | 0.97 | -2.7852 | -4.3651 | 10.526 | 8.2434 | 2.4505 | -0.30356 | -3.552%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5238 | 0.97 | -2.5238 | -4.7267 | 10.526 | 7.7367 | 2.2808 | -0.3103 | -3.856%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1789 | 1.0293 | -0.94449 | 1.0038 | -3.0651 | -5.263 | 5.263 | 7.612 | 1.4919 | -0.104 | -1.348%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0296 | -0.91705 | 1.0048 | -2.9806 | -5.263 | 5.263 | 7.4157 | 1.4536 | -0.10129 | -1.348%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.9019 | 1.0053 | -2.9339 | -5.263 | 5.263 | 7.3072 | 1.4324 | -0.099825 | -1.348%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90066 | 1.0053 | -2.9301 | -5.263 | 5.263 | 7.2983 | 1.4307 | -0.099706 | -1.348%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92339 | 1.0046 | -3.0001 | -5.263 | 5.263 | 7.4611 | 1.4625 | -0.10191 | -1.347%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.029 | -0.98178 | 1.0025 | -3.1801 | -5.263 | 5.263 | 7.8784 | 1.544 | -0.10755 | -1.347%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2525 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0283 | -1.0672 | 0.99962 | -3.4415 | -5.2525 | 5.2525 | 8.5114 | 1.6684 | -0.11459 | -1.328%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1156 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0281 | -1.1304 | 0.99786 | -3.6295 | -5.1156 | 5.1156 | 8.942 | 1.7543 | -0.11697 | -1.291%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.7051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.029 | -1.1572 | 0.99829 | -3.6887 | -4.7051 | 4.7051 | 9.0724 | 1.785 | -0.10861 | -1.183%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.142 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0304 | -1.1778 | 0.99944 | -3.7207 | -4.142 | 4.142 | 9.1343 | 1.8043 | -0.095735 | -1.037%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5736 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0317 | -1.2057 | 1.0004 | -3.7778 | -3.5736 | 3.5736 | 9.1756 | 1.8181 | -0.085401 | -0.9222%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.2578 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0324 | -1.2165 | 1.0011 | -3.7931 | -3.2578 | 3.2578 | 9.2142 | 1.8299 | -0.077797 | -0.8372%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.3525 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0323 | -1.209 | 1.001 | -3.7714 | -3.3525 | 3.3525 | 9.2448 | 1.8364 | -0.07725 | -0.8287%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5052 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0319 | -1.2075 | 1.0005 | -3.7758 | -3.5052 | 3.5052 | 9.2569 | 1.8368 | -0.081094 | -0.8684%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.942 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0307 | -1.2062 | 0.99911 | -3.7966 | -3.942 | 3.942 | 9.3117 | 1.842 | -0.092322 | -0.9817%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.4578 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0291 | -1.2204 | 0.99687 | -3.8707 | -4.4578 | 4.4578 | 9.4869 | 1.8696 | -0.10714 | -1.117%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.9209 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0275 | -1.2525 | 0.99416 | -3.9991 | -4.9209 | 4.9209 | 9.7595 | 1.9162 | -0.12347 | -1.249%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1893 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0266 | -1.2633 | 0.99287 | -4.0489 | -5.1893 | 5.1893 | 9.8677 | 1.9334 | -0.1323 | -1.323%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2577 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0265 | -1.2571 | 0.99286 | -4.0338 | -5.2577 | 5.2577 | 9.8323 | 1.9254 | -0.13373 | -1.342%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0266 | -1.2418 | 0.99339 | -3.9863 | -5.263 | 5.263 | 9.7246 | 1.9044 | -0.13243 | -1.344%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0269 | -1.2087 | 0.99457 | -3.8832 | -5.263 | 5.263 | 9.4907 | 1.8588 | -0.12929 | -1.344%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1417 | 0.99695 | -3.6749 | -5.263 | 5.263 | 9.0161 | 1.7662 | -0.1229 | -1.345%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0283 | -1.0594 | 0.99984 | -3.42 | -5.263 | 5.263 | 8.432 | 1.6521 | -0.11503 | -1.346%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99021 | 1.0023 | -3.2061 | -5.263 | 5.263 | 7.9386 | 1.5558 | -0.10837 | -1.347%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.9445 | 1.0038 | -3.0651 | -5.263 | 5.263 | 7.612 | 1.492 | -0.10395 | -1.347%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0296 | -0.91705 | 1.0048 | -2.9806 | -5.263 | 5.263 | 7.4157 | 1.4536 | -0.10129 | -1.348%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.9019 | 1.0053 | -2.9339 | -5.263 | 5.263 | 7.3072 | 1.4324 | -0.099825 | -1.348%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90066 | 1.0053 | -2.9301 | -5.263 | 5.263 | 7.2983 | 1.4307 | -0.099706 | -1.348%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92339 | 1.0046 | -3.0001 | -5.263 | 5.263 | 7.4611 | 1.4625 | -0.10191 | -1.347%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.029 | -0.98178 | 1.0025 | -3.1801 | -5.263 | 5.263 | 7.8784 | 1.544 | -0.10755 | -1.347%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0704 | 0.99946 | -3.454 | -5.263 | 5.263 | 8.5099 | 1.6674 | -0.11608 | -1.346%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0277 | -1.1306 | 0.99736 | -3.6404 | -5.2577 | 5.2577 | 8.9373 | 1.7509 | -0.12171 | -1.344%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0276 | -1.1487 | 0.99689 | -3.6934 | -5.2051 | 5.2051 | 9.059 | 1.7753 | -0.122 | -1.329%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0279 | -1.1546 | 0.99707 | -3.7034 | -5.0946 | 5.0946 | 9.1114 | 1.7877 | -0.11861 | -1.285%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0282 | -1.1617 | 0.99721 | -3.7187 | -4.9788 | 4.9788 | 9.1448 | 1.7957 | -0.11618 | -1.255%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0283 | -1.1675 | 0.99722 | -3.733 | -4.9156 | 4.9156 | 9.177 | 1.8028 | -0.11502 | -1.238%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0281 | -1.17 | 0.9969 | -3.7449 | -4.9841 | 4.9841 | 9.2049 | 1.8074 | -0.11706 | -1.256%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.028 | -1.1715 | 0.99674 | -3.7512 | -5.0156 | 5.0156 | 9.22 | 1.8099 | -0.11803 | -1.264%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0276 | -1.1775 | 0.99608 | -3.7776 | -5.1472 | 5.1472 | 9.2819 | 1.8203 | -0.1221 | -1.298%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0271 | -1.2018 | 0.99492 | -3.8582 | -5.2367 | 5.2367 | 9.4672 | 1.8553 | -0.12677 | -1.321%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0266 | -1.2454 | 0.99326 | -3.9976 | -5.263 | 5.263 | 9.7502 | 1.9094 | -0.13277 | -1.343%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0264 | -1.2618 | 0.99267 | -4.0486 | -5.263 | 5.263 | 9.8657 | 1.9319 | -0.13432 | -1.343%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.257 | 0.99284 | -4.0338 | -5.263 | 5.263 | 9.8321 | 1.9253 | -0.13387 | -1.343%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0266 | -1.2418 | 0.99339 | -3.9863 | -5.263 | 5.263 | 9.7246 | 1.9044 | -0.13243 | -1.344%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0269 | -1.2087 | 0.99457 | -3.8832 | -5.263 | 5.263 | 9.4907 | 1.8588 | -0.12929 | -1.344%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1417 | 0.99695 | -3.6749 | -5.263 | 5.263 | 9.0161 | 1.7662 | -0.1229 | -1.345%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0283 | -1.0594 | 0.99984 | -3.42 | -5.263 | 5.263 | 8.432 | 1.6521 | -0.11503 | -1.346%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99021 | 1.0023 | -3.2061 | -5.263 | 5.263 | 7.9386 | 1.5558 | -0.10837 | -1.347%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.9445 | 1.0038 | -3.0651 | -5.263 | 5.263 | 7.612 | 1.492 | -0.10395 | -1.347%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0296 | -0.91705 | 1.0048 | -2.9806 | -5.263 | 5.263 | 7.4157 | 1.4536 | -0.10129 | -1.348%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.9019 | 1.0053 | -2.9339 | -5.263 | 5.263 | 7.3072 | 1.4324 | -0.099825 | -1.348%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90066 | 1.0053 | -2.9301 | -5.263 | 5.263 | 7.2983 | 1.4307 | -0.099706 | -1.348%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92339 | 1.0046 | -3.0001 | -5.263 | 5.263 | 7.4611 | 1.4625 | -0.10191 | -1.347%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.029 | -0.98178 | 1.0025 | -3.1801 | -5.263 | 5.263 | 7.8784 | 1.544 | -0.10755 | -1.347%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0704 | 0.99946 | -3.454 | -5.263 | 5.263 | 8.5099 | 1.6674 | -0.11608 | -1.346%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1305 | 0.99734 | -3.6404 | -5.263 | 5.263 | 8.9372 | 1.7508 | -0.12184 | -1.345%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0275 | -1.1475 | 0.99674 | -3.6931 | -5.263 | 5.263 | 9.0575 | 1.7743 | -0.12346 | -1.345%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0274 | -1.1544 | 0.99651 | -3.7143 | -5.2577 | 5.2577 | 9.106 | 1.7838 | -0.12398 | -1.343%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2419 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0274 | -1.1591 | 0.9964 | -3.7278 | -5.2419 | 5.2419 | 9.137 | 1.79 | -0.12399 | -1.339%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0274 | -1.1637 | 0.99629 | -3.7413 | -5.2262 | 5.2262 | 9.168 | 1.7963 | -0.124 | -1.334%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0274 | -1.1679 | 0.99614 | -3.7542 | -5.2262 | 5.2262 | 9.1976 | 1.8021 | -0.12439 | -1.334%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2367 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0274 | -1.1662 | 0.99618 | -3.7476 | -5.2367 | 5.2367 | 9.2145 | 1.806 | -0.12346 | -1.322%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2525 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0273 | -1.175 | 0.99582 | -3.7759 | -5.2525 | 5.2525 | 9.2793 | 1.8184 | -0.12471 | -1.326%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.027 | -1.2052 | 0.99471 | -3.872 | -5.2577 | 5.2577 | 9.4652 | 1.8539 | -0.1288 | -1.343%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0266 | -1.2454 | 0.99326 | -3.9976 | -5.263 | 5.263 | 9.7502 | 1.9094 | -0.13277 | -1.343%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0264 | -1.2618 | 0.99267 | -4.0486 | -5.263 | 5.263 | 9.8657 | 1.9319 | -0.13432 | -1.343%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.257 | 0.99284 | -4.0338 | -5.263 | 5.263 | 9.8321 | 1.9253 | -0.13387 | -1.343%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0266 | -1.2418 | 0.99339 | -3.9863 | -5.263 | 5.263 | 9.7246 | 1.9044 | -0.13243 | -1.344%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0269 | -1.2087 | 0.99457 | -3.8832 | -5.263 | 5.263 | 9.4907 | 1.8588 | -0.12929 | -1.344%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1417 | 0.99695 | -3.6749 | -5.263 | 5.263 | 9.0161 | 1.7662 | -0.1229 | -1.345%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0283 | -1.0594 | 0.99984 | -3.42 | -5.263 | 5.263 | 8.432 | 1.6521 | -0.11503 | -1.346%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99021 | 1.0023 | -3.2061 | -5.263 | 5.263 | 7.9386 | 1.5558 | -0.10837 | -1.347%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.82044 | 0.99018 | -2.9845 | -10.526 | 10.526 | 7.5029 | 1.4143 | -0.21311 | -2.762%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0157 | -0.7929 | 0.99112 | -2.8986 | -10.526 | 10.526 | 7.3094 | 1.3781 | -0.20761 | -2.762%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0158 | -0.77769 | 0.99164 | -2.8513 | -10.526 | 10.526 | 7.2024 | 1.3581 | -0.20457 | -2.762%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.77645 | 0.99168 | -2.8474 | -10.526 | 10.526 | 7.1937 | 1.3565 | -0.20432 | -2.762%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0156 | -0.79927 | 0.99091 | -2.9185 | -10.526 | 10.526 | 7.3541 | 1.3865 | -0.20888 | -2.762%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0151 | -0.85786 | 0.9889 | -3.1012 | -10.526 | 10.526 | 7.7654 | 1.4635 | -0.22059 | -2.762%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5049 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0145 | -0.93958 | 0.98617 | -3.352 | -10.5049 | 10.5049 | 8.3907 | 1.5819 | -0.23533 | -2.728%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.2313 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0147 | -1.0062 | 0.98479 | -3.5444 | -10.2313 | 10.2313 | 8.8186 | 1.6654 | -0.24037 | -2.653%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0167 | -1.0433 | 0.98632 | -3.6111 | -9.4102 | 9.4102 | 8.9577 | 1.7022 | -0.22329 | -2.432%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.284 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0196 | -1.0789 | 0.98892 | -3.656 | -8.284 | 8.284 | 9.0328 | 1.7309 | -0.19717 | -2.136%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.1472 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0224 | -1.1191 | 0.9914 | -3.717 | -7.1472 | 7.1472 | 9.0886 | 1.755 | -0.17236 | -1.861%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.5156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.024 | -1.1367 | 0.99291 | -3.734 | -6.5156 | 6.5156 | 9.1351 | 1.7725 | -0.15685 | -1.688%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.7051 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0236 | -1.1287 | 0.99255 | -3.7168 | -6.7051 | 6.7051 | 9.1626 | 1.7767 | -0.1594 | -1.71%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.0103 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0228 | -1.1235 | 0.99169 | -3.7187 | -7.0103 | 7.0103 | 9.1708 | 1.7743 | -0.16723 | -1.791%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.884 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0204 | -1.1116 | 0.98914 | -3.7336 | -7.884 | 7.884 | 9.2137 | 1.7709 | -0.19032 | -2.024%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.9155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0175 | -1.1127 | 0.98557 | -3.7989 | -8.9155 | 8.9155 | 9.3735 | 1.7874 | -0.22051 | -2.298%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.8418 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0145 | -1.1369 | 0.98153 | -3.9342 | -9.8418 | 9.8418 | 9.6288 | 1.8213 | -0.25416 | -2.572%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.3786 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0129 | -1.142 | 0.97951 | -3.9839 | -10.3786 | 10.3786 | 9.7278 | 1.8317 | -0.27223 | -2.722%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5155 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0126 | -1.1343 | 0.97931 | -3.9683 | -10.5155 | 10.5155 | 9.6909 | 1.8228 | -0.27513 | -2.761%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0127 | -1.1188 | 0.97982 | -3.92 | -10.526 | 10.526 | 9.5846 | 1.8029 | -0.2724 | -2.764%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.013 | -1.0856 | 0.98099 | -3.8153 | -10.526 | 10.526 | 9.3542 | 1.76 | -0.26584 | -2.763%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -1.0183 | 0.98335 | -3.6037 | -10.526 | 10.526 | 8.8865 | 1.6728 | -0.25251 | -2.763%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0144 | -0.93579 | 0.98622 | -3.3449 | -10.526 | 10.526 | 8.3109 | 1.5654 | -0.23612 | -2.763%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.86632 | 0.98861 | -3.1276 | -10.526 | 10.526 | 7.8247 | 1.4745 | -0.22228 | -2.762%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.82044 | 0.99018 | -2.9845 | -10.526 | 10.526 | 7.5029 | 1.4143 | -0.21312 | -2.762%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0157 | -0.7929 | 0.99112 | -2.8986 | -10.526 | 10.526 | 7.3094 | 1.3781 | -0.20761 | -2.762%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0158 | -0.77769 | 0.99164 | -2.8513 | -10.526 | 10.526 | 7.2024 | 1.3581 | -0.20457 | -2.762%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.77645 | 0.99168 | -2.8474 | -10.526 | 10.526 | 7.1937 | 1.3565 | -0.20432 | -2.762%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0156 | -0.79927 | 0.99091 | -2.9185 | -10.526 | 10.526 | 7.3541 | 1.3865 | -0.20888 | -2.762%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0151 | -0.85786 | 0.9889 | -3.1012 | -10.526 | 10.526 | 7.7654 | 1.4635 | -0.22059 | -2.762%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0143 | -0.94678 | 0.98584 | -3.3793 | -10.526 | 10.526 | 8.3877 | 1.5797 | -0.23831 | -2.763%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0138 | -1.0074 | 0.98377 | -3.5687 | -10.5155 | 10.5155 | 8.809 | 1.6585 | -0.25003 | -2.76%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0139 | -1.0266 | 0.98346 | -3.6228 | -10.4102 | 10.4102 | 8.9303 | 1.6826 | -0.2507 | -2.731%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0146 | -1.031 | 0.98407 | -3.6194 | -10.1892 | 10.1892 | 8.9862 | 1.6973 | -0.24383 | -2.642%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0151 | -1.041 | 0.98452 | -3.6368 | -9.9576 | 9.9576 | 9.0221 | 1.7071 | -0.23886 | -2.579%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0154 | -1.0484 | 0.9847 | -3.6524 | -9.8313 | 9.8313 | 9.0555 | 1.7151 | -0.23649 | -2.545%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.015 | -1.0492 | 0.9842 | -3.6632 | -9.9681 | 9.9681 | 9.0813 | 1.7181 | -0.24068 | -2.582%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0148 | -1.0498 | 0.98396 | -3.6691 | -10.0313 | 10.0313 | 9.0953 | 1.7199 | -0.24268 | -2.599%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0141 | -1.0525 | 0.98295 | -3.6935 | -10.2944 | 10.2944 | 9.1529 | 1.7272 | -0.25106 | -2.67%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0133 | -1.0745 | 0.98156 | -3.7736 | -10.4734 | 10.4734 | 9.3333 | 1.7584 | -0.26073 | -2.718%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0127 | -1.1224 | 0.97969 | -3.9315 | -10.526 | 10.526 | 9.6099 | 1.8076 | -0.27312 | -2.764%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0125 | -1.1389 | 0.97911 | -3.9833 | -10.526 | 10.526 | 9.7236 | 1.8287 | -0.27637 | -2.764%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0126 | -1.1341 | 0.97928 | -3.9683 | -10.526 | 10.526 | 9.6906 | 1.8226 | -0.27542 | -2.764%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0127 | -1.1188 | 0.97982 | -3.92 | -10.526 | 10.526 | 9.5846 | 1.8029 | -0.2724 | -2.764%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.013 | -1.0856 | 0.98099 | -3.8153 | -10.526 | 10.526 | 9.3542 | 1.76 | -0.26584 | -2.763%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -1.0183 | 0.98335 | -3.6037 | -10.526 | 10.526 | 8.8865 | 1.6728 | -0.25251 | -2.763%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0144 | -0.93579 | 0.98622 | -3.3449 | -10.526 | 10.526 | 8.3109 | 1.5654 | -0.23612 | -2.763%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.86632 | 0.98861 | -3.1276 | -10.526 | 10.526 | 7.8247 | 1.4745 | -0.22228 | -2.762%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0154 | -0.82044 | 0.99018 | -2.9845 | -10.526 | 10.526 | 7.5029 | 1.4143 | -0.21312 | -2.762%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0157 | -0.7929 | 0.99112 | -2.8986 | -10.526 | 10.526 | 7.3094 | 1.3781 | -0.20761 | -2.762%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0158 | -0.77769 | 0.99164 | -2.8513 | -10.526 | 10.526 | 7.2024 | 1.3581 | -0.20457 | -2.762%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0158 | -0.77645 | 0.99168 | -2.8474 | -10.526 | 10.526 | 7.1937 | 1.3565 | -0.20432 | -2.762%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0156 | -0.79927 | 0.99091 | -2.9185 | -10.526 | 10.526 | 7.3541 | 1.3865 | -0.20888 | -2.762%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0151 | -0.85786 | 0.9889 | -3.1012 | -10.526 | 10.526 | 7.7654 | 1.4635 | -0.22059 | -2.762%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0143 | -0.94678 | 0.98584 | -3.3793 | -10.526 | 10.526 | 8.3877 | 1.5797 | -0.23831 | -2.763%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0137 | -1.0071 | 0.98374 | -3.5686 | -10.526 | 10.526 | 8.8087 | 1.6583 | -0.2503 | -2.763%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0136 | -1.0242 | 0.98315 | -3.6222 | -10.526 | 10.526 | 8.9273 | 1.6804 | -0.25367 | -2.763%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0136 | -1.0312 | 0.98294 | -3.6437 | -10.5155 | 10.5155 | 8.9752 | 1.6895 | -0.25476 | -2.76%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4839 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0136 | -1.0362 | 0.98287 | -3.6575 | -10.4839 | 10.4839 | 9.0062 | 1.6957 | -0.2548 | -2.751%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0136 | -1.0413 | 0.9828 | -3.6713 | -10.4523 | 10.4523 | 9.0372 | 1.7019 | -0.25484 | -2.743%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0136 | -1.0454 | 0.98266 | -3.6845 | -10.4523 | 10.4523 | 9.0663 | 1.7074 | -0.25566 | -2.743%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4734 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0137 | -1.039 | 0.98281 | -3.6618 | -10.4734 | 10.4734 | 9.0842 | 1.7119 | -0.25382 | -2.718%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5049 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0135 | -1.0473 | 0.98241 | -3.6901 | -10.5049 | 10.5049 | 9.1476 | 1.7233 | -0.2564 | -2.727%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0131 | -1.0822 | 0.98115 | -3.8039 | -10.5155 | 10.5155 | 9.3292 | 1.7555 | -0.26483 | -2.76%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0127 | -1.1224 | 0.97969 | -3.9315 | -10.526 | 10.526 | 9.6099 | 1.8076 | -0.27312 | -2.764%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0125 | -1.1389 | 0.97911 | -3.9833 | -10.526 | 10.526 | 9.7236 | 1.8287 | -0.27637 | -2.764%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0126 | -1.1341 | 0.97928 | -3.9683 | -10.526 | 10.526 | 9.6906 | 1.8226 | -0.27542 | -2.764%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0127 | -1.1188 | 0.97982 | -3.92 | -10.526 | 10.526 | 9.5846 | 1.8029 | -0.2724 | -2.764%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.013 | -1.0856 | 0.98099 | -3.8153 | -10.526 | 10.526 | 9.3542 | 1.76 | -0.26584 | -2.763%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0136 | -1.0183 | 0.98335 | -3.6037 | -10.526 | 10.526 | 8.8865 | 1.6728 | -0.25251 | -2.763%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0144 | -0.93579 | 0.98622 | -3.3449 | -10.526 | 10.526 | 8.3109 | 1.5654 | -0.23612 | -2.763%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.015 | -0.86632 | 0.98861 | -3.1276 | -10.526 | 10.526 | 7.8247 | 1.4745 | -0.22228 | -2.762%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0296 | -2.1143 | 1.0168 | -3.1788 | 1.0021 | -1.669 | 0.98964 | -2.7653 | -5.263 | 5.263 | 7.4985 | 1.4113 | -0.21748 | -2.819%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.614 | 0.99058 | -2.6804 | -5.263 | 5.263 | 7.3052 | 1.3752 | -0.21183 | -2.818%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5837 | 0.9911 | -2.6335 | -5.263 | 5.263 | 7.1983 | 1.3552 | -0.20871 | -2.818%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0031 | -1.5812 | 0.99114 | -2.6297 | -5.263 | 5.263 | 7.1895 | 1.3536 | -0.20845 | -2.818%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0026 | -1.6268 | 0.99036 | -2.7 | -5.263 | 5.263 | 7.3499 | 1.3835 | -0.21313 | -2.818%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0013 | -1.7438 | 0.98835 | -2.8808 | -5.263 | 5.263 | 7.7609 | 1.4602 | -0.22515 | -2.819%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2525 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99957 | -1.9059 | 0.98562 | -3.1296 | -5.2525 | 5.2525 | 8.3857 | 1.5783 | -0.24029 | -2.786%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1156 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99896 | -2.0375 | 0.98425 | -3.3261 | -5.1156 | 5.1156 | 8.8135 | 1.6617 | -0.24551 | -2.71%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.7051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 1.0008 | -2.1066 | 0.98582 | -3.4104 | -4.7051 | 4.7051 | 8.9529 | 1.6988 | -0.22807 | -2.484%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.142 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 1.0036 | -2.1713 | 0.98848 | -3.4799 | -4.142 | 4.142 | 9.0286 | 1.7278 | -0.2014 | -2.182%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5736 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 1.0063 | -2.2455 | 0.99102 | -3.5648 | -3.5736 | 3.5736 | 9.085 | 1.7524 | -0.17602 | -1.901%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.2578 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 1.0079 | -2.2766 | 0.99256 | -3.5956 | -3.2578 | 3.2578 | 9.1318 | 1.7701 | -0.16018 | -1.724%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.3525 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 1.0075 | -2.2608 | 0.9922 | -3.575 | -3.3525 | 3.3525 | 9.1592 | 1.7743 | -0.1628 | -1.746%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5052 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 1.0066 | -2.2524 | 0.99133 | -3.5702 | -3.5052 | 3.5052 | 9.1672 | 1.7717 | -0.1708 | -1.829%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.942 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 1.0041 | -2.2341 | 0.98872 | -3.5658 | -3.942 | 3.942 | 9.2096 | 1.7679 | -0.19442 | -2.067%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.4578 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 1.0008 | -2.2426 | 0.9851 | -3.6075 | -4.4578 | 4.4578 | 9.3687 | 1.7839 | -0.22529 | -2.348%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.9209 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.9972 | -2.2977 | 0.98098 | -3.7203 | -4.9209 | 4.9209 | 9.6232 | 1.8172 | -0.25977 | -2.628%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1893 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99534 | -2.3115 | 0.97893 | -3.7572 | -5.1893 | 5.1893 | 9.7217 | 1.8274 | -0.27827 | -2.783%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2577 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99507 | -2.2971 | 0.97872 | -3.7387 | -5.2577 | 5.2577 | 9.6848 | 1.8184 | -0.28123 | -2.822%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.9954 | -2.266 | 0.97924 | -3.6907 | -5.263 | 5.263 | 9.5786 | 1.7985 | -0.27842 | -2.825%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99616 | -2.1994 | 0.98042 | -3.5871 | -5.263 | 5.263 | 9.3483 | 1.7558 | -0.27166 | -2.824%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99769 | -2.0647 | 0.98278 | -3.3778 | -5.263 | 5.263 | 8.881 | 1.6689 | -0.25795 | -2.823%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99955 | -1.8996 | 0.98566 | -3.1218 | -5.263 | 5.263 | 8.3059 | 1.5618 | -0.2411 | -2.821%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0011 | -1.7607 | 0.98806 | -2.9069 | -5.263 | 5.263 | 7.8201 | 1.4713 | -0.22688 | -2.819%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0021 | -1.669 | 0.98964 | -2.7653 | -5.263 | 5.263 | 7.4985 | 1.4113 | -0.21748 | -2.819%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.614 | 0.99058 | -2.6804 | -5.263 | 5.263 | 7.3052 | 1.3752 | -0.21183 | -2.818%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5837 | 0.9911 | -2.6335 | -5.263 | 5.263 | 7.1983 | 1.3552 | -0.20871 | -2.818%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0031 | -1.5812 | 0.99114 | -2.6297 | -5.263 | 5.263 | 7.1895 | 1.3536 | -0.20845 | -2.818%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0026 | -1.6268 | 0.99036 | -2.7 | -5.263 | 5.263 | 7.3499 | 1.3835 | -0.21313 | -2.818%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0013 | -1.7438 | 0.98835 | -2.8808 | -5.263 | 5.263 | 7.7609 | 1.4602 | -0.22515 | -2.819%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.9993 | -1.9216 | 0.98528 | -3.1559 | -5.263 | 5.263 | 8.3827 | 1.5762 | -0.24334 | -2.821%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99797 | -2.0427 | 0.9832 | -3.3434 | -5.2577 | 5.2577 | 8.8036 | 1.6547 | -0.2554 | -2.819%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99788 | -2.0806 | 0.98289 | -3.3993 | -5.2051 | 5.2051 | 8.9249 | 1.6787 | -0.25611 | -2.79%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99853 | -2.0868 | 0.98353 | -3.4013 | -5.0946 | 5.0946 | 8.9809 | 1.6936 | -0.24907 | -2.698%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99906 | -2.1054 | 0.98399 | -3.4236 | -4.9788 | 4.9788 | 9.017 | 1.7035 | -0.244 | -2.635%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.9993 | -2.1194 | 0.98417 | -3.4419 | -4.9156 | 4.9156 | 9.0504 | 1.7114 | -0.24158 | -2.6%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99883 | -2.1218 | 0.98366 | -3.4495 | -4.9841 | 4.9841 | 9.0761 | 1.7144 | -0.24587 | -2.638%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99862 | -2.1236 | 0.98342 | -3.454 | -5.0156 | 5.0156 | 9.0901 | 1.7161 | -0.24792 | -2.655%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.9977 | -2.1306 | 0.9824 | -3.4722 | -5.1472 | 5.1472 | 9.1475 | 1.7233 | -0.25649 | -2.728%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99662 | -2.1758 | 0.98099 | -3.5474 | -5.2367 | 5.2367 | 9.3276 | 1.7543 | -0.26642 | -2.777%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99531 | -2.2733 | 0.97911 | -3.7021 | -5.263 | 5.263 | 9.6038 | 1.8032 | -0.27916 | -2.825%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99493 | -2.3062 | 0.97853 | -3.7533 | -5.263 | 5.263 | 9.7175 | 1.8243 | -0.2825 | -2.825%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99504 | -2.2967 | 0.9787 | -3.7384 | -5.263 | 5.263 | 9.6845 | 1.8182 | -0.28153 | -2.825%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.9954 | -2.266 | 0.97924 | -3.6907 | -5.263 | 5.263 | 9.5786 | 1.7985 | -0.27842 | -2.825%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99616 | -2.1994 | 0.98042 | -3.5871 | -5.263 | 5.263 | 9.3483 | 1.7558 | -0.27166 | -2.824%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99769 | -2.0647 | 0.98278 | -3.3778 | -5.263 | 5.263 | 8.881 | 1.6689 | -0.25795 | -2.823%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99955 | -1.8996 | 0.98566 | -3.1218 | -5.263 | 5.263 | 8.3059 | 1.5618 | -0.2411 | -2.821%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0011 | -1.7607 | 0.98806 | -2.9069 | -5.263 | 5.263 | 7.8201 | 1.4713 | -0.22688 | -2.819%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0021 | -1.669 | 0.98964 | -2.7653 | -5.263 | 5.263 | 7.4985 | 1.4113 | -0.21748 | -2.819%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0027 | -1.614 | 0.99058 | -2.6804 | -5.263 | 5.263 | 7.3052 | 1.3752 | -0.21183 | -2.818%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.003 | -1.5837 | 0.9911 | -2.6335 | -5.263 | 5.263 | 7.1983 | 1.3552 | -0.20871 | -2.818%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0031 | -1.5812 | 0.99114 | -2.6297 | -5.263 | 5.263 | 7.1895 | 1.3536 | -0.20845 | -2.818%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0026 | -1.6268 | 0.99036 | -2.7 | -5.263 | 5.263 | 7.3499 | 1.3835 | -0.21313 | -2.818%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.0013 | -1.7438 | 0.98835 | -2.8808 | -5.263 | 5.263 | 7.7609 | 1.4602 | -0.22515 | -2.819%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.9993 | -1.9216 | 0.98528 | -3.1559 | -5.263 | 5.263 | 8.3827 | 1.5762 | -0.24334 | -2.821%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99794 | -2.0423 | 0.98317 | -3.3431 | -5.263 | 5.263 | 8.8033 | 1.6545 | -0.25567 | -2.822%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99756 | -2.0764 | 0.98258 | -3.3961 | -5.263 | 5.263 | 8.9219 | 1.6765 | -0.25914 | -2.823%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99743 | -2.0905 | 0.98237 | -3.4176 | -5.2577 | 5.2577 | 8.9697 | 1.6856 | -0.26026 | -2.82%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2419 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99742 | -2.1003 | 0.9823 | -3.432 | -5.2419 | 5.2419 | 9.0007 | 1.6918 | -0.26031 | -2.811%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99741 | -2.1102 | 0.98223 | -3.4463 | -5.2262 | 5.2262 | 9.0316 | 1.698 | -0.26035 | -2.802%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99731 | -2.1186 | 0.98209 | -3.4594 | -5.2262 | 5.2262 | 9.0608 | 1.7034 | -0.2612 | -2.802%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2367 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99743 | -2.1046 | 0.98225 | -3.4368 | -5.2367 | 5.2367 | 9.0787 | 1.708 | -0.25931 | -2.777%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2525 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99713 | -2.1215 | 0.98184 | -3.4641 | -5.2525 | 5.2525 | 9.142 | 1.7193 | -0.26196 | -2.786%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99627 | -2.1925 | 0.98057 | -3.5761 | -5.2577 | 5.2577 | 9.3234 | 1.7513 | -0.27063 | -2.821%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99531 | -2.2733 | 0.97911 | -3.7021 | -5.263 | 5.263 | 9.6038 | 1.8032 | -0.27916 | -2.825%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99493 | -2.3062 | 0.97853 | -3.7533 | -5.263 | 5.263 | 9.7175 | 1.8243 | -0.2825 | -2.825%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99504 | -2.2967 | 0.9787 | -3.7384 | -5.263 | 5.263 | 9.6845 | 1.8182 | -0.28153 | -2.825%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.9954 | -2.266 | 0.97924 | -3.6907 | -5.263 | 5.263 | 9.5786 | 1.7985 | -0.27842 | -2.825%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99616 | -2.1994 | 0.98042 | -3.5871 | -5.263 | 5.263 | 9.3483 | 1.7558 | -0.27166 | -2.824%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.99769 | -2.0647 | 0.98278 | -3.3778 | -5.263 | 5.263 | 8.881 | 1.6689 | -0.25795 | -2.823%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99955 | -1.8996 | 0.98566 | -3.1218 | -5.263 | 5.263 | 8.3059 | 1.5618 | -0.2411 | -2.821%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0011 | -1.7607 | 0.98806 | -2.9069 | -5.263 | 5.263 | 7.8201 | 1.4713 | -0.22688 | -2.819%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4761 | 0.97729 | -2.5916 | -7.5395 | 10.526 | 7.3999 | 1.342 | -0.31609 | -4.097%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99025 | -1.4212 | 0.97824 | -2.5062 | -7.5369 | 10.526 | 7.2092 | 1.3079 | -0.30776 | -4.094%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3908 | 0.97876 | -2.4591 | -7.5358 | 10.526 | 7.1038 | 1.289 | -0.30317 | -4.093%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3884 | 0.9788 | -2.4552 | -7.5357 | 10.526 | 7.0952 | 1.2875 | -0.30279 | -4.093%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4339 | 0.97802 | -2.5259 | -7.5375 | 10.526 | 7.2533 | 1.3158 | -0.30969 | -4.095%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5508 | 0.976 | -2.7078 | -7.5419 | 10.526 | 7.6586 | 1.3882 | -0.32739 | -4.1%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5049 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7284 | 0.97291 | -2.9847 | -7.5487 | 10.5049 | 8.2717 | 1.4976 | -0.35427 | -4.107%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.2313 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.849 | 0.97079 | -3.1731 | -7.5532 | 10.2313 | 8.6865 | 1.5714 | -0.37252 | -4.112%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.98501 | -1.8831 | 0.97019 | -3.2264 | -7.5544 | 9.4102 | 8.8033 | 1.5922 | -0.37766 | -4.114%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.284 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99486 | -2.0567 | 0.9798 | -3.3916 | -5.7255 | 8.284 | 8.945 | 1.6679 | -0.28496 | -3.087%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.1472 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0653 | 0.97965 | -3.405 | -5.7262 | 7.1472 | 8.9751 | 1.6734 | -0.28594 | -3.088%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.5156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.074 | 0.97949 | -3.4186 | -5.7264 | 6.5156 | 9.0051 | 1.6789 | -0.28693 | -3.088%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.7051 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0824 | 0.97934 | -3.4316 | -5.7267 | 6.7051 | 9.0341 | 1.6843 | -0.28788 | -3.088%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.0103 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0869 | 0.97926 | -3.4386 | -5.7268 | 7.0103 | 9.0496 | 1.6871 | -0.28838 | -3.088%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.884 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1054 | 0.97894 | -3.4674 | -5.7274 | 7.884 | 9.1135 | 1.6989 | -0.29048 | -3.089%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.9155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1587 | 0.97799 | -3.5504 | -5.7289 | 8.9155 | 9.2975 | 1.7327 | -0.29651 | -3.091%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.8418 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2399 | 0.97654 | -3.6771 | -5.7312 | 9.8418 | 9.5773 | 1.7841 | -0.3057 | -3.093%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.3786 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2729 | 0.97595 | -3.7285 | -5.7322 | 10.3786 | 9.6906 | 1.8049 | -0.30942 | -3.094%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5155 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.2633 | 0.97612 | -3.7135 | -5.7319 | 10.5155 | 9.6577 | 1.7989 | -0.30834 | -3.094%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2326 | 0.97667 | -3.6657 | -5.731 | 10.526 | 9.5521 | 1.7795 | -0.30487 | -3.093%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.166 | 0.97786 | -3.5618 | -5.7291 | 10.526 | 9.3227 | 1.7374 | -0.29733 | -3.091%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8714 | 0.97039 | -3.208 | -7.5544 | 10.526 | 8.7631 | 1.585 | -0.37589 | -4.113%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7064 | 0.97329 | -2.9504 | -7.5477 | 10.526 | 8.196 | 1.4841 | -0.35095 | -4.106%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5677 | 0.97571 | -2.7341 | -7.5424 | 10.526 | 7.717 | 1.3987 | -0.32995 | -4.1%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4761 | 0.97729 | -2.5916 | -7.539 | 10.526 | 7.3999 | 1.342 | -0.31609 | -4.096%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99025 | -1.4212 | 0.97824 | -2.5062 | -7.5369 | 10.526 | 7.2092 | 1.3079 | -0.30776 | -4.094%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3908 | 0.97876 | -2.4591 | -7.5358 | 10.526 | 7.1038 | 1.289 | -0.30317 | -4.093%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3884 | 0.9788 | -2.4552 | -7.5357 | 10.526 | 7.0952 | 1.2875 | -0.30279 | -4.093%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4339 | 0.97802 | -2.5259 | -7.5375 | 10.526 | 7.2533 | 1.3158 | -0.30969 | -4.095%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5508 | 0.976 | -2.7078 | -7.5419 | 10.526 | 7.6586 | 1.3882 | -0.32739 | -4.1%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7284 | 0.97291 | -2.9847 | -7.5487 | 10.526 | 8.2717 | 1.4976 | -0.35427 | -4.107%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.849 | 0.97079 | -3.1731 | -7.5532 | 10.5155 | 8.6865 | 1.5714 | -0.37252 | -4.112%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.98501 | -1.8831 | 0.97019 | -3.2264 | -7.5544 | 10.4102 | 8.8033 | 1.5922 | -0.37766 | -4.114%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99486 | -2.0567 | 0.9798 | -3.3916 | -5.7255 | 10.1892 | 8.945 | 1.6679 | -0.28496 | -3.087%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0653 | 0.97965 | -3.405 | -5.7262 | 9.9576 | 8.9751 | 1.6734 | -0.28594 | -3.088%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.074 | 0.97949 | -3.4186 | -5.7264 | 9.8313 | 9.0051 | 1.6789 | -0.28693 | -3.088%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0824 | 0.97934 | -3.4316 | -5.7267 | 9.9681 | 9.0341 | 1.6843 | -0.28788 | -3.088%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0869 | 0.97926 | -3.4386 | -5.7268 | 10.0313 | 9.0496 | 1.6871 | -0.28838 | -3.088%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1054 | 0.97894 | -3.4674 | -5.7274 | 10.2944 | 9.1135 | 1.6989 | -0.29048 | -3.089%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1587 | 0.97799 | -3.5504 | -5.7289 | 10.4734 | 9.2975 | 1.7327 | -0.29651 | -3.091%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2399 | 0.97654 | -3.6771 | -5.7312 | 10.526 | 9.5773 | 1.7841 | -0.3057 | -3.093%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2729 | 0.97595 | -3.7285 | -5.7322 | 10.526 | 9.6906 | 1.8049 | -0.30942 | -3.094%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.2633 | 0.97612 | -3.7135 | -5.7319 | 10.526 | 9.6577 | 1.7989 | -0.30834 | -3.094%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2326 | 0.97667 | -3.6657 | -5.731 | 10.526 | 9.5521 | 1.7795 | -0.30487 | -3.093%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.166 | 0.97786 | -3.5618 | -5.7291 | 10.526 | 9.3227 | 1.7374 | -0.29733 | -3.091%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8714 | 0.97039 | -3.208 | -7.5544 | 10.526 | 8.7631 | 1.585 | -0.37589 | -4.113%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7064 | 0.97329 | -2.9504 | -7.5477 | 10.526 | 8.196 | 1.4841 | -0.35095 | -4.106%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5677 | 0.97571 | -2.7341 | -7.5424 | 10.526 | 7.717 | 1.3987 | -0.32995 | -4.1%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4761 | 0.97729 | -2.5916 | -7.539 | 10.526 | 7.3999 | 1.342 | -0.31609 | -4.096%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99025 | -1.4212 | 0.97824 | -2.5062 | -7.5369 | 10.526 | 7.2092 | 1.3079 | -0.30776 | -4.094%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3908 | 0.97876 | -2.4591 | -7.5358 | 10.526 | 7.1038 | 1.289 | -0.30317 | -4.093%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3884 | 0.9788 | -2.4552 | -7.5357 | 10.526 | 7.0952 | 1.2875 | -0.30279 | -4.093%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4339 | 0.97802 | -2.5259 | -7.5375 | 10.526 | 7.2533 | 1.3158 | -0.30969 | -4.095%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5508 | 0.976 | -2.7078 | -7.5419 | 10.526 | 7.6586 | 1.3882 | -0.32739 | -4.1%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7284 | 0.97291 | -2.9847 | -7.5487 | 10.526 | 8.2717 | 1.4976 | -0.35427 | -4.107%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.849 | 0.97079 | -3.1731 | -7.5532 | 10.526 | 8.6865 | 1.5714 | -0.37252 | -4.112%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.98501 | -1.8831 | 0.97019 | -3.2264 | -7.5544 | 10.526 | 8.8033 | 1.5922 | -0.37766 | -4.114%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99486 | -2.0567 | 0.9798 | -3.3916 | -5.7255 | 10.5155 | 8.945 | 1.6679 | -0.28496 | -3.087%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4839 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0653 | 0.97965 | -3.405 | -5.7262 | 10.4839 | 8.9751 | 1.6734 | -0.28594 | -3.088%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.074 | 0.97949 | -3.4186 | -5.7264 | 10.4523 | 9.0051 | 1.6789 | -0.28693 | -3.088%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0824 | 0.97934 | -3.4316 | -5.7267 | 10.4523 | 9.0341 | 1.6843 | -0.28788 | -3.088%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4734 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.0869 | 0.97926 | -3.4386 | -5.7268 | 10.4734 | 9.0496 | 1.6871 | -0.28838 | -3.088%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5049 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1054 | 0.97894 | -3.4674 | -5.7274 | 10.5049 | 9.1135 | 1.6989 | -0.29048 | -3.089%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1587 | 0.97799 | -3.5504 | -5.7289 | 10.5155 | 9.2975 | 1.7327 | -0.29651 | -3.091%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2399 | 0.97654 | -3.6771 | -5.7312 | 10.526 | 9.5773 | 1.7841 | -0.3057 | -3.093%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2729 | 0.97595 | -3.7285 | -5.7322 | 10.526 | 9.6906 | 1.8049 | -0.30942 | -3.094%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.2633 | 0.97612 | -3.7135 | -5.7319 | 10.526 | 9.6577 | 1.7989 | -0.30834 | -3.094%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2326 | 0.97667 | -3.6657 | -5.731 | 10.526 | 9.5521 | 1.7795 | -0.30487 | -3.093%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.166 | 0.97786 | -3.5618 | -5.7291 | 10.526 | 9.3227 | 1.7374 | -0.29733 | -3.091%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8714 | 0.97039 | -3.208 | -7.5544 | 10.526 | 8.7631 | 1.585 | -0.37589 | -4.113%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7064 | 0.97329 | -2.9504 | -7.5477 | 10.526 | 8.196 | 1.4841 | -0.35095 | -4.106%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5677 | 0.97571 | -2.7341 | -7.5424 | 10.526 | 7.717 | 1.3987 | -0.32995 | -4.1%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0168 | -3.1788 | 1.0168 | -3.1788 | 0.97509 | -2.3937 | 0.97509 | -2.3937 | -5.263 | 5.263 | 7.3823 | 1.3297 | -0.33368 | -4.325%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97605 | -2.3071 | 0.97605 | -2.3071 | -5.263 | 5.263 | 7.1923 | 1.296 | -0.32474 | -4.32%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97659 | -2.2594 | 0.97659 | -2.2594 | -5.263 | 5.263 | 7.0872 | 1.2774 | -0.3198 | -4.318%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97663 | -2.2555 | 0.97663 | -2.2555 | -5.263 | 5.263 | 7.0786 | 1.2759 | -0.3194 | -4.317%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97583 | -2.3271 | 0.97583 | -2.3271 | -5.263 | 5.263 | 7.2362 | 1.3038 | -0.32681 | -4.321%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97377 | -2.5119 | 0.97377 | -2.5119 | -5.263 | 5.263 | 7.6402 | 1.3753 | -0.34584 | -4.331%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2525 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.2525 | 5.2525 | 8.2457 | 1.4793 | -0.38031 | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1156 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 5.1156 | 8.679 | 1.5661 | -0.37996 | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.7051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97259 | -3.1094 | 0.97259 | -3.1094 | -4.7051 | 4.7051 | 8.8263 | 1.6084 | -0.35469 | -3.863%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.142 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97712 | -3.1972 | 0.97712 | -3.1972 | -4.142 | 4.142 | 8.9192 | 1.6495 | -0.31077 | -3.367%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5736 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.9813 | -3.3257 | 0.9813 | -3.3257 | -3.5736 | 3.5736 | 8.991 | 1.6848 | -0.26997 | -2.915%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.2578 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.98368 | -3.3863 | 0.98368 | -3.3863 | -3.2578 | 3.2578 | 9.0456 | 1.708 | -0.24636 | -2.651%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.3525 | 5 | 1.0089 | -3.8658 | 1.0089 | -3.8658 | 0.98277 | -3.3851 | 0.98277 | -3.3851 | -3.3525 | 3.3525 | 9.0675 | 1.7082 | -0.25453 | -2.73%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.5052 | 5 | 1.0088 | -3.8727 | 1.0088 | -3.8727 | 0.98147 | -3.3691 | 0.98147 | -3.3691 | -3.5052 | 3.5052 | 9.0711 | 1.7025 | -0.26689 | -2.858%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 5.263 | 3.942 | 5 | 1.0085 | -3.9012 | 1.0085 | -3.9012 | 0.97792 | -3.2983 | 0.97792 | -3.2983 | -3.942 | 3.942 | 9.1036 | 1.6918 | -0.30042 | -3.195%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.4578 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97259 | -3.3242 | 0.97259 | -3.3242 | -4.4578 | 4.4578 | 9.2434 | 1.694 | -0.35062 | -3.655%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 5.263 | 4.9209 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 4.9209 | 9.5097 | 1.7357 | -0.3733 | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.1893 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 5.1893 | 9.6283 | 1.7602 | -0.37171 | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.2577 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 5.2577 | 9.5938 | 1.7531 | -0.37219 | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 5.263 | 9.4834 | 1.7302 | -0.37364 | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 5.263 | 9.2437 | 1.6809 | -0.37629 | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 5.263 | 8.7593 | 1.5824 | -0.37966 | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97101 | -2.7601 | 0.97101 | -2.7601 | -5.263 | 5.263 | 8.1758 | 1.4699 | -0.37122 | -4.343%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97347 | -2.5387 | 0.97347 | -2.5387 | -5.263 | 5.263 | 7.6984 | 1.3856 | -0.3486 | -4.332%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97509 | -2.3937 | 0.97509 | -2.3937 | -5.263 | 5.263 | 7.3823 | 1.3297 | -0.33369 | -4.325%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97605 | -2.3071 | 0.97605 | -2.3071 | -5.263 | 5.263 | 7.1923 | 1.296 | -0.32474 | -4.32%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97659 | -2.2594 | 0.97659 | -2.2594 | -5.263 | 5.263 | 7.0872 | 1.2774 | -0.3198 | -4.318%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97663 | -2.2555 | 0.97663 | -2.2555 | -5.263 | 5.263 | 7.0786 | 1.2759 | -0.3194 | -4.317%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97583 | -2.3271 | 0.97583 | -2.3271 | -5.263 | 5.263 | 7.2362 | 1.3038 | -0.32681 | -4.321%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97377 | -2.5119 | 0.97377 | -2.5119 | -5.263 | 5.263 | 7.6402 | 1.3753 | -0.34584 | -4.331%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.263 | 5.263 | 8.2457 | 1.4793 | -0.38031 | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2577 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 5.2577 | 8.679 | 1.5661 | -0.37996 | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 5.2051 | 8.8015 | 1.5909 | -0.37947 | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0946 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 5.0946 | 8.8508 | 1.6009 | -0.37923 | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9788 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 4.9788 | 8.8819 | 1.6072 | -0.37906 | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9156 | 4.9156 | 8.9131 | 1.6135 | -0.37888 | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 5.263 | 4.9841 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 4.9841 | 8.9433 | 1.6196 | -0.3787 | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.0156 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 5.0156 | 8.9594 | 1.6229 | -0.37859 | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.1472 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 5.1472 | 9.0259 | 1.6364 | -0.37814 | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.2367 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 5.2367 | 9.2175 | 1.6756 | -0.37654 | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 5.263 | 9.5097 | 1.7357 | -0.3733 | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 5.263 | 9.6283 | 1.7602 | -0.37171 | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 5.263 | 9.5938 | 1.7531 | -0.37219 | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 5.263 | 9.4834 | 1.7302 | -0.37364 | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 5.263 | 9.2437 | 1.6809 | -0.37629 | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 5.263 | 8.7593 | 1.5824 | -0.37966 | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97101 | -2.7601 | 0.97101 | -2.7601 | -5.263 | 5.263 | 8.1758 | 1.4699 | -0.37122 | -4.343%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97347 | -2.5387 | 0.97347 | -2.5387 | -5.263 | 5.263 | 7.6984 | 1.3856 | -0.3486 | -4.332%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97509 | -2.3937 | 0.97509 | -2.3937 | -5.263 | 5.263 | 7.3823 | 1.3297 | -0.33369 | -4.325%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97605 | -2.3071 | 0.97605 | -2.3071 | -5.263 | 5.263 | 7.1923 | 1.296 | -0.32474 | -4.32%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97659 | -2.2594 | 0.97659 | -2.2594 | -5.263 | 5.263 | 7.0872 | 1.2774 | -0.3198 | -4.318%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97663 | -2.2555 | 0.97663 | -2.2555 | -5.263 | 5.263 | 7.0786 | 1.2759 | -0.3194 | -4.317%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97583 | -2.3271 | 0.97583 | -2.3271 | -5.263 | 5.263 | 7.2362 | 1.3038 | -0.32681 | -4.321%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97377 | -2.5119 | 0.97377 | -2.5119 | -5.263 | 5.263 | 7.6402 | 1.3753 | -0.34584 | -4.331%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.263 | 5.263 | 8.2457 | 1.4793 | -0.38031 | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 5.263 | 8.679 | 1.5661 | -0.37996 | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 5.263 | 8.8015 | 1.5909 | -0.37947 | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 5.2577 | 8.8508 | 1.6009 | -0.37923 | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2419 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 5.2419 | 8.8819 | 1.6072 | -0.37906 | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 5.2262 | 8.9131 | 1.6135 | -0.37888 | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2262 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 5.2262 | 8.9433 | 1.6196 | -0.3787 | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2367 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 5.2367 | 8.9594 | 1.6229 | -0.37859 | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2525 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 5.2525 | 9.0259 | 1.6364 | -0.37814 | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.2577 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 5.2577 | 9.2175 | 1.6756 | -0.37654 | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 5.263 | 9.5097 | 1.7357 | -0.3733 | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 5.263 | 9.6283 | 1.7602 | -0.37171 | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 5.263 | 9.5938 | 1.7531 | -0.37219 | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 5.263 | 9.4834 | 1.7302 | -0.37364 | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 5.263 | 9.2437 | 1.6809 | -0.37629 | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 5.263 | 8.7593 | 1.5824 | -0.37966 | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97101 | -2.7601 | 0.97101 | -2.7601 | -5.263 | 5.263 | 8.1758 | 1.4699 | -0.37122 | -4.343%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97347 | -2.5387 | 0.97347 | -2.5387 | -5.263 | 5.263 | 7.6984 | 1.3856 | -0.3486 | -4.332%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.3203 | 0.97 | -2.3203 | -5.8537 | 10.526 | 7.3417 | 1.3015 | -0.37426 | -4.85%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2192 | 0.97 | -2.2192 | -5.9647 | 10.526 | 7.1452 | 1.2634 | -0.37175 | -4.945%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1635 | 0.97 | -2.1635 | -6.0257 | 10.526 | 7.0368 | 1.2425 | -0.37018 | -4.998%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1589 | 0.97 | -2.1589 | -6.0306 | 10.526 | 7.028 | 1.2408 | -0.37005 | -5.002%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2426 | 0.97 | -2.2426 | -5.9391 | 10.526 | 7.1906 | 1.2722 | -0.37238 | -4.924%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4579 | 0.97 | -2.4579 | -5.7019 | 10.526 | 7.609 | 1.3536 | -0.37702 | -4.721%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5049 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.3356 | 10.5049 | 8.2457 | 1.4793 | -0.38033 | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.2313 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 10.2313 | 8.679 | 1.5661 | -0.37996 | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 9.4102 | 8.8015 | 1.5909 | -0.37947 | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.284 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 8.284 | 8.8508 | 1.6009 | -0.37923 | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.1472 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 7.1472 | 8.8819 | 1.6072 | -0.37906 | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.5156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 6.5156 | 8.9131 | 1.6135 | -0.37888 | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | very sunny | 10.526 | 6.7051 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 6.7051 | 8.9433 | 1.6196 | -0.3787 | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.0103 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 7.0103 | 8.9594 | 1.6229 | -0.37859 | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | very sunny | 10.526 | 7.884 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 7.884 | 9.0259 | 1.6364 | -0.37814 | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | very sunny | 10.526 | 8.9155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 8.9155 | 9.2175 | 1.6756 | -0.37654 | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | very sunny | 10.526 | 9.8418 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 9.8418 | 9.5097 | 1.7357 | -0.3733 | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.3786 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 10.3786 | 9.6283 | 1.7602 | -0.37171 | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.5155 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 10.5155 | 9.5938 | 1.7531 | -0.37219 | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 10.526 | 9.4834 | 1.7302 | -0.37364 | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 10.526 | 9.2437 | 1.6809 | -0.37629 | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 10.526 | 8.7593 | 1.5824 | -0.37966 | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7456 | 0.97 | -2.7456 | -5.3813 | 10.526 | 8.1668 | 1.4636 | -0.38015 | -4.448%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | very sunny | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.4891 | 0.97 | -2.4891 | -5.6674 | 10.526 | 7.6695 | 1.3654 | -0.37752 | -4.691%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.3203 | 0.97 | -2.3203 | -5.8538 | 10.526 | 7.3417 | 1.3015 | -0.37427 | -4.851%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2192 | 0.97 | -2.2192 | -5.9647 | 10.526 | 7.1452 | 1.2634 | -0.37175 | -4.945%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1635 | 0.97 | -2.1635 | -6.0257 | 10.526 | 7.0368 | 1.2425 | -0.37018 | -4.998%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1589 | 0.97 | -2.1589 | -6.0306 | 10.526 | 7.028 | 1.2408 | -0.37005 | -5.002%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2426 | 0.97 | -2.2426 | -5.9391 | 10.526 | 7.1906 | 1.2722 | -0.37238 | -4.924%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4579 | 0.97 | -2.4579 | -5.7019 | 10.526 | 7.609 | 1.3536 | -0.37702 | -4.721%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.3356 | 10.526 | 8.2457 | 1.4793 | -0.38033 | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.5155 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 10.5155 | 8.679 | 1.5661 | -0.37996 | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 10.4102 | 8.8015 | 1.5909 | -0.37947 | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.1892 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 10.1892 | 8.8508 | 1.6009 | -0.37923 | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9576 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 9.9576 | 8.8819 | 1.6072 | -0.37906 | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.8313 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 9.8313 | 8.9131 | 1.6135 | -0.37888 | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | moderate sun | 10.526 | 9.9681 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 9.9681 | 8.9433 | 1.6196 | -0.3787 | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.0313 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 10.0313 | 8.9594 | 1.6229 | -0.37859 | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.2944 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 10.2944 | 9.0259 | 1.6364 | -0.37814 | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.4734 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 10.4734 | 9.2175 | 1.6756 | -0.37654 | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 10.526 | 9.5097 | 1.7357 | -0.3733 | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 10.526 | 9.6283 | 1.7602 | -0.37171 | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 10.526 | 9.5938 | 1.7531 | -0.37219 | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 10.526 | 9.4834 | 1.7302 | -0.37364 | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 10.526 | 9.2437 | 1.6809 | -0.37629 | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 10.526 | 8.7593 | 1.5824 | -0.37966 | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7456 | 0.97 | -2.7456 | -5.3813 | 10.526 | 8.1668 | 1.4636 | -0.38015 | -4.448%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | moderate sun | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.4891 | 0.97 | -2.4891 | -5.6674 | 10.526 | 7.6695 | 1.3654 | -0.37752 | -4.691%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.3203 | 0.97 | -2.3203 | -5.8538 | 10.526 | 7.3417 | 1.3015 | -0.37427 | -4.851%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2192 | 0.97 | -2.2192 | -5.9647 | 10.526 | 7.1452 | 1.2634 | -0.37175 | -4.945%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1635 | 0.97 | -2.1635 | -6.0257 | 10.526 | 7.0368 | 1.2425 | -0.37018 | -4.998%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1589 | 0.97 | -2.1589 | -6.0306 | 10.526 | 7.028 | 1.2408 | -0.37005 | -5.002%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2426 | 0.97 | -2.2426 | -5.9391 | 10.526 | 7.1906 | 1.2722 | -0.37238 | -4.924%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4579 | 0.97 | -2.4579 | -5.7019 | 10.526 | 7.609 | 1.3536 | -0.37702 | -4.721%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7863 | 0.97 | -2.7863 | -5.3356 | 10.526 | 8.2457 | 1.4793 | -0.38033 | -4.409%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0102 | 0.97 | -3.0102 | -5.0825 | 10.526 | 8.679 | 1.5661 | -0.37996 | -4.194%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0736 | 0.97 | -3.0736 | -5.0105 | 10.526 | 8.8015 | 1.5909 | -0.37947 | -4.133%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.099 | 0.97 | -3.099 | -4.9814 | 10.5155 | 8.8508 | 1.6009 | -0.37923 | -4.109%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4839 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1152 | 0.97 | -3.1152 | -4.963 | 10.4839 | 8.8819 | 1.6072 | -0.37906 | -4.093%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1313 | 0.97 | -3.1313 | -4.9446 | 10.4523 | 8.9131 | 1.6135 | -0.37888 | -4.077%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4523 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1469 | 0.97 | -3.1469 | -4.9268 | 10.4523 | 8.9433 | 1.6196 | -0.3787 | -4.062%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.4734 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1553 | 0.97 | -3.1553 | -4.9172 | 10.4734 | 8.9594 | 1.6229 | -0.37859 | -4.054%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5049 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.1897 | 0.97 | -3.1897 | -4.8779 | 10.5049 | 9.0259 | 1.6364 | -0.37814 | -4.021%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.5155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.2889 | 0.97 | -3.2889 | -4.7639 | 10.5155 | 9.2175 | 1.6756 | -0.37654 | -3.925%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4404 | 0.97 | -3.4404 | -4.589 | 10.526 | 9.5097 | 1.7357 | -0.3733 | -3.777%
18 | 10 | 2.0306 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5019 | 0.97 | -3.5019 | -4.5176 | 10.526 | 9.6283 | 1.7602 | -0.37171 | -3.717%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.484 | 0.97 | -3.484 | -4.5384 | 10.526 | 9.5938 | 1.7531 | -0.37219 | -3.735%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4267 | 0.97 | -3.4267 | -4.6048 | 10.526 | 9.4834 | 1.7302 | -0.37364 | -3.791%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3025 | 0.97 | -3.3025 | -4.7483 | 10.526 | 9.2437 | 1.6809 | -0.37629 | -3.912%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.0517 | 0.97 | -3.0517 | -5.0353 | 10.526 | 8.7593 | 1.5824 | -0.37966 | -4.154%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7456 | 0.97 | -2.7456 | -5.3813 | 10.526 | 8.1668 | 1.4636 | -0.38015 | -4.448%
24 | 8.047 | 1.634 | 0.98 | ZIP - Res | cloudy | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.4891 | 0.97 | -2.4891 | -5.6674 | 10.526 | 7.6695 | 1.3654 | -0.37752 | -4.691%

## Commerical ZIP Parameters
hour | load MW | load Mvar | PF | load type | sun rating | PV_size (MVA) | Q limit (MVar) | PV bus # | PV bus V pu (no CVR) | PV bus angle (no CVR) | Load bus (5) pu (no CVR) | Load bus (5) angle (no CVR) | PV bus V pu (CVR) | PV bus angle (CVR) | Load bus (5) pu (CVR) | Load bus (5) angle (CVR) | PV bus Q (MVar) | PV bus Q limit (MVar) | load MW CVR | load MVar CVR | MW reduction in P | % reduction in P
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0369 | -1.0325 | 0.99876 | -2.9186 | 1.0235 | -0.90736 | 0.9859 | -2.8254 | -5.263 | 5.263 | 7.6172 | 3.5941 | -0.098845 | -1.281%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.88064 | 0.98735 | -2.7457 | -5.263 | 5.263 | 7.4207 | 3.5018 | -0.096259 | -1.281%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0241 | -0.86588 | 0.98814 | -2.7018 | -5.263 | 5.263 | 7.3121 | 3.4507 | -0.0949 | -1.281%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0242 | -0.86467 | 0.98821 | -2.6982 | -5.263 | 5.263 | 7.3032 | 3.4465 | -0.094788 | -1.281%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.88681 | 0.98701 | -2.7641 | -5.263 | 5.263 | 7.4662 | 3.5232 | -0.096826 | -1.28%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.023 | -0.94372 | 0.98393 | -2.934 | -5.263 | 5.263 | 7.884 | 3.7198 | -0.10203 | -1.278%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0217 | -1.0305 | 0.97923 | -3.1934 | -5.2525 | 5.2525 | 8.5164 | 4.0174 | -0.10964 | -1.271%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9315 | 5.1156 | 8.9725 | 4.2602 | -0.086487 | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 4.7051 | 9.0934 | 4.3174 | -0.087614 | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.142 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 4.142 | 9.1419 | 4.3404 | -0.088066 | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0246 | -1.1585 | 0.9785 | -3.4864 | -3.5736 | 3.5736 | 9.1808 | 4.367 | -0.080159 | -0.8656%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0253 | -1.1698 | 0.97904 | -3.5027 | -3.2578 | 3.2578 | 9.2188 | 4.3923 | -0.073174 | -0.7875%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.025 | -1.1718 | 0.97858 | -3.5139 | -3.3525 | 3.3525 | 9.2464 | 4.4032 | -0.075579 | -0.8108%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0246 | -1.1706 | 0.97808 | -3.5189 | -3.5052 | 3.5052 | 9.2588 | 4.4056 | -0.079221 | -0.8484%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.942 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 3.942 | 9.3143 | 4.422 | -0.089671 | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 4.4578 | 9.5026 | 4.5111 | -0.091419 | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 4.9209 | 9.7889 | 4.6466 | -0.094076 | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 5.1893 | 9.9049 | 4.7014 | -0.09515 | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 5.2577 | 9.8712 | 4.6855 | -0.094836 | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 5.263 | 9.7632 | 4.6344 | -0.093839 | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 5.263 | 9.5283 | 4.5233 | -0.091658 | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 5.263 | 9.0518 | 4.2977 | -0.087226 | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0218 | -1.0195 | 0.97979 | -3.1611 | -5.263 | 5.263 | 8.4381 | 3.9804 | -0.1089 | -1.274%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.95195 | 0.98348 | -2.9586 | -5.263 | 5.263 | 7.9442 | 3.7481 | -0.10278 | -1.277%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0235 | -0.90737 | 0.9859 | -2.8254 | -5.263 | 5.263 | 7.6173 | 3.5943 | -0.098713 | -1.279%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.88064 | 0.98735 | -2.7457 | -5.263 | 5.263 | 7.4207 | 3.5018 | -0.096259 | -1.281%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0241 | -0.86588 | 0.98814 | -2.7018 | -5.263 | 5.263 | 7.3121 | 3.4507 | -0.0949 | -1.281%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0242 | -0.86467 | 0.98821 | -2.6982 | -5.263 | 5.263 | 7.3032 | 3.4465 | -0.094788 | -1.281%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.88681 | 0.98701 | -2.7641 | -5.263 | 5.263 | 7.4662 | 3.5232 | -0.096826 | -1.28%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.023 | -0.94372 | 0.98393 | -2.934 | -5.263 | 5.263 | 7.884 | 3.7198 | -0.10203 | -1.278%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0216 | -1.0302 | 0.9792 | -3.1933 | -5.263 | 5.263 | 8.5161 | 4.0171 | -0.10986 | -1.274%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9315 | 5.2577 | 8.9725 | 4.2602 | -0.086487 | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 5.2051 | 9.0934 | 4.3174 | -0.087614 | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 5.0946 | 9.1419 | 4.3404 | -0.088066 | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 4.9788 | 9.1726 | 4.3549 | -0.088353 | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 4.9156 | 9.2034 | 4.3695 | -0.088639 | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 4.9841 | 9.2331 | 4.3836 | -0.088914 | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 5.0156 | 9.2489 | 4.3911 | -0.089063 | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 5.1472 | 9.3143 | 4.422 | -0.089671 | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 5.2367 | 9.5026 | 4.5111 | -0.091419 | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 5.263 | 9.7889 | 4.6466 | -0.094076 | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 5.263 | 9.9049 | 4.7014 | -0.09515 | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 5.263 | 9.8712 | 4.6855 | -0.094836 | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 5.263 | 9.7632 | 4.6344 | -0.093839 | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 5.263 | 9.5283 | 4.5233 | -0.091658 | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 5.263 | 9.0518 | 4.2977 | -0.087226 | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0218 | -1.0195 | 0.97979 | -3.1611 | -5.263 | 5.263 | 8.4381 | 3.9804 | -0.1089 | -1.274%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.95195 | 0.98348 | -2.9586 | -5.263 | 5.263 | 7.9442 | 3.7481 | -0.10278 | -1.277%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0235 | -0.90737 | 0.9859 | -2.8254 | -5.263 | 5.263 | 7.6173 | 3.5943 | -0.098713 | -1.279%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0239 | -0.88064 | 0.98735 | -2.7457 | -5.263 | 5.263 | 7.4207 | 3.5018 | -0.096259 | -1.281%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0241 | -0.86588 | 0.98814 | -2.7018 | -5.263 | 5.263 | 7.3121 | 3.4507 | -0.0949 | -1.281%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0242 | -0.86467 | 0.98821 | -2.6982 | -5.263 | 5.263 | 7.3032 | 3.4465 | -0.094788 | -1.281%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.0238 | -0.88681 | 0.98701 | -2.7641 | -5.263 | 5.263 | 7.4662 | 3.5232 | -0.096826 | -1.28%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.023 | -0.94372 | 0.98393 | -2.934 | -5.263 | 5.263 | 7.884 | 3.7198 | -0.10203 | -1.278%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.0216 | -1.0302 | 0.9792 | -3.1933 | -5.263 | 5.263 | 8.5161 | 4.0171 | -0.10986 | -1.274%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9315 | 5.263 | 8.9725 | 4.2602 | -0.086487 | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 5.263 | 9.0934 | 4.3174 | -0.087614 | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 5.2577 | 9.1419 | 4.3404 | -0.088066 | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 5.2419 | 9.1726 | 4.3549 | -0.088353 | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 5.2262 | 9.2034 | 4.3695 | -0.088639 | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 5.2262 | 9.2331 | 4.3836 | -0.088914 | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 5.2367 | 9.2489 | 4.3911 | -0.089063 | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 5.2525 | 9.3143 | 4.422 | -0.089671 | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 5.2577 | 9.5026 | 4.5111 | -0.091419 | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 5.263 | 9.7889 | 4.6466 | -0.094076 | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 5.263 | 9.9049 | 4.7014 | -0.09515 | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 5.263 | 9.8712 | 4.6855 | -0.094836 | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 5.263 | 9.7632 | 4.6344 | -0.093839 | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 5.263 | 9.5283 | 4.5233 | -0.091658 | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 5.263 | 9.0518 | 4.2977 | -0.087226 | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0218 | -1.0195 | 0.97979 | -3.1611 | -5.263 | 5.263 | 8.4381 | 3.9804 | -0.1089 | -1.274%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0228 | -0.95195 | 0.98348 | -2.9586 | -5.263 | 5.263 | 7.9442 | 3.7481 | -0.10278 | -1.277%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84943 | 0.97951 | -2.7916 | -7.7761 | 10.526 | 7.5685 | 3.5239 | -0.14752 | -1.912%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0101 | -0.7552 | 0.97397 | -2.6618 | -10.526 | 10.526 | 7.3215 | 3.3593 | -0.19546 | -2.6%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0103 | -0.7404 | 0.97476 | -2.6171 | -10.526 | 10.526 | 7.2143 | 3.3104 | -0.19269 | -2.601%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0103 | -0.73919 | 0.97483 | -2.6135 | -10.526 | 10.526 | 7.2055 | 3.3064 | -0.19246 | -2.602%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.01 | -0.76139 | 0.97364 | -2.6805 | -10.526 | 10.526 | 7.3664 | 3.3798 | -0.19662 | -2.6%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88586 | 0.97754 | -2.9012 | -7.7778 | 10.526 | 7.8334 | 3.6467 | -0.15255 | -1.91%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97254 | 0.97283 | -3.1631 | -7.7823 | 10.5049 | 8.4616 | 3.9375 | -0.16442 | -1.906%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9314 | 10.2313 | 8.9725 | 4.2602 | -0.086487 | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 9.4102 | 9.0934 | 4.3174 | -0.087614 | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.284 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 8.284 | 9.1419 | 4.3404 | -0.088066 | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 7.1472 | 9.1726 | 4.3549 | -0.088353 | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 6.5156 | 9.2034 | 4.3695 | -0.088639 | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 6.7051 | 9.2331 | 4.3836 | -0.088914 | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 7.0103 | 9.2489 | 4.3911 | -0.089063 | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.884 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 7.884 | 9.3143 | 4.422 | -0.089671 | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 8.9155 | 9.5026 | 4.5111 | -0.091419 | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 9.8418 | 9.7889 | 4.6466 | -0.094076 | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 10.3786 | 9.9049 | 4.7014 | -0.09515 | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 10.5155 | 9.8712 | 4.6855 | -0.094836 | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 10.526 | 9.7632 | 4.6344 | -0.093839 | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 10.526 | 9.5283 | 4.5233 | -0.091658 | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 10.526 | 9.0518 | 4.2977 | -0.087226 | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96182 | 0.97341 | -3.1306 | -7.7817 | 10.526 | 8.384 | 3.9017 | -0.16296 | -1.907%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.8941 | 0.9771 | -2.9261 | -7.7783 | 10.526 | 7.8933 | 3.6744 | -0.15369 | -1.91%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84943 | 0.97951 | -2.7916 | -7.776 | 10.526 | 7.5685 | 3.5239 | -0.14752 | -1.912%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0101 | -0.7552 | 0.97397 | -2.6618 | -10.526 | 10.526 | 7.3215 | 3.3593 | -0.19546 | -2.6%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0103 | -0.7404 | 0.97476 | -2.6171 | -10.526 | 10.526 | 7.2143 | 3.3104 | -0.19269 | -2.601%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0103 | -0.73919 | 0.97483 | -2.6135 | -10.526 | 10.526 | 7.2055 | 3.3064 | -0.19246 | -2.602%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.01 | -0.76139 | 0.97364 | -2.6805 | -10.526 | 10.526 | 7.3664 | 3.3798 | -0.19662 | -2.6%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88586 | 0.97754 | -2.9012 | -7.7778 | 10.526 | 7.8334 | 3.6467 | -0.15255 | -1.91%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97254 | 0.97283 | -3.1631 | -7.7823 | 10.526 | 8.4616 | 3.9375 | -0.16442 | -1.906%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9314 | 10.5155 | 8.9725 | 4.2602 | -0.086487 | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 10.4102 | 9.0934 | 4.3174 | -0.087614 | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 10.1892 | 9.1419 | 4.3404 | -0.088066 | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 9.9576 | 9.1726 | 4.3549 | -0.088353 | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 9.8313 | 9.2034 | 4.3695 | -0.088639 | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 9.9681 | 9.2331 | 4.3836 | -0.088914 | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 10.0313 | 9.2489 | 4.3911 | -0.089063 | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 10.2944 | 9.3143 | 4.422 | -0.089671 | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 10.4734 | 9.5026 | 4.5111 | -0.091419 | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 10.526 | 9.7889 | 4.6466 | -0.094076 | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 10.526 | 9.9049 | 4.7014 | -0.09515 | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 10.526 | 9.8712 | 4.6855 | -0.094836 | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 10.526 | 9.7632 | 4.6344 | -0.093839 | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 10.526 | 9.5283 | 4.5233 | -0.091658 | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 10.526 | 9.0518 | 4.2977 | -0.087226 | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96182 | 0.97341 | -3.1306 | -7.7817 | 10.526 | 8.384 | 3.9017 | -0.16296 | -1.907%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.8941 | 0.9771 | -2.9261 | -7.7783 | 10.526 | 7.8933 | 3.6744 | -0.15369 | -1.91%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0369 | -1.0326 | 0.99874 | -2.9194 | 1.0169 | -0.84943 | 0.97951 | -2.7916 | -7.776 | 10.526 | 7.5685 | 3.5239 | -0.14752 | -1.912%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0373 | -1.0059 | 1.0002 | -2.8406 | 1.0101 | -0.7552 | 0.97397 | -2.6618 | -10.526 | 10.526 | 7.3215 | 3.3593 | -0.19546 | -2.6%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0375 | -0.9911 | 1.001 | -2.7972 | 1.0103 | -0.7404 | 0.97476 | -2.6171 | -10.526 | 10.526 | 7.2143 | 3.3104 | -0.19269 | -2.601%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0376 | -0.98989 | 1.0011 | -2.7936 | 1.0103 | -0.73919 | 0.97483 | -2.6135 | -10.526 | 10.526 | 7.2055 | 3.3064 | -0.19246 | -2.602%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0372 | -1.0121 | 0.99987 | -2.8588 | 1.01 | -0.76139 | 0.97364 | -2.6805 | -10.526 | 10.526 | 7.3664 | 3.3798 | -0.19662 | -2.6%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.069 | 0.99675 | -3.0268 | 1.0164 | -0.88586 | 0.97754 | -2.9012 | -7.7778 | 10.526 | 7.8334 | 3.6467 | -0.15255 | -1.91%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.035 | -1.1557 | 0.99196 | -3.2831 | 1.015 | -0.97254 | 0.97283 | -3.1631 | -7.7823 | 10.526 | 8.4616 | 3.9375 | -0.16442 | -1.906%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0341 | -1.2145 | 0.98868 | -3.4582 | 1.0241 | -1.1229 | 0.97914 | -3.3995 | -3.9314 | 10.526 | 8.9725 | 4.2602 | -0.086487 | -0.9547%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0338 | -1.2312 | 0.98775 | -3.5077 | 1.0238 | -1.1396 | 0.97822 | -3.4496 | -3.9319 | 10.526 | 9.0934 | 4.3174 | -0.087614 | -0.9543%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0337 | -1.2379 | 0.98738 | -3.5277 | 1.0237 | -1.1463 | 0.97785 | -3.4697 | -3.9321 | 10.5155 | 9.1419 | 4.3404 | -0.088066 | -0.9541%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 3 | 1.0337 | -1.2421 | 0.98714 | -3.5403 | 1.0237 | -1.1505 | 0.97761 | -3.4825 | -3.9322 | 10.4839 | 9.1726 | 4.3549 | -0.088353 | -0.954%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0336 | -1.2463 | 0.98691 | -3.5529 | 1.0236 | -1.1547 | 0.97738 | -3.4952 | -3.9323 | 10.4523 | 9.2034 | 4.3695 | -0.088639 | -0.9539%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0335 | -1.2504 | 0.98668 | -3.5651 | 1.0235 | -1.1588 | 0.97715 | -3.5076 | -3.9324 | 10.4523 | 9.2331 | 4.3836 | -0.088914 | -0.9538%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 3 | 1.0335 | -1.2526 | 0.98655 | -3.5717 | 1.0235 | -1.161 | 0.97703 | -3.5142 | -3.9325 | 10.4734 | 9.2489 | 4.3911 | -0.089063 | -0.9538%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 3 | 1.0334 | -1.2616 | 0.98605 | -3.5986 | 1.0234 | -1.17 | 0.97653 | -3.5414 | -3.9327 | 10.5049 | 9.3143 | 4.422 | -0.089671 | -0.9535%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0329 | -1.2876 | 0.98459 | -3.6763 | 1.0229 | -1.1961 | 0.97508 | -3.6199 | -3.9334 | 10.5155 | 9.5026 | 4.5111 | -0.091419 | -0.9529%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0323 | -1.3273 | 0.98235 | -3.795 | 1.0223 | -1.2357 | 0.97286 | -3.7399 | -3.9344 | 10.526 | 9.7889 | 4.6466 | -0.094076 | -0.9519%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3433 | 0.98144 | -3.8432 | 1.0221 | -1.2518 | 0.97195 | -3.7887 | -3.9348 | 10.526 | 9.9049 | 4.7014 | -0.09515 | -0.9515%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0321 | -1.3387 | 0.98171 | -3.8292 | 1.0221 | -1.2471 | 0.97222 | -3.7745 | -3.9347 | 10.526 | 9.8712 | 4.6855 | -0.094836 | -0.9516%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0324 | -1.3237 | 0.98255 | -3.7843 | 1.0224 | -1.2321 | 0.97306 | -3.7291 | -3.9343 | 10.526 | 9.7632 | 4.6344 | -0.093839 | -0.952%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0329 | -1.2912 | 0.98439 | -3.6869 | 1.0229 | -1.1996 | 0.97488 | -3.6307 | -3.9335 | 10.526 | 9.5283 | 4.5233 | -0.091658 | -0.9528%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0339 | -1.2254 | 0.98807 | -3.4907 | 1.0239 | -1.1338 | 0.97854 | -3.4323 | -3.9318 | 10.526 | 9.0518 | 4.2977 | -0.087226 | -0.9544%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0352 | -1.1449 | 0.99256 | -3.2513 | 1.0152 | -0.96182 | 0.97341 | -3.1306 | -7.7817 | 10.526 | 8.384 | 3.9017 | -0.16296 | -1.907%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0362 | -1.0773 | 0.99629 | -3.0511 | 1.0162 | -0.8941 | 0.9771 | -2.9261 | -7.7783 | 10.526 | 7.8933 | 3.6744 | -0.15369 | -1.91%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 5.263 | 7.5657 | 3.5199 | -0.15034 | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99118 | -1.471 | 0.97327 | -2.4423 | -5.263 | 5.263 | 7.3163 | 3.3518 | -0.20068 | -2.67%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99169 | -1.4424 | 0.97406 | -2.3981 | -5.263 | 5.263 | 7.2092 | 3.3031 | -0.1978 | -2.67%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99173 | -1.44 | 0.97412 | -2.3945 | -5.263 | 5.263 | 7.2004 | 3.2991 | -0.19756 | -2.671%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99096 | -1.483 | 0.97294 | -2.4608 | -5.263 | 5.263 | 7.3611 | 3.3722 | -0.20188 | -2.669%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 5.263 | 7.8304 | 3.6423 | -0.15558 | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 5.2525 | 8.458 | 3.9324 | -0.16798 | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 5.1156 | 8.9705 | 4.2573 | -0.088473 | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 4.7051 | 9.0913 | 4.3144 | -0.089658 | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.142 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 4.142 | 9.1399 | 4.3374 | -0.090133 | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 3.5736 | 9.1706 | 4.3519 | -0.090433 | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 3.2578 | 9.2013 | 4.3664 | -0.090735 | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 3.3525 | 9.231 | 4.3804 | -0.091025 | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 3.5052 | 9.2468 | 4.3879 | -0.091182 | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.942 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 3.942 | 9.3122 | 4.4188 | -0.091822 | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 4.4578 | 9.5003 | 4.5078 | -0.093662 | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 4.9209 | 9.7865 | 4.643 | -0.096466 | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 5.1893 | 9.9024 | 4.6978 | -0.097599 | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 5.2577 | 9.8687 | 4.6819 | -0.097268 | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 5.263 | 9.7608 | 4.6309 | -0.096213 | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 5.263 | 9.5261 | 4.52 | -0.093915 | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 5.263 | 9.0498 | 4.2948 | -0.08925 | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 5.263 | 8.3806 | 3.8966 | -0.16645 | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 5.263 | 7.8902 | 3.67 | -0.15676 | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 5.263 | 7.5657 | 3.5199 | -0.15034 | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99118 | -1.471 | 0.97327 | -2.4423 | -5.263 | 5.263 | 7.3163 | 3.3518 | -0.20068 | -2.67%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99169 | -1.4424 | 0.97406 | -2.3981 | -5.263 | 5.263 | 7.2092 | 3.3031 | -0.1978 | -2.67%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99173 | -1.44 | 0.97412 | -2.3945 | -5.263 | 5.263 | 7.2004 | 3.2991 | -0.19756 | -2.671%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99096 | -1.483 | 0.97294 | -2.4608 | -5.263 | 5.263 | 7.3611 | 3.3722 | -0.20188 | -2.669%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 5.263 | 7.8304 | 3.6423 | -0.15558 | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 5.263 | 8.458 | 3.9324 | -0.16798 | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 5.2577 | 8.9705 | 4.2573 | -0.088473 | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 5.2051 | 9.0913 | 4.3144 | -0.089658 | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 5.0946 | 9.1399 | 4.3374 | -0.090133 | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 4.9788 | 9.1706 | 4.3519 | -0.090433 | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 4.9156 | 9.2013 | 4.3664 | -0.090735 | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 4.9841 | 9.231 | 4.3804 | -0.091025 | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 5.0156 | 9.2468 | 4.3879 | -0.091182 | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 5.1472 | 9.3122 | 4.4188 | -0.091822 | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 5.2367 | 9.5003 | 4.5078 | -0.093662 | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 5.263 | 9.7865 | 4.643 | -0.096466 | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 5.263 | 9.9024 | 4.6978 | -0.097599 | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 5.263 | 9.8687 | 4.6819 | -0.097268 | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 5.263 | 9.7608 | 4.6309 | -0.096213 | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 5.263 | 9.5261 | 4.52 | -0.093915 | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 5.263 | 9.0498 | 4.2948 | -0.08925 | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 5.263 | 8.3806 | 3.8966 | -0.16645 | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 5.263 | 7.8902 | 3.67 | -0.15676 | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 5.263 | 7.5657 | 3.5199 | -0.15034 | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.99118 | -1.471 | 0.97327 | -2.4423 | -5.263 | 5.263 | 7.3163 | 3.3518 | -0.20068 | -2.67%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.99169 | -1.4424 | 0.97406 | -2.3981 | -5.263 | 5.263 | 7.2092 | 3.3031 | -0.1978 | -2.67%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.99173 | -1.44 | 0.97412 | -2.3945 | -5.263 | 5.263 | 7.2004 | 3.2991 | -0.19756 | -2.671%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.99096 | -1.483 | 0.97294 | -2.4608 | -5.263 | 5.263 | 7.3611 | 3.3722 | -0.20188 | -2.669%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 5.263 | 7.8304 | 3.6423 | -0.15558 | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 5.263 | 8.458 | 3.9324 | -0.16798 | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 5.263 | 8.9705 | 4.2573 | -0.088473 | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 5.263 | 9.0913 | 4.3144 | -0.089658 | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 5.2577 | 9.1399 | 4.3374 | -0.090133 | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 5.2419 | 9.1706 | 4.3519 | -0.090433 | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 5.2262 | 9.2013 | 4.3664 | -0.090735 | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 5.2262 | 9.231 | 4.3804 | -0.091025 | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 5.2367 | 9.2468 | 4.3879 | -0.091182 | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 5.2525 | 9.3122 | 4.4188 | -0.091822 | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 5.2577 | 9.5003 | 4.5078 | -0.093662 | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 5.263 | 9.7865 | 4.643 | -0.096466 | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 5.263 | 9.9024 | 4.6978 | -0.097599 | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 5.263 | 9.8687 | 4.6819 | -0.097268 | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 5.263 | 9.7608 | 4.6309 | -0.096213 | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 5.263 | 9.5261 | 4.52 | -0.093915 | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 5.263 | 9.0498 | 4.2948 | -0.08925 | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 5.263 | 8.3806 | 3.8966 | -0.16645 | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 5.263 | 7.8902 | 3.67 | -0.15676 | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 10.526 | 7.5657 | 3.5199 | -0.15034 | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.4333 | 0.97078 | -2.4094 | -5.7277 | 10.526 | 7.298 | 3.3256 | -0.21899 | -2.913%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4048 | 0.97158 | -2.3652 | -5.7264 | 10.526 | 7.1912 | 3.2774 | -0.2158 | -2.913%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.4024 | 0.97165 | -2.3616 | -5.7263 | 10.526 | 7.1825 | 3.2734 | -0.21554 | -2.913%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4453 | 0.97045 | -2.4279 | -5.728 | 10.526 | 7.3427 | 3.3458 | -0.22032 | -2.913%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 10.526 | 7.8304 | 3.6423 | -0.15558 | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 10.5049 | 8.458 | 3.9324 | -0.16798 | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 10.2313 | 8.9705 | 4.2573 | -0.088473 | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 9.4102 | 9.0913 | 4.3144 | -0.089658 | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.284 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 8.284 | 9.1399 | 4.3374 | -0.090133 | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 7.1472 | 9.1706 | 4.3519 | -0.090433 | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 6.5156 | 9.2013 | 4.3664 | -0.090735 | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 6.7051 | 9.231 | 4.3804 | -0.091025 | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 7.0103 | 9.2468 | 4.3879 | -0.091182 | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.884 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 7.884 | 9.3122 | 4.4188 | -0.091822 | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 8.9155 | 9.5003 | 4.5078 | -0.093662 | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 9.8418 | 9.7865 | 4.643 | -0.096466 | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 10.3786 | 9.9024 | 4.6978 | -0.097599 | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 10.5155 | 9.8687 | 4.6819 | -0.097268 | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 10.526 | 9.7608 | 4.6309 | -0.096213 | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 10.526 | 9.5261 | 4.52 | -0.093915 | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 10.526 | 9.0498 | 4.2948 | -0.08925 | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 10.526 | 8.3806 | 3.8966 | -0.16645 | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 10.526 | 7.8902 | 3.67 | -0.15676 | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 10.526 | 7.5657 | 3.5199 | -0.15034 | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.4333 | 0.97078 | -2.4094 | -5.7277 | 10.526 | 7.298 | 3.3256 | -0.21899 | -2.913%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4048 | 0.97158 | -2.3652 | -5.7264 | 10.526 | 7.1912 | 3.2774 | -0.2158 | -2.913%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.4024 | 0.97165 | -2.3616 | -5.7263 | 10.526 | 7.1825 | 3.2734 | -0.21554 | -2.913%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4453 | 0.97045 | -2.4279 | -5.728 | 10.526 | 7.3427 | 3.3458 | -0.22032 | -2.913%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 10.526 | 7.8304 | 3.6423 | -0.15558 | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 10.526 | 8.458 | 3.9324 | -0.16798 | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 10.5155 | 8.9705 | 4.2573 | -0.088473 | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 10.4102 | 9.0913 | 4.3144 | -0.089658 | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 10.1892 | 9.1399 | 4.3374 | -0.090133 | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 9.9576 | 9.1706 | 4.3519 | -0.090433 | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 9.8313 | 9.2013 | 4.3664 | -0.090735 | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 9.9681 | 9.231 | 4.3804 | -0.091025 | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 10.0313 | 9.2468 | 4.3879 | -0.091182 | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 10.2944 | 9.3122 | 4.4188 | -0.091822 | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 10.4734 | 9.5003 | 4.5078 | -0.093662 | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 10.526 | 9.7865 | 4.643 | -0.096466 | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 10.526 | 9.9024 | 4.6978 | -0.097599 | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 10.526 | 9.8687 | 4.6819 | -0.097268 | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 10.526 | 9.7608 | 4.6309 | -0.096213 | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 10.526 | 9.5261 | 4.52 | -0.093915 | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 10.526 | 9.0498 | 4.2948 | -0.08925 | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 10.526 | 8.3806 | 3.8966 | -0.16645 | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 10.526 | 7.8902 | 3.67 | -0.15676 | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0177 | -1.9588 | 0.99874 | -2.9194 | 0.99771 | -1.6427 | 0.97914 | -2.6321 | -3.8599 | 10.526 | 7.5657 | 3.5199 | -0.15034 | -1.948%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -1.907 | 1.0002 | -2.8406 | 0.98866 | -1.4333 | 0.97078 | -2.4094 | -5.7277 | 10.526 | 7.298 | 3.3256 | -0.21899 | -2.913%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8784 | 1.001 | -2.7972 | 0.98918 | -1.4048 | 0.97158 | -2.3652 | -5.7264 | 10.526 | 7.1912 | 3.2774 | -0.2158 | -2.913%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -1.8761 | 1.0011 | -2.7936 | 0.98922 | -1.4024 | 0.97165 | -2.3616 | -5.7263 | 10.526 | 7.1825 | 3.2734 | -0.21554 | -2.913%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0184 | -1.919 | 0.99987 | -2.8588 | 0.98844 | -1.4453 | 0.97045 | -2.4279 | -5.728 | 10.526 | 7.3427 | 3.3458 | -0.22032 | -2.913%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0164 | -2.0293 | 0.99675 | -3.0268 | 0.99642 | -1.7132 | 0.97716 | -2.7406 | -3.8618 | 10.526 | 7.8304 | 3.6423 | -0.15558 | -1.948%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0133 | -2.1973 | 0.99196 | -3.2831 | 0.99334 | -1.8811 | 0.97241 | -2.9998 | -3.8667 | 10.526 | 8.458 | 3.9324 | -0.16798 | -1.947%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0112 | -2.3117 | 0.98868 | -3.4582 | 1.0012 | -2.1533 | 0.97892 | -3.3171 | -1.9551 | 10.526 | 8.9705 | 4.2573 | -0.088473 | -0.9766%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0106 | -2.344 | 0.98775 | -3.5077 | 1.0006 | -2.1857 | 0.978 | -3.3669 | -1.9556 | 10.526 | 9.0913 | 4.3144 | -0.089658 | -0.9766%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0104 | -2.357 | 0.98738 | -3.5277 | 1.0004 | -2.1987 | 0.97762 | -3.387 | -1.9559 | 10.5155 | 9.1399 | 4.3374 | -0.090133 | -0.9765%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 4 | 1.0102 | -2.3652 | 0.98714 | -3.5403 | 1.0002 | -2.2069 | 0.97739 | -3.3997 | -1.9559 | 10.4839 | 9.1706 | 4.3519 | -0.090433 | -0.9765%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0101 | -2.3734 | 0.98691 | -3.5529 | 1.0001 | -2.2151 | 0.97715 | -3.4124 | -1.9561 | 10.4523 | 9.2013 | 4.3664 | -0.090735 | -0.9765%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0099 | -2.3814 | 0.98668 | -3.5651 | 0.99992 | -2.2231 | 0.97692 | -3.4247 | -1.9562 | 10.4523 | 9.231 | 4.3804 | -0.091025 | -0.9765%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 4 | 1.0098 | -2.3857 | 0.98655 | -3.5717 | 0.99984 | -2.2273 | 0.9768 | -3.4312 | -1.9563 | 10.4734 | 9.2468 | 4.3879 | -0.091182 | -0.9765%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 4 | 1.0095 | -2.4032 | 0.98605 | -3.5986 | 0.99951 | -2.2449 | 0.9763 | -3.4583 | -1.9565 | 10.5049 | 9.3122 | 4.4188 | -0.091822 | -0.9764%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0086 | -2.4538 | 0.98459 | -3.6763 | 0.99857 | -2.2955 | 0.97484 | -3.5365 | -1.9573 | 10.5155 | 9.5003 | 4.5078 | -0.093662 | -0.9763%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0071 | -2.531 | 0.98235 | -3.795 | 0.99712 | -2.3727 | 0.97262 | -3.6558 | -1.9584 | 10.526 | 9.7865 | 4.643 | -0.096466 | -0.9761%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0065 | -2.5623 | 0.98144 | -3.8432 | 0.99653 | -2.404 | 0.97171 | -3.7043 | -1.9589 | 10.526 | 9.9024 | 4.6978 | -0.097599 | -0.976%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0067 | -2.5532 | 0.98171 | -3.8292 | 0.9967 | -2.3949 | 0.97197 | -3.6902 | -1.9588 | 10.526 | 9.8687 | 4.6819 | -0.097268 | -0.976%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0072 | -2.524 | 0.98255 | -3.7843 | 0.99725 | -2.3657 | 0.97282 | -3.6451 | -1.9583 | 10.526 | 9.7608 | 4.6309 | -0.096213 | -0.9761%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0084 | -2.4607 | 0.98439 | -3.6869 | 0.99844 | -2.3024 | 0.97464 | -3.5472 | -1.9574 | 10.526 | 9.5261 | 4.52 | -0.093915 | -0.9762%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0108 | -2.3328 | 0.98807 | -3.4907 | 1.0008 | -2.1745 | 0.97832 | -3.3498 | -1.9555 | 10.526 | 9.0498 | 4.2948 | -0.08925 | -0.9766%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0137 | -2.1765 | 0.99256 | -3.2513 | 0.99372 | -1.8603 | 0.973 | -2.9677 | -3.8661 | 10.526 | 8.3806 | 3.8966 | -0.16645 | -1.947%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0161 | -2.0453 | 0.99629 | -3.0511 | 0.99613 | -1.7291 | 0.97671 | -2.7652 | -3.8623 | 10.526 | 7.8902 | 3.67 | -0.15676 | -1.948%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 5.263 | 7.4963 | 3.4201 | -0.21975 | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 5.263 | 7.2922 | 3.3173 | -0.22478 | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 5.263 | 7.1797 | 3.2609 | -0.22728 | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 5.263 | 7.1705 | 3.2563 | -0.22748 | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 5.263 | 7.3393 | 3.341 | -0.22367 | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 5.263 | 7.7741 | 3.5611 | -0.21192 | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 5.2525 | 8.4374 | 3.9024 | -0.18856 | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 5.1156 | 8.8902 | 4.1394 | -0.16883 | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 4.7051 | 9.0183 | 4.2071 | -0.16269 | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.142 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 4.142 | 9.0698 | 4.2344 | -0.16015 | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 3.5736 | 9.1025 | 4.2517 | -0.15852 | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 3.2578 | 9.1351 | 4.2691 | -0.15688 | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 3.3525 | 9.1667 | 4.2859 | -0.15527 | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 3.5052 | 9.1836 | 4.2948 | -0.15441 | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 5.263 | 3.942 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 3.942 | 9.2532 | 4.3319 | -0.1508 | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 4.4578 | 9.454 | 4.4393 | -0.13997 | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 4.9209 | 9.7607 | 4.6047 | -0.12227 | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 5.1893 | 9.8853 | 4.6724 | -0.11468 | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 5.2577 | 9.8491 | 4.6527 | -0.11691 | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 5.263 | 9.7331 | 4.5898 | -0.12392 | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 5.263 | 9.4816 | 4.4541 | -0.13844 | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 5.263 | 8.9742 | 4.1838 | -0.16483 | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 5.263 | 8.3552 | 3.8597 | -0.19181 | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 5.263 | 7.837 | 3.5931 | -0.20999 | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 5.263 | 7.4962 | 3.4201 | -0.21975 | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 5.263 | 7.2922 | 3.3173 | -0.22478 | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 5.263 | 7.1797 | 3.2609 | -0.22728 | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 5.263 | 7.1705 | 3.2563 | -0.22748 | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 5.263 | 7.3393 | 3.341 | -0.22367 | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 5.263 | 7.7741 | 3.5611 | -0.21192 | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 5.263 | 8.4374 | 3.9024 | -0.18856 | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 5.2577 | 8.8902 | 4.1394 | -0.16883 | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 5.2051 | 9.0183 | 4.2071 | -0.16269 | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 5.0946 | 9.0698 | 4.2344 | -0.16015 | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 4.9788 | 9.1025 | 4.2517 | -0.15852 | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 4.9156 | 9.1351 | 4.2691 | -0.15688 | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 4.9841 | 9.1667 | 4.2859 | -0.15527 | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 5.0156 | 9.1836 | 4.2948 | -0.15441 | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 5.1472 | 9.2532 | 4.3319 | -0.1508 | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 5.2367 | 9.454 | 4.4393 | -0.13997 | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 5.263 | 9.7607 | 4.6047 | -0.12227 | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 5.263 | 9.8853 | 4.6724 | -0.11468 | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 5.263 | 9.8491 | 4.6527 | -0.11691 | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 5.263 | 9.7331 | 4.5898 | -0.12392 | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 5.263 | 9.4816 | 4.4541 | -0.13844 | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 5.263 | 8.9742 | 4.1838 | -0.16483 | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 5.263 | 8.3552 | 3.8597 | -0.19181 | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 5.263 | 7.837 | 3.5931 | -0.20999 | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 5.263 | 7.4962 | 3.4201 | -0.21975 | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 5.263 | 7.2922 | 3.3173 | -0.22478 | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 5.263 | 7.1797 | 3.2609 | -0.22728 | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 5.263 | 7.1705 | 3.2563 | -0.22748 | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 5.263 | 7.3393 | 3.341 | -0.22367 | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 5.263 | 7.7741 | 3.5611 | -0.21192 | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 5.263 | 8.4374 | 3.9024 | -0.18856 | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 5.263 | 8.8902 | 4.1394 | -0.16883 | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 5.263 | 9.0183 | 4.2071 | -0.16269 | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 5.2577 | 9.0698 | 4.2344 | -0.16015 | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 5.2419 | 9.1025 | 4.2517 | -0.15852 | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 5.2262 | 9.1351 | 4.2691 | -0.15688 | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 5.2262 | 9.1667 | 4.2859 | -0.15527 | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 5.2367 | 9.1836 | 4.2948 | -0.15441 | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 5.2525 | 9.2532 | 4.3319 | -0.1508 | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 5.2577 | 9.454 | 4.4393 | -0.13997 | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 5.263 | 9.7607 | 4.6047 | -0.12227 | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 5.263 | 9.8853 | 4.6724 | -0.11468 | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 5.263 | 9.8491 | 4.6527 | -0.11691 | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 5.263 | 9.7331 | 4.5898 | -0.12392 | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 5.263 | 9.4816 | 4.4541 | -0.13844 | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 5.263 | 8.9742 | 4.1838 | -0.16483 | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 5.263 | 8.3552 | 3.8597 | -0.19181 | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 5.263 | 7.837 | 3.5931 | -0.20999 | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 10.526 | 7.4962 | 3.4201 | -0.21975 | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 10.526 | 7.2922 | 3.3173 | -0.22478 | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 10.526 | 7.1797 | 3.2609 | -0.22728 | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 10.526 | 7.1705 | 3.2563 | -0.22748 | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 10.526 | 7.3393 | 3.341 | -0.22367 | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 10.526 | 7.7741 | 3.5611 | -0.21192 | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 10.5049 | 8.4374 | 3.9024 | -0.18856 | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 10.2313 | 8.8902 | 4.1394 | -0.16883 | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 9.4102 | 9.0183 | 4.2071 | -0.16269 | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.284 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 8.284 | 9.0698 | 4.2344 | -0.16015 | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 7.1472 | 9.1025 | 4.2517 | -0.15852 | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 6.5156 | 9.1351 | 4.2691 | -0.15688 | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 6.7051 | 9.1667 | 4.2859 | -0.15527 | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 7.0103 | 9.1836 | 4.2948 | -0.15441 | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | very sunny | 10.526 | 7.884 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 7.884 | 9.2532 | 4.3319 | -0.1508 | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 8.9155 | 9.454 | 4.4393 | -0.13997 | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 9.8418 | 9.7607 | 4.6047 | -0.12227 | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 10.3786 | 9.8853 | 4.6724 | -0.11468 | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 10.5155 | 9.8491 | 4.6527 | -0.11691 | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 10.526 | 9.7331 | 4.5898 | -0.12392 | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 10.526 | 9.4816 | 4.4541 | -0.13844 | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 10.526 | 8.9742 | 4.1838 | -0.16483 | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 10.526 | 8.3552 | 3.8597 | -0.19181 | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 10.526 | 7.837 | 3.5931 | -0.20999 | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 10.526 | 7.4962 | 3.4201 | -0.21975 | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 10.526 | 7.2922 | 3.3173 | -0.22478 | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 10.526 | 7.1797 | 3.2609 | -0.22728 | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 10.526 | 7.1705 | 3.2563 | -0.22748 | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 10.526 | 7.3393 | 3.341 | -0.22367 | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 10.526 | 7.7741 | 3.5611 | -0.21192 | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 10.526 | 8.4374 | 3.9024 | -0.18856 | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 10.5155 | 8.8902 | 4.1394 | -0.16883 | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 10.4102 | 9.0183 | 4.2071 | -0.16269 | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 10.1892 | 9.0698 | 4.2344 | -0.16015 | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 9.9576 | 9.1025 | 4.2517 | -0.15852 | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 9.8313 | 9.1351 | 4.2691 | -0.15688 | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 9.9681 | 9.1667 | 4.2859 | -0.15527 | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 10.0313 | 9.1836 | 4.2948 | -0.15441 | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 10.2944 | 9.2532 | 4.3319 | -0.1508 | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 10.4734 | 9.454 | 4.4393 | -0.13997 | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 10.526 | 9.7607 | 4.6047 | -0.12227 | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 10.526 | 9.8853 | 4.6724 | -0.11468 | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 10.526 | 9.8491 | 4.6527 | -0.11691 | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 10.526 | 9.7331 | 4.5898 | -0.12392 | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 10.526 | 9.4816 | 4.4541 | -0.13844 | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 10.526 | 8.9742 | 4.1838 | -0.16483 | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 10.526 | 8.3552 | 3.8597 | -0.19181 | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 10.526 | 7.837 | 3.5931 | -0.20999 | -2.609%
1 | 7.716 | 3.737 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99874 | -2.9194 | 0.99874 | -2.9194 | 0.97 | -2.4 | 0.97 | -2.4 | -3.6772 | 10.526 | 7.4962 | 3.4201 | -0.21975 | -2.848%
2 | 7.517 | 3.6406 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -2.8406 | 1.0002 | -2.8406 | 0.97 | -2.2949 | 0.97 | -2.2949 | -3.8559 | 10.526 | 7.2922 | 3.3173 | -0.22478 | -2.99%
3 | 7.407 | 3.5874 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.001 | -2.7972 | 1.001 | -2.7972 | 0.97 | -2.237 | 0.97 | -2.237 | -3.9541 | 10.526 | 7.1797 | 3.2609 | -0.22728 | -3.068%
4 | 7.398 | 3.583 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0011 | -2.7936 | 1.0011 | -2.7936 | 0.97 | -2.2323 | 0.97 | -2.2323 | -3.9621 | 10.526 | 7.1705 | 3.2563 | -0.22748 | -3.075%
5 | 7.563 | 3.6629 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99987 | -2.8588 | 0.99987 | -2.8588 | 0.97 | -2.3192 | 0.97 | -2.3192 | -3.8148 | 10.526 | 7.3393 | 3.341 | -0.22367 | -2.957%
6 | 7.986 | 3.8678 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99675 | -3.0268 | 0.99675 | -3.0268 | 0.97 | -2.5431 | 0.97 | -2.5431 | -3.4321 | 10.526 | 7.7741 | 3.5611 | -0.21192 | -2.654%
7 | 8.626 | 4.1778 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99196 | -3.2832 | 0.99196 | -3.2832 | 0.97 | -2.8854 | 0.97 | -2.8854 | -2.8387 | 10.526 | 8.4374 | 3.9024 | -0.18856 | -2.186%
8 | 9.059 | 4.3875 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98868 | -3.4582 | 0.98868 | -3.4582 | 0.97 | -3.1195 | 0.97 | -3.1195 | -2.4272 | 10.526 | 8.8902 | 4.1394 | -0.16883 | -1.864%
9 | 9.181 | 4.4466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98775 | -3.5077 | 0.98775 | -3.5077 | 0.97 | -3.1859 | 0.97 | -3.1859 | -2.3097 | 10.526 | 9.0183 | 4.2071 | -0.16269 | -1.772%
10 | 9.23 | 4.4703 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.98738 | -3.5277 | 0.98738 | -3.5277 | 0.97 | -3.2125 | 0.97 | -3.2125 | -2.2623 | 10.5155 | 9.0698 | 4.2344 | -0.16015 | -1.735%
11 | 9.261 | 4.4853 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 5 | 0.98714 | -3.5403 | 0.98714 | -3.5403 | 0.97 | -3.2294 | 0.97 | -3.2294 | -2.2323 | 10.4839 | 9.1025 | 4.2517 | -0.15852 | -1.712%
12 | 9.292 | 4.5003 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.98691 | -3.5529 | 0.98691 | -3.5529 | 0.97 | -3.2463 | 0.97 | -3.2463 | -2.2022 | 10.4523 | 9.1351 | 4.2691 | -0.15688 | -1.688%
13 | 9.322 | 4.5149 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.98668 | -3.5651 | 0.98668 | -3.5651 | 0.97 | -3.2627 | 0.97 | -3.2627 | -2.1731 | 10.4523 | 9.1667 | 4.2859 | -0.15527 | -1.666%
14 | 9.338 | 4.5226 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 5 | 0.98655 | -3.5717 | 0.98655 | -3.5717 | 0.97 | -3.2714 | 0.97 | -3.2714 | -2.1575 | 10.4734 | 9.1836 | 4.2948 | -0.15441 | -1.654%
15 | 9.404 | 4.5546 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 5 | 0.98605 | -3.5986 | 0.98605 | -3.5986 | 0.97 | -3.3075 | 0.97 | -3.3075 | -2.0932 | 10.5049 | 9.2532 | 4.3319 | -0.1508 | -1.604%
16 | 9.594 | 4.6466 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.98459 | -3.6763 | 0.98459 | -3.6763 | 0.97 | -3.4116 | 0.97 | -3.4116 | -1.9069 | 10.5155 | 9.454 | 4.4393 | -0.13997 | -1.459%
17 | 9.883 | 4.7866 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98235 | -3.795 | 0.98235 | -3.795 | 0.97 | -3.5707 | 0.97 | -3.5707 | -1.6203 | 10.526 | 9.7607 | 4.6047 | -0.12227 | -1.237%
18 | 10 | 4.8432 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98144 | -3.8432 | 0.98144 | -3.8432 | 0.97 | -3.6354 | 0.97 | -3.6354 | -1.5031 | 10.526 | 9.8853 | 4.6724 | -0.11468 | -1.147%
19 | 9.966 | 4.8268 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98171 | -3.8292 | 0.98171 | -3.8292 | 0.97 | -3.6166 | 0.97 | -3.6166 | -1.5372 | 10.526 | 9.8491 | 4.6527 | -0.11691 | -1.173%
20 | 9.857 | 4.774 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98255 | -3.7843 | 0.98255 | -3.7843 | 0.97 | -3.5563 | 0.97 | -3.5563 | -1.6462 | 10.526 | 9.7331 | 4.5898 | -0.12392 | -1.257%
21 | 9.62 | 4.6592 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98439 | -3.6869 | 0.98439 | -3.6869 | 0.97 | -3.4259 | 0.97 | -3.4259 | -1.8813 | 10.526 | 9.4816 | 4.4541 | -0.13844 | -1.439%
22 | 9.139 | 4.4262 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.98807 | -3.4907 | 0.98807 | -3.4907 | 0.97 | -3.163 | 0.97 | -3.163 | -2.3502 | 10.526 | 8.9742 | 4.1838 | -0.16483 | -1.804%
23 | 8.547 | 4.1395 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99256 | -3.2513 | 0.99256 | -3.2513 | 0.97 | -2.843 | 0.97 | -2.843 | -2.913 | 10.526 | 8.3552 | 3.8597 | -0.19181 | -2.244%
24 | 8.047 | 3.8973 | 0.9 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99629 | -3.0511 | 0.99629 | -3.0511 | 0.97 | -2.5756 | 0.97 | -2.5756 | -3.3763 | 10.526 | 7.837 | 3.5931 | -0.20999 | -2.609%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0639 | 1.0267 | -0.93035 | 0.99578 | -2.9668 | -5.263 | 5.263 | 7.616 | 2.4396 | -0.10004 | -1.297%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.90316 | 0.99694 | -2.8842 | -5.263 | 5.263 | 7.4195 | 2.3768 | -0.097491 | -1.297%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.88815 | 0.99759 | -2.8386 | -5.263 | 5.263 | 7.3109 | 2.3421 | -0.096093 | -1.297%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.88692 | 0.99764 | -2.8349 | -5.263 | 5.263 | 7.302 | 2.3392 | -0.095977 | -1.297%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.027 | -0.90944 | 0.99667 | -2.9033 | -5.263 | 5.263 | 7.4649 | 2.3913 | -0.098076 | -1.297%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.96731 | 0.99418 | -3.0793 | -5.263 | 5.263 | 7.8826 | 2.5248 | -0.10345 | -1.295%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.0545 | 0.99048 | -3.3433 | -5.2525 | 5.2525 | 8.5154 | 2.7275 | -0.11059 | -1.282%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.025 | -1.1174 | 0.98821 | -3.528 | -5.1156 | 5.1156 | 8.9461 | 2.8671 | -0.11289 | -1.246%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0259 | -1.144 | 0.9885 | -3.5861 | -4.7051 | 4.7051 | 9.076 | 2.9148 | -0.10498 | -1.143%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.142 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0272 | -1.1642 | 0.9896 | -3.6163 | -4.142 | 4.142 | 9.1373 | 2.9429 | -0.092715 | -1.004%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0285 | -1.1849 | 0.99066 | -3.6504 | -3.5736 | 3.5736 | 9.1795 | 2.964 | -0.081503 | -0.8801%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0293 | -1.1963 | 0.99127 | -3.6673 | -3.2578 | 3.2578 | 9.2176 | 2.9811 | -0.074406 | -0.8007%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0291 | -1.1954 | 0.99102 | -3.6668 | -3.3525 | 3.3525 | 9.2468 | 2.9902 | -0.075229 | -0.807%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0287 | -1.194 | 0.99054 | -3.6712 | -3.5052 | 3.5052 | 9.2591 | 2.9918 | -0.078886 | -0.8448%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.942 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0274 | -1.1928 | 0.98905 | -3.6923 | -3.942 | 3.942 | 9.3144 | 3.0029 | -0.089597 | -0.9528%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0258 | -1.2069 | 0.9866 | -3.7651 | -4.4578 | 4.4578 | 9.4903 | 3.0514 | -0.10365 | -1.08%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0241 | -1.2368 | 0.98359 | -3.8853 | -4.9209 | 4.9209 | 9.7643 | 3.1312 | -0.11873 | -1.201%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0231 | -1.247 | 0.98217 | -3.9325 | -5.1893 | 5.1893 | 9.8731 | 3.1615 | -0.12695 | -1.269%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.023 | -1.2407 | 0.98221 | -3.9172 | -5.2577 | 5.2577 | 9.8377 | 3.149 | -0.12827 | -1.287%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0232 | -1.2254 | 0.98287 | -3.8704 | -5.263 | 5.263 | 9.73 | 3.1146 | -0.12704 | -1.289%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1925 | 0.98433 | -3.769 | -5.263 | 5.263 | 9.4959 | 3.0399 | -0.12406 | -1.29%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.1259 | 0.98727 | -3.5644 | -5.263 | 5.263 | 9.021 | 2.8883 | -0.11802 | -1.291%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0443 | 0.99084 | -3.3143 | -5.263 | 5.263 | 8.4365 | 2.7017 | -0.11055 | -1.293%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.97567 | 0.99382 | -3.1048 | -5.263 | 5.263 | 7.9428 | 2.544 | -0.10422 | -1.295%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0267 | -0.93035 | 0.99577 | -2.9668 | -5.263 | 5.263 | 7.616 | 2.4396 | -0.10002 | -1.296%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.90316 | 0.99694 | -2.8842 | -5.263 | 5.263 | 7.4195 | 2.3768 | -0.097491 | -1.297%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.88815 | 0.99759 | -2.8386 | -5.263 | 5.263 | 7.3109 | 2.3421 | -0.096093 | -1.297%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.88692 | 0.99764 | -2.8349 | -5.263 | 5.263 | 7.302 | 2.3392 | -0.095977 | -1.297%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.027 | -0.90944 | 0.99667 | -2.9033 | -5.263 | 5.263 | 7.4649 | 2.3913 | -0.098076 | -1.297%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.96731 | 0.99418 | -3.0793 | -5.263 | 5.263 | 7.8826 | 2.5248 | -0.10345 | -1.295%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.0552 | 0.99036 | -3.3476 | -5.263 | 5.263 | 8.5145 | 2.7266 | -0.11154 | -1.293%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0246 | -1.115 | 0.98777 | -3.5305 | -5.2577 | 5.2577 | 8.9421 | 2.8632 | -0.11689 | -1.29%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0245 | -1.1331 | 0.98716 | -3.5829 | -5.2051 | 5.2051 | 9.0638 | 2.9029 | -0.11719 | -1.276%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0248 | -1.1415 | 0.98722 | -3.6007 | -5.0946 | 5.0946 | 9.1155 | 2.9216 | -0.11448 | -1.24%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.025 | -1.1485 | 0.98733 | -3.6157 | -4.9788 | 4.9788 | 9.1488 | 2.934 | -0.11218 | -1.211%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0251 | -1.1543 | 0.9873 | -3.6298 | -4.9156 | 4.9156 | 9.1809 | 2.9452 | -0.11108 | -1.195%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0249 | -1.1568 | 0.98694 | -3.6415 | -4.9841 | 4.9841 | 9.209 | 2.9531 | -0.11302 | -1.212%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0248 | -1.1583 | 0.98676 | -3.6478 | -5.0156 | 5.0156 | 9.2241 | 2.9575 | -0.11394 | -1.22%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0243 | -1.1643 | 0.98603 | -3.6737 | -5.1472 | 5.1472 | 9.2862 | 2.9753 | -0.11781 | -1.253%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0238 | -1.1884 | 0.98464 | -3.7532 | -5.2367 | 5.2367 | 9.4717 | 3.0332 | -0.12226 | -1.274%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0232 | -1.229 | 0.98271 | -3.8815 | -5.263 | 5.263 | 9.7556 | 3.1227 | -0.12736 | -1.289%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.023 | -1.2453 | 0.98198 | -3.9317 | -5.263 | 5.263 | 9.8712 | 3.1596 | -0.12883 | -1.288%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.023 | -1.2406 | 0.98219 | -3.9171 | -5.263 | 5.263 | 9.8376 | 3.1489 | -0.1284 | -1.288%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0232 | -1.2254 | 0.98287 | -3.8704 | -5.263 | 5.263 | 9.73 | 3.1146 | -0.12704 | -1.289%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1925 | 0.98433 | -3.769 | -5.263 | 5.263 | 9.4959 | 3.0399 | -0.12406 | -1.29%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.1259 | 0.98727 | -3.5644 | -5.263 | 5.263 | 9.021 | 2.8883 | -0.11802 | -1.291%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0443 | 0.99084 | -3.3143 | -5.263 | 5.263 | 8.4365 | 2.7017 | -0.11055 | -1.293%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.97567 | 0.99382 | -3.1048 | -5.263 | 5.263 | 7.9428 | 2.544 | -0.10422 | -1.295%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0267 | -0.93035 | 0.99577 | -2.9668 | -5.263 | 5.263 | 7.616 | 2.4396 | -0.10002 | -1.296%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.027 | -0.90316 | 0.99694 | -2.8842 | -5.263 | 5.263 | 7.4195 | 2.3768 | -0.097491 | -1.297%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0272 | -0.88815 | 0.99759 | -2.8386 | -5.263 | 5.263 | 7.3109 | 2.3421 | -0.096093 | -1.297%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0272 | -0.88692 | 0.99764 | -2.8349 | -5.263 | 5.263 | 7.302 | 2.3392 | -0.095977 | -1.297%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.027 | -0.90944 | 0.99667 | -2.9033 | -5.263 | 5.263 | 7.4649 | 2.3913 | -0.098076 | -1.297%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0263 | -0.96731 | 0.99418 | -3.0793 | -5.263 | 5.263 | 7.8826 | 2.5248 | -0.10345 | -1.295%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0253 | -1.0552 | 0.99036 | -3.3476 | -5.263 | 5.263 | 8.5145 | 2.7266 | -0.11154 | -1.293%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0245 | -1.1149 | 0.98775 | -3.5304 | -5.263 | 5.263 | 8.942 | 2.8631 | -0.11701 | -1.292%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.2578 | 0.99998 | -3.6734 | 1.0243 | -1.1317 | 0.98701 | -3.5822 | -5.263 | 5.263 | 9.0625 | 2.9016 | -0.11854 | -1.291%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0243 | -1.1386 | 0.98673 | -3.603 | -5.2577 | 5.2577 | 9.111 | 2.9171 | -0.11904 | -1.29%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0243 | -1.1433 | 0.98658 | -3.6164 | -5.2419 | 5.2419 | 9.1419 | 2.9273 | -0.11905 | -1.286%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0243 | -1.1479 | 0.98643 | -3.6297 | -5.2262 | 5.2262 | 9.1729 | 2.9374 | -0.11907 | -1.281%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0242 | -1.1521 | 0.98625 | -3.6425 | -5.2262 | 5.2262 | 9.2026 | 2.9468 | -0.11944 | -1.281%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0242 | -1.153 | 0.98621 | -3.6443 | -5.2367 | 5.2367 | 9.2189 | 2.9524 | -0.11909 | -1.275%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0241 | -1.1618 | 0.98577 | -3.6721 | -5.2525 | 5.2525 | 9.2837 | 2.9729 | -0.12028 | -1.279%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0237 | -1.189 | 0.9845 | -3.758 | -5.2577 | 5.2577 | 9.4704 | 3.0318 | -0.12361 | -1.288%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0232 | -1.229 | 0.98271 | -3.8815 | -5.263 | 5.263 | 9.7556 | 3.1227 | -0.12736 | -1.289%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.023 | -1.2453 | 0.98198 | -3.9317 | -5.263 | 5.263 | 9.8712 | 3.1596 | -0.12883 | -1.288%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.023 | -1.2406 | 0.98219 | -3.9171 | -5.263 | 5.263 | 9.8376 | 3.1489 | -0.1284 | -1.288%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0232 | -1.2254 | 0.98287 | -3.8704 | -5.263 | 5.263 | 9.73 | 3.1146 | -0.12704 | -1.289%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.0236 | -1.1925 | 0.98433 | -3.769 | -5.263 | 5.263 | 9.4959 | 3.0399 | -0.12406 | -1.29%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0244 | -1.1259 | 0.98727 | -3.5644 | -5.263 | 5.263 | 9.021 | 2.8883 | -0.11802 | -1.291%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0254 | -1.0443 | 0.99084 | -3.3143 | -5.263 | 5.263 | 8.4365 | 2.7017 | -0.11055 | -1.293%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0262 | -0.97567 | 0.99382 | -3.1048 | -5.263 | 5.263 | 7.9428 | 2.544 | -0.10422 | -1.295%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0128 | -0.80449 | 0.9822 | -2.8808 | -10.526 | 10.526 | 7.5129 | 2.3405 | -0.20311 | -2.632%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.77724 | 0.98335 | -2.797 | -10.526 | 10.526 | 7.319 | 2.2804 | -0.19796 | -2.634%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.7622 | 0.98399 | -2.7507 | -10.526 | 10.526 | 7.2119 | 2.2472 | -0.19511 | -2.634%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.76097 | 0.98404 | -2.747 | -10.526 | 10.526 | 7.2031 | 2.2445 | -0.19488 | -2.634%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0131 | -0.78354 | 0.98309 | -2.8164 | -10.526 | 10.526 | 7.3638 | 2.2943 | -0.19915 | -2.633%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.84153 | 0.98062 | -2.9949 | -10.526 | 10.526 | 7.7759 | 2.422 | -0.2101 | -2.631%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.9301 | 0.97689 | -3.2674 | -10.5049 | 10.5049 | 8.3998 | 2.6155 | -0.22616 | -2.622%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0114 | -0.99632 | 0.97501 | -3.4563 | -10.2313 | 10.2313 | 8.8281 | 2.7522 | -0.23089 | -2.549%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0134 | -1.0324 | 0.97644 | -3.5184 | -9.4102 | 9.4102 | 8.9666 | 2.808 | -0.21444 | -2.336%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.284 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0164 | -1.0655 | 0.9791 | -3.5527 | -8.284 | 8.284 | 9.0414 | 2.8492 | -0.18863 | -2.044%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0192 | -1.0996 | 0.98167 | -3.5939 | -7.1472 | 7.1472 | 9.097 | 2.8833 | -0.16403 | -1.771%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0209 | -1.1184 | 0.98311 | -3.6146 | -6.5156 | 6.5156 | 9.1424 | 2.9075 | -0.14963 | -1.61%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0204 | -1.1158 | 0.9826 | -3.6147 | -6.7051 | 6.7051 | 9.1689 | 2.9139 | -0.15312 | -1.643%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0196 | -1.1107 | 0.98173 | -3.6168 | -7.0103 | 7.0103 | 9.1775 | 2.9119 | -0.16053 | -1.719%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.884 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1055 | 0.97923 | -3.648 | -7.7578 | 7.884 | 9.2229 | 2.9134 | -0.18112 | -1.926%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1319 | 0.97807 | -3.7297 | -7.7583 | 8.9155 | 9.4093 | 2.9719 | -0.18472 | -1.925%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1721 | 0.97629 | -3.8545 | -7.759 | 9.8418 | 9.6928 | 3.061 | -0.19019 | -1.924%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1884 | 0.97557 | -3.9051 | -7.7593 | 10.3786 | 9.8076 | 3.097 | -0.1924 | -1.924%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1836 | 0.97578 | -3.8904 | -7.7592 | 10.5155 | 9.7742 | 3.0865 | -0.19176 | -1.924%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1684 | 0.97645 | -3.8432 | -7.7589 | 10.526 | 9.6673 | 3.053 | -0.18969 | -1.924%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1355 | 0.97791 | -3.7409 | -7.7583 | 10.526 | 9.4348 | 2.9799 | -0.18521 | -1.925%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -1.0005 | 0.97376 | -3.4871 | -10.526 | 10.526 | 8.8992 | 2.7696 | -0.23985 | -2.624%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0115 | -0.91871 | 0.9773 | -3.2334 | -10.526 | 10.526 | 8.3224 | 2.5912 | -0.2246 | -2.628%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.8499 | 0.98026 | -3.0208 | -10.526 | 10.526 | 7.8353 | 2.4404 | -0.21168 | -2.631%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0128 | -0.80449 | 0.9822 | -2.8808 | -10.526 | 10.526 | 7.5129 | 2.3405 | -0.20312 | -2.632%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.77724 | 0.98335 | -2.797 | -10.526 | 10.526 | 7.319 | 2.2804 | -0.19796 | -2.634%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.7622 | 0.98399 | -2.7507 | -10.526 | 10.526 | 7.2119 | 2.2472 | -0.19511 | -2.634%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.76097 | 0.98404 | -2.747 | -10.526 | 10.526 | 7.2031 | 2.2445 | -0.19488 | -2.634%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0131 | -0.78354 | 0.98309 | -2.8164 | -10.526 | 10.526 | 7.3638 | 2.2943 | -0.19915 | -2.633%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.84153 | 0.98062 | -2.9949 | -10.526 | 10.526 | 7.7759 | 2.422 | -0.2101 | -2.631%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.9296 | 0.97683 | -3.2672 | -10.526 | 10.526 | 8.3994 | 2.615 | -0.22663 | -2.627%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0107 | -0.98967 | 0.97427 | -3.4529 | -10.5155 | 10.5155 | 8.8215 | 2.7457 | -0.23754 | -2.622%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0108 | -1.009 | 0.97381 | -3.5066 | -10.4102 | 10.4102 | 8.9428 | 2.7849 | -0.23818 | -2.594%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0113 | -1.021 | 0.97409 | -3.5303 | -10.1892 | 10.1892 | 8.9958 | 2.8048 | -0.23415 | -2.537%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0118 | -1.0307 | 0.97451 | -3.5464 | -9.9576 | 9.9576 | 9.0316 | 2.8196 | -0.22938 | -2.477%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0176 | -1.0899 | 0.97991 | -3.6 | -7.7574 | 9.8313 | 9.113 | 2.8788 | -0.17899 | -1.926%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0175 | -1.0941 | 0.97973 | -3.6128 | -7.7575 | 9.9681 | 9.1424 | 2.8881 | -0.17956 | -1.926%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0963 | 0.97963 | -3.6197 | -7.7576 | 10.0313 | 9.1581 | 2.893 | -0.17987 | -1.926%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1055 | 0.97923 | -3.648 | -7.7578 | 10.2944 | 9.2229 | 2.9134 | -0.18112 | -1.926%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1319 | 0.97807 | -3.7297 | -7.7583 | 10.4734 | 9.4093 | 2.9719 | -0.18472 | -1.925%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1721 | 0.97629 | -3.8545 | -7.759 | 10.526 | 9.6928 | 3.061 | -0.19019 | -1.924%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1884 | 0.97557 | -3.9051 | -7.7593 | 10.526 | 9.8076 | 3.097 | -0.1924 | -1.924%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1836 | 0.97578 | -3.8904 | -7.7592 | 10.526 | 9.7742 | 3.0865 | -0.19176 | -1.924%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1684 | 0.97645 | -3.8432 | -7.7589 | 10.526 | 9.6673 | 3.053 | -0.18969 | -1.924%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1355 | 0.97791 | -3.7409 | -7.7583 | 10.526 | 9.4348 | 2.9799 | -0.18521 | -1.925%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -1.0005 | 0.97376 | -3.4871 | -10.526 | 10.526 | 8.8992 | 2.7696 | -0.23985 | -2.624%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0115 | -0.91871 | 0.9773 | -3.2334 | -10.526 | 10.526 | 8.3224 | 2.5912 | -0.2246 | -2.628%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.8499 | 0.98026 | -3.0208 | -10.526 | 10.526 | 7.8353 | 2.4404 | -0.21168 | -2.631%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0402 | -1.0561 | 1.0088 | -3.0638 | 1.0128 | -0.80449 | 0.9822 | -2.8808 | -10.526 | 10.526 | 7.5129 | 2.3405 | -0.20312 | -2.632%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0405 | -1.0289 | 1.01 | -2.982 | 1.0131 | -0.77724 | 0.98335 | -2.797 | -10.526 | 10.526 | 7.319 | 2.2804 | -0.19796 | -2.634%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0138 | 1.0107 | -2.9368 | 1.0133 | -0.7622 | 0.98399 | -2.7507 | -10.526 | 10.526 | 7.2119 | 2.2472 | -0.19511 | -2.634%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0407 | -1.0126 | 1.0107 | -2.9331 | 1.0133 | -0.76097 | 0.98404 | -2.747 | -10.526 | 10.526 | 7.2031 | 2.2445 | -0.19488 | -2.634%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0404 | -1.0352 | 1.0097 | -3.0009 | 1.0131 | -0.78354 | 0.98309 | -2.8164 | -10.526 | 10.526 | 7.3638 | 2.2943 | -0.19915 | -2.633%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0397 | -1.0931 | 1.0072 | -3.1753 | 1.0124 | -0.84153 | 0.98062 | -2.9949 | -10.526 | 10.526 | 7.7759 | 2.422 | -0.2101 | -2.631%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0387 | -1.1812 | 1.0034 | -3.441 | 1.0114 | -0.9296 | 0.97683 | -3.2672 | -10.526 | 10.526 | 8.3994 | 2.615 | -0.22663 | -2.627%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.038 | -1.241 | 1.0007 | -3.6221 | 1.0106 | -0.98943 | 0.97424 | -3.4527 | -10.526 | 10.526 | 8.8212 | 2.7455 | -0.23779 | -2.625%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.2579 | 0.99998 | -3.6733 | 1.0104 | -1.0063 | 0.9735 | -3.5052 | -10.526 | 10.526 | 8.9401 | 2.7822 | -0.24093 | -2.624%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0377 | -1.2646 | 0.99968 | -3.6939 | 1.0104 | -1.0134 | 0.97324 | -3.5265 | -10.5155 | 10.5155 | 8.9881 | 2.7972 | -0.24194 | -2.621%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 3 | 1.0376 | -1.2689 | 0.99949 | -3.707 | 1.0104 | -1.0184 | 0.97313 | -3.5402 | -10.4839 | 10.4839 | 9.019 | 2.8073 | -0.24198 | -2.613%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0376 | -1.2732 | 0.9993 | -3.72 | 1.0176 | -1.0899 | 0.97991 | -3.6 | -7.7574 | 10.4523 | 9.113 | 2.8788 | -0.17899 | -1.926%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0375 | -1.2774 | 0.99911 | -3.7327 | 1.0175 | -1.0941 | 0.97973 | -3.6128 | -7.7575 | 10.4523 | 9.1424 | 2.8881 | -0.17956 | -1.926%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 3 | 1.0375 | -1.2796 | 0.99901 | -3.7394 | 1.0175 | -1.0963 | 0.97963 | -3.6197 | -7.7576 | 10.4734 | 9.1581 | 2.893 | -0.17987 | -1.926%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 3 | 1.0374 | -1.2887 | 0.99861 | -3.7672 | 1.0174 | -1.1055 | 0.97923 | -3.648 | -7.7578 | 10.5049 | 9.2229 | 2.9134 | -0.18112 | -1.926%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0371 | -1.3151 | 0.99743 | -3.8474 | 1.0171 | -1.1319 | 0.97807 | -3.7297 | -7.7583 | 10.5155 | 9.4093 | 2.9719 | -0.18472 | -1.925%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3553 | 0.99563 | -3.9698 | 1.0166 | -1.1721 | 0.97629 | -3.8545 | -7.759 | 10.526 | 9.6928 | 3.061 | -0.19019 | -1.924%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3716 | 0.9949 | -4.0195 | 1.0164 | -1.1884 | 0.97557 | -3.9051 | -7.7593 | 10.526 | 9.8076 | 3.097 | -0.1924 | -1.924%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0364 | -1.3668 | 0.99511 | -4.0051 | 1.0164 | -1.1836 | 0.97578 | -3.8904 | -7.7592 | 10.526 | 9.7742 | 3.0865 | -0.19176 | -1.924%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0366 | -1.3517 | 0.99579 | -3.9588 | 1.0166 | -1.1684 | 0.97645 | -3.8432 | -7.7589 | 10.526 | 9.6673 | 3.053 | -0.18969 | -1.924%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.037 | -1.3187 | 0.99727 | -3.8584 | 1.017 | -1.1355 | 0.97791 | -3.7409 | -7.7583 | 10.526 | 9.4348 | 2.9799 | -0.18521 | -1.925%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0378 | -1.252 | 1.0002 | -3.6557 | 1.0105 | -1.0005 | 0.97376 | -3.4871 | -10.526 | 10.526 | 8.8992 | 2.7696 | -0.23985 | -2.624%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0388 | -1.1703 | 1.0038 | -3.4081 | 1.0115 | -0.91871 | 0.9773 | -3.2334 | -10.526 | 10.526 | 8.3224 | 2.5912 | -0.2246 | -2.628%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0396 | -1.1015 | 1.0069 | -3.2005 | 1.0123 | -0.8499 | 0.98026 | -3.0208 | -10.526 | 10.526 | 7.8353 | 2.4404 | -0.21168 | -2.631%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99673 | -1.606 | 0.98157 | -2.6607 | -5.263 | 5.263 | 7.5082 | 2.336 | -0.20784 | -2.694%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99749 | -1.5523 | 0.98274 | -2.5778 | -5.263 | 5.263 | 7.3145 | 2.2761 | -0.20252 | -2.694%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.9979 | -1.5227 | 0.98338 | -2.532 | -5.263 | 5.263 | 7.2074 | 2.2429 | -0.19958 | -2.694%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99793 | -1.5203 | 0.98343 | -2.5283 | -5.263 | 5.263 | 7.1987 | 2.2402 | -0.19934 | -2.694%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99731 | -1.5647 | 0.98247 | -2.5969 | -5.263 | 5.263 | 7.3593 | 2.2899 | -0.20375 | -2.694%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99571 | -1.679 | 0.97998 | -2.7735 | -5.263 | 5.263 | 7.7709 | 2.4172 | -0.21505 | -2.693%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99331 | -1.8537 | 0.97624 | -3.0434 | -5.2525 | 5.2525 | 8.3943 | 2.6101 | -0.23166 | -2.686%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99236 | -1.983 | 0.97437 | -3.2362 | -5.1156 | 5.1156 | 8.8224 | 2.7466 | -0.23662 | -2.612%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99413 | -2.0495 | 0.97585 | -3.3162 | -4.7051 | 4.7051 | 8.9612 | 2.8028 | -0.21978 | -2.394%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.142 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8432 | 4.142 | 9.0495 | 2.8571 | -0.18049 | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99979 | -2.17 | 0.98123 | -3.4409 | -3.5736 | 3.5736 | 9.0929 | 2.8794 | -0.16807 | -1.815%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 1.0014 | -2.2035 | 0.98271 | -3.4754 | -3.2578 | 3.2578 | 9.1387 | 2.9039 | -0.15331 | -1.65%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 1.0009 | -2.1988 | 0.98219 | -3.472 | -3.3525 | 3.3525 | 9.1651 | 2.9102 | -0.15687 | -1.683%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 1 | -2.1904 | 0.9813 | -3.4673 | -3.5052 | 3.5052 | 9.1735 | 2.9081 | -0.16446 | -1.761%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.942 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 3.942 | 9.2201 | 2.9106 | -0.1839 | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 4.4578 | 9.4064 | 2.9691 | -0.18761 | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 4.9209 | 9.6897 | 3.058 | -0.19327 | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 5.1893 | 9.8044 | 3.0939 | -0.19556 | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 5.2577 | 9.7711 | 3.0835 | -0.19489 | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 5.263 | 9.6642 | 3.05 | -0.19276 | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 5.263 | 9.4319 | 2.9771 | -0.18812 | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99124 | -1.993 | 0.97309 | -3.2601 | -5.263 | 5.263 | 8.8932 | 2.7638 | -0.24582 | -2.69%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99355 | -1.8313 | 0.97665 | -3.0093 | -5.263 | 5.263 | 8.317 | 2.5859 | -0.23004 | -2.691%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99548 | -1.6956 | 0.97962 | -2.799 | -5.263 | 5.263 | 7.8303 | 2.4356 | -0.21669 | -2.693%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99673 | -1.606 | 0.98157 | -2.6607 | -5.263 | 5.263 | 7.5082 | 2.336 | -0.20784 | -2.694%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99749 | -1.5523 | 0.98274 | -2.5778 | -5.263 | 5.263 | 7.3145 | 2.2761 | -0.20252 | -2.694%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.9979 | -1.5227 | 0.98338 | -2.532 | -5.263 | 5.263 | 7.2074 | 2.2429 | -0.19958 | -2.694%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99793 | -1.5203 | 0.98343 | -2.5283 | -5.263 | 5.263 | 7.1987 | 2.2402 | -0.19934 | -2.694%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99731 | -1.5647 | 0.98247 | -2.5969 | -5.263 | 5.263 | 7.3593 | 2.2899 | -0.20375 | -2.694%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99571 | -1.679 | 0.97998 | -2.7735 | -5.263 | 5.263 | 7.7709 | 2.4172 | -0.21505 | -2.693%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99325 | -1.8528 | 0.97618 | -3.0426 | -5.263 | 5.263 | 8.3939 | 2.6097 | -0.23214 | -2.691%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99159 | -1.9715 | 0.9736 | -3.2264 | -5.2577 | 5.2577 | 8.8156 | 2.74 | -0.24344 | -2.687%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.9914 | -2.0091 | 0.97315 | -3.2819 | -5.2051 | 5.2051 | 8.9369 | 2.7791 | -0.24413 | -2.659%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8432 | 5.0946 | 9.0495 | 2.8571 | -0.18049 | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 4.9788 | 9.0799 | 2.8666 | -0.1811 | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 4.9156 | 9.1103 | 2.8762 | -0.1817 | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 4.9841 | 9.1397 | 2.8854 | -0.18229 | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 5.0156 | 9.1554 | 2.8903 | -0.1826 | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 5.1472 | 9.2201 | 2.9106 | -0.18389 | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 5.2367 | 9.4064 | 2.9691 | -0.18761 | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 5.263 | 9.6897 | 3.058 | -0.19327 | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 5.263 | 9.8044 | 3.0939 | -0.19556 | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 5.263 | 9.7711 | 3.0835 | -0.19489 | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 5.263 | 9.6642 | 3.05 | -0.19276 | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 5.263 | 9.4319 | 2.9771 | -0.18812 | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99124 | -1.993 | 0.97309 | -3.2601 | -5.263 | 5.263 | 8.8932 | 2.7638 | -0.24582 | -2.69%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99355 | -1.8313 | 0.97665 | -3.0093 | -5.263 | 5.263 | 8.317 | 2.5859 | -0.23004 | -2.691%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99548 | -1.6956 | 0.97962 | -2.799 | -5.263 | 5.263 | 7.8303 | 2.4356 | -0.21669 | -2.693%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99673 | -1.606 | 0.98157 | -2.6607 | -5.263 | 5.263 | 7.5082 | 2.336 | -0.20784 | -2.694%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.99749 | -1.5523 | 0.98274 | -2.5778 | -5.263 | 5.263 | 7.3145 | 2.2761 | -0.20252 | -2.694%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0255 | -1.9617 | 1.0107 | -2.9368 | 0.9979 | -1.5227 | 0.98338 | -2.532 | -5.263 | 5.263 | 7.2074 | 2.2429 | -0.19958 | -2.694%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.99793 | -1.5203 | 0.98343 | -2.5283 | -5.263 | 5.263 | 7.1987 | 2.2402 | -0.19934 | -2.694%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.99731 | -1.5647 | 0.98247 | -2.5969 | -5.263 | 5.263 | 7.3593 | 2.2899 | -0.20375 | -2.694%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99571 | -1.679 | 0.97998 | -2.7735 | -5.263 | 5.263 | 7.7709 | 2.4172 | -0.21505 | -2.693%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99325 | -1.8528 | 0.97618 | -3.0426 | -5.263 | 5.263 | 8.3939 | 2.6097 | -0.23214 | -2.691%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0191 | -2.4103 | 1.0007 | -3.6221 | 0.99156 | -1.9711 | 0.97358 | -3.2261 | -5.263 | 5.263 | 8.8153 | 2.7398 | -0.24369 | -2.69%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.99108 | -2.0045 | 0.97284 | -3.278 | -5.263 | 5.263 | 8.9341 | 2.7764 | -0.24694 | -2.69%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 5.2577 | 9.0495 | 2.8571 | -0.18049 | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 5.2419 | 9.0799 | 2.8666 | -0.1811 | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 5.2262 | 9.1103 | 2.8762 | -0.1817 | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 5.2262 | 9.1397 | 2.8854 | -0.18229 | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 5.2367 | 9.1554 | 2.8903 | -0.1826 | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 5.2525 | 9.2201 | 2.9106 | -0.18389 | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 5.2577 | 9.4064 | 2.9691 | -0.18761 | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 5.263 | 9.6897 | 3.058 | -0.19327 | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 5.263 | 9.8044 | 3.0939 | -0.19556 | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 5.263 | 9.7711 | 3.0835 | -0.19489 | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 5.263 | 9.6642 | 3.05 | -0.19276 | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 5.263 | 9.4319 | 2.9771 | -0.18812 | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.99124 | -1.993 | 0.97309 | -3.2601 | -5.263 | 5.263 | 8.8932 | 2.7638 | -0.24582 | -2.69%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99355 | -1.8313 | 0.97665 | -3.0093 | -5.263 | 5.263 | 8.317 | 2.5859 | -0.23004 | -2.691%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.99548 | -1.6956 | 0.97962 | -2.799 | -5.263 | 5.263 | 7.8303 | 2.4356 | -0.21669 | -2.693%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5706 | 0.97922 | -2.6295 | -5.697 | 10.526 | 7.4904 | 2.319 | -0.22556 | -2.923%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3594 | 0.97052 | -2.4027 | -7.5155 | 10.526 | 7.225 | 2.1906 | -0.29202 | -3.885%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3299 | 0.97116 | -2.3568 | -7.5143 | 10.526 | 7.1193 | 2.1588 | -0.28774 | -3.885%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3274 | 0.97122 | -2.353 | -7.5142 | 10.526 | 7.1106 | 2.1562 | -0.28739 | -3.885%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3719 | 0.97025 | -2.422 | -7.5154 | 10.526 | 7.2692 | 2.2039 | -0.2938 | -3.885%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6436 | 0.97763 | -2.7425 | -5.698 | 10.526 | 7.7525 | 2.3996 | -0.23345 | -2.923%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8173 | 0.97381 | -3.012 | -5.7018 | 10.5049 | 8.3738 | 2.5903 | -0.25218 | -2.923%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9354 | 0.9712 | -3.1957 | -5.7039 | 10.2313 | 8.7942 | 2.7192 | -0.26484 | -2.924%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9688 | 0.97045 | -3.2477 | -5.7045 | 9.4102 | 8.9126 | 2.7555 | -0.26841 | -2.924%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.284 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 8.284 | 9.0495 | 2.8571 | -0.18049 | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 7.1472 | 9.0799 | 2.8666 | -0.1811 | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 6.5156 | 9.1103 | 2.8762 | -0.1817 | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 6.7051 | 9.1397 | 2.8854 | -0.18229 | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 7.0103 | 9.1554 | 2.8903 | -0.1826 | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.884 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 7.884 | 9.2201 | 2.9106 | -0.18389 | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 8.9155 | 9.4064 | 2.9691 | -0.18761 | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 9.8418 | 9.6897 | 3.058 | -0.19327 | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 10.3786 | 9.8044 | 3.0939 | -0.19556 | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 10.5155 | 9.7711 | 3.0835 | -0.19489 | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 10.526 | 9.6642 | 3.05 | -0.19276 | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 10.526 | 9.4319 | 2.9771 | -0.18812 | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.9573 | 0.97071 | -3.2298 | -5.7044 | 10.526 | 8.8718 | 2.743 | -0.26718 | -2.924%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7958 | 0.97428 | -2.9786 | -5.7013 | 10.526 | 8.2971 | 2.5668 | -0.24987 | -2.923%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6601 | 0.97727 | -2.7681 | -5.6987 | 10.526 | 7.8118 | 2.4177 | -0.23524 | -2.923%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5706 | 0.97922 | -2.6296 | -5.697 | 10.526 | 7.4904 | 2.319 | -0.22556 | -2.923%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3594 | 0.97052 | -2.4027 | -7.5155 | 10.526 | 7.225 | 2.1906 | -0.29202 | -3.885%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3299 | 0.97116 | -2.3568 | -7.5143 | 10.526 | 7.1193 | 2.1588 | -0.28774 | -3.885%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3274 | 0.97122 | -2.353 | -7.5142 | 10.526 | 7.1106 | 2.1562 | -0.28739 | -3.885%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3719 | 0.97025 | -2.422 | -7.5154 | 10.526 | 7.2692 | 2.2039 | -0.2938 | -3.885%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6436 | 0.97763 | -2.7425 | -5.698 | 10.526 | 7.7525 | 2.3996 | -0.23345 | -2.923%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8173 | 0.97381 | -3.012 | -5.7018 | 10.526 | 8.3738 | 2.5903 | -0.25218 | -2.923%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9354 | 0.9712 | -3.1957 | -5.7039 | 10.5155 | 8.7942 | 2.7192 | -0.26484 | -2.924%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9688 | 0.97045 | -3.2477 | -5.7045 | 10.4102 | 8.9126 | 2.7555 | -0.26841 | -2.924%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 10.1892 | 9.0495 | 2.8571 | -0.18049 | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 9.9576 | 9.0799 | 2.8666 | -0.1811 | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 9.8313 | 9.1103 | 2.8762 | -0.1817 | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 9.9681 | 9.1397 | 2.8854 | -0.18229 | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 10.0313 | 9.1554 | 2.8903 | -0.1826 | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 10.2944 | 9.2201 | 2.9106 | -0.18389 | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 10.4734 | 9.4064 | 2.9691 | -0.18761 | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 10.526 | 9.6897 | 3.058 | -0.19327 | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 10.526 | 9.8044 | 3.0939 | -0.19556 | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 10.526 | 9.7711 | 3.0835 | -0.19489 | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 10.526 | 9.6642 | 3.05 | -0.19276 | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 10.526 | 9.4319 | 2.9771 | -0.18812 | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.9573 | 0.97071 | -3.2298 | -5.7044 | 10.526 | 8.8718 | 2.743 | -0.26718 | -2.924%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7958 | 0.97428 | -2.9786 | -5.7013 | 10.526 | 8.2971 | 2.5668 | -0.24987 | -2.923%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6601 | 0.97727 | -2.7681 | -5.6987 | 10.526 | 7.8118 | 2.4177 | -0.23524 | -2.923%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0244 | -2.0451 | 1.0088 | -3.0638 | 0.99436 | -1.5706 | 0.97922 | -2.6296 | -5.697 | 10.526 | 7.4904 | 2.319 | -0.22556 | -2.923%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -1.9914 | 1.01 | -2.982 | 0.98512 | -1.3594 | 0.97052 | -2.4027 | -7.5155 | 10.526 | 7.225 | 2.1906 | -0.29202 | -3.885%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0255 | -1.9618 | 1.0107 | -2.9368 | 0.98554 | -1.3299 | 0.97116 | -2.3568 | -7.5143 | 10.526 | 7.1193 | 2.1588 | -0.28774 | -3.885%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0256 | -1.9593 | 1.0107 | -2.9331 | 0.98558 | -1.3274 | 0.97122 | -2.353 | -7.5142 | 10.526 | 7.1106 | 2.1562 | -0.28739 | -3.885%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0249 | -2.0038 | 1.0097 | -3.0009 | 0.98495 | -1.3719 | 0.97025 | -2.422 | -7.5154 | 10.526 | 7.2692 | 2.2039 | -0.2938 | -3.885%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0233 | -2.1182 | 1.0072 | -3.1753 | 0.99333 | -1.6436 | 0.97763 | -2.7425 | -5.698 | 10.526 | 7.7525 | 2.3996 | -0.23345 | -2.923%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0209 | -2.292 | 1.0034 | -3.441 | 0.99085 | -1.8173 | 0.97381 | -3.012 | -5.7018 | 10.526 | 8.3738 | 2.5903 | -0.25218 | -2.923%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0192 | -2.4103 | 1.0007 | -3.6221 | 0.98915 | -1.9354 | 0.9712 | -3.1957 | -5.7039 | 10.526 | 8.7942 | 2.7192 | -0.26484 | -2.924%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0187 | -2.4437 | 0.99998 | -3.6734 | 0.98867 | -1.9688 | 0.97045 | -3.2477 | -5.7045 | 10.526 | 8.9126 | 2.7555 | -0.26841 | -2.924%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0185 | -2.4571 | 0.99968 | -3.694 | 0.99847 | -2.1402 | 0.98 | -3.4096 | -3.8431 | 10.5155 | 9.0495 | 2.8571 | -0.18049 | -1.955%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 4 | 1.0183 | -2.4656 | 0.99949 | -3.707 | 0.99835 | -2.1487 | 0.97981 | -3.4227 | -3.8433 | 10.4839 | 9.0799 | 2.8666 | -0.1811 | -1.955%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0182 | -2.4741 | 0.9993 | -3.72 | 0.99823 | -2.1572 | 0.97962 | -3.4359 | -3.8435 | 10.4523 | 9.1103 | 2.8762 | -0.1817 | -1.955%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0181 | -2.4823 | 0.99911 | -3.7327 | 0.99811 | -2.1654 | 0.97943 | -3.4486 | -3.8435 | 10.4523 | 9.1397 | 2.8854 | -0.18229 | -1.955%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 4 | 1.018 | -2.4867 | 0.99901 | -3.7394 | 0.99804 | -2.1698 | 0.97933 | -3.4554 | -3.8436 | 10.4734 | 9.1554 | 2.8903 | -0.1826 | -1.956%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 4 | 1.0178 | -2.5048 | 0.99861 | -3.7672 | 0.99778 | -2.1879 | 0.97893 | -3.4835 | -3.8438 | 10.5049 | 9.2201 | 2.9106 | -0.18389 | -1.955%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.017 | -2.5571 | 0.99743 | -3.8474 | 0.99702 | -2.2401 | 0.97776 | -3.5645 | -3.8445 | 10.5155 | 9.4064 | 2.9691 | -0.18761 | -1.956%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0159 | -2.6367 | 0.99563 | -3.9698 | 0.99586 | -2.3197 | 0.97598 | -3.6881 | -3.8455 | 10.526 | 9.6897 | 3.058 | -0.19327 | -1.956%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0154 | -2.669 | 0.9949 | -4.0195 | 0.99539 | -2.352 | 0.97525 | -3.7383 | -3.8459 | 10.526 | 9.8044 | 3.0939 | -0.19556 | -1.956%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0155 | -2.6596 | 0.99511 | -4.0051 | 0.99552 | -2.3426 | 0.97546 | -3.7237 | -3.8458 | 10.526 | 9.7711 | 3.0835 | -0.19489 | -1.956%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.016 | -2.6295 | 0.99579 | -3.9588 | 0.99596 | -2.3125 | 0.97614 | -3.677 | -3.8454 | 10.526 | 9.6642 | 3.05 | -0.19276 | -1.956%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0169 | -2.5642 | 0.99727 | -3.8584 | 0.99692 | -2.2472 | 0.9776 | -3.5756 | -3.8446 | 10.526 | 9.4319 | 2.9771 | -0.18812 | -1.956%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0188 | -2.4322 | 1.0002 | -3.6557 | 0.98883 | -1.9573 | 0.97071 | -3.2298 | -5.7044 | 10.526 | 8.8718 | 2.743 | -0.26718 | -2.924%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0212 | -2.2705 | 1.0038 | -3.4081 | 0.99116 | -1.7958 | 0.97428 | -2.9786 | -5.7013 | 10.526 | 8.2971 | 2.5668 | -0.24987 | -2.923%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0231 | -2.1347 | 1.0069 | -3.2005 | 0.9931 | -1.6601 | 0.97727 | -2.7681 | -5.6987 | 10.526 | 7.8118 | 2.4177 | -0.23524 | -2.923%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0088 | -3.0638 | 1.0088 | -3.0638 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 5.263 | 7.4211 | 2.2527 | -0.29491 | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 5.263 | 7.2212 | 2.187 | -0.29583 | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 5.263 | 7.1109 | 2.1509 | -0.29611 | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 5.263 | 7.1019 | 2.1479 | -0.29613 | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 5.263 | 7.2673 | 2.2021 | -0.29567 | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 5.263 | 7.6931 | 2.3425 | -0.2929 | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 5.2525 | 8.3417 | 2.5593 | -0.28433 | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 5.1156 | 8.7835 | 2.7089 | -0.27545 | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 4.7051 | 8.9085 | 2.7515 | -0.2725 | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.142 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 4.142 | 8.9587 | 2.7687 | -0.27125 | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97143 | -3.195 | 0.97143 | -3.195 | -3.5736 | 3.5736 | 9.0036 | 2.7923 | -0.25744 | -2.78%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97383 | -3.2509 | 0.97383 | -3.2509 | -3.2578 | 3.2578 | 9.0573 | 2.8245 | -0.23469 | -2.526%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97287 | -3.251 | 0.97287 | -3.251 | -3.3525 | 3.3525 | 9.0794 | 2.8266 | -0.24259 | -2.602%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97152 | -3.2373 | 0.97152 | -3.2373 | -3.5052 | 3.5052 | 9.0835 | 2.8202 | -0.25449 | -2.725%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 5.263 | 3.942 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 3.942 | 9.1374 | 2.83 | -0.26657 | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 4.4578 | 9.333 | 2.8974 | -0.26098 | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 4.9209 | 9.6315 | 3.0008 | -0.25152 | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 5.1893 | 9.7526 | 3.043 | -0.24735 | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 5.2577 | 9.7174 | 3.0307 | -0.24858 | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 5.263 | 9.6046 | 2.9915 | -0.25241 | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 5.263 | 9.3598 | 2.9066 | -0.26018 | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 5.263 | 8.8655 | 2.7369 | -0.27354 | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 5.263 | 8.2613 | 2.5322 | -0.28567 | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 5.263 | 7.7547 | 2.363 | -0.29231 | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 5.263 | 7.4211 | 2.2527 | -0.29493 | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 5.263 | 7.2212 | 2.187 | -0.29583 | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 5.263 | 7.1109 | 2.1509 | -0.29611 | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 5.263 | 7.1019 | 2.1479 | -0.29613 | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 5.263 | 7.2673 | 2.2021 | -0.29567 | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 5.263 | 7.6931 | 2.3425 | -0.2929 | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 5.263 | 8.3417 | 2.5593 | -0.28433 | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 5.2577 | 8.7835 | 2.7089 | -0.27545 | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 5.2051 | 8.9085 | 2.7515 | -0.2725 | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 5.0946 | 8.9587 | 2.7687 | -0.27125 | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 4.9788 | 8.9906 | 2.7796 | -0.27045 | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 4.9156 | 9.0224 | 2.7905 | -0.26963 | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 4.9841 | 9.0532 | 2.8011 | -0.26883 | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 5.0156 | 9.0696 | 2.8067 | -0.2684 | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 5.1472 | 9.1374 | 2.83 | -0.26657 | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 5.2367 | 9.333 | 2.8974 | -0.26098 | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 5.263 | 9.6315 | 3.0008 | -0.25152 | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 5.263 | 9.7526 | 3.043 | -0.24735 | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 5.263 | 9.7174 | 3.0307 | -0.24858 | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 5.263 | 9.6046 | 2.9915 | -0.25241 | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 5.263 | 9.3598 | 2.9066 | -0.26018 | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 5.263 | 8.8655 | 2.7369 | -0.27354 | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 5.263 | 8.2613 | 2.5322 | -0.28567 | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 5.263 | 7.7547 | 2.363 | -0.29231 | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 5.263 | 7.4211 | 2.2527 | -0.29493 | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 5.263 | 7.2212 | 2.187 | -0.29583 | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 5.263 | 7.1109 | 2.1509 | -0.29611 | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 5.263 | 7.1019 | 2.1479 | -0.29613 | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 5.263 | 7.2673 | 2.2021 | -0.29567 | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 5.263 | 7.6931 | 2.3425 | -0.2929 | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 5.263 | 8.3417 | 2.5593 | -0.28433 | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 5.263 | 8.7835 | 2.7089 | -0.27545 | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 5.263 | 8.9085 | 2.7515 | -0.2725 | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 5.2577 | 8.9587 | 2.7687 | -0.27125 | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 5.2419 | 8.9906 | 2.7796 | -0.27045 | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 5.2262 | 9.0224 | 2.7905 | -0.26963 | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 5.2262 | 9.0532 | 2.8011 | -0.26883 | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 5.2367 | 9.0696 | 2.8067 | -0.2684 | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 5.2525 | 9.1374 | 2.83 | -0.26657 | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 5.2577 | 9.333 | 2.8974 | -0.26098 | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 5.263 | 9.6315 | 3.0008 | -0.25152 | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 5.263 | 9.7526 | 3.043 | -0.24735 | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 5.263 | 9.7174 | 3.0307 | -0.24858 | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 5.263 | 9.6046 | 2.9915 | -0.25241 | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 5.263 | 9.3598 | 2.9066 | -0.26018 | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 5.263 | 8.8655 | 2.7369 | -0.27354 | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 5.263 | 8.2613 | 2.5322 | -0.28567 | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 5.263 | 7.7547 | 2.363 | -0.29231 | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 10.526 | 7.4211 | 2.2527 | -0.29493 | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 10.526 | 7.2212 | 2.187 | -0.29583 | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 10.526 | 7.1109 | 2.1509 | -0.29611 | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 10.526 | 7.1019 | 2.1479 | -0.29613 | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 10.526 | 7.2673 | 2.2021 | -0.29567 | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 10.526 | 7.6931 | 2.3425 | -0.2929 | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 10.5049 | 8.3417 | 2.5593 | -0.28433 | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 10.2313 | 8.7835 | 2.7089 | -0.27545 | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 9.4102 | 8.9085 | 2.7515 | -0.2725 | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.284 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 8.284 | 8.9587 | 2.7687 | -0.27125 | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 7.1472 | 8.9906 | 2.7796 | -0.27045 | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 6.5156 | 9.0224 | 2.7905 | -0.26963 | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 6.7051 | 9.0532 | 2.8011 | -0.26883 | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 7.0103 | 9.0696 | 2.8067 | -0.2684 | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | very sunny | 10.526 | 7.884 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 7.884 | 9.1374 | 2.83 | -0.26657 | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 8.9155 | 9.333 | 2.8974 | -0.26098 | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 9.8418 | 9.6315 | 3.0008 | -0.25152 | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 10.3786 | 9.7526 | 3.043 | -0.24735 | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 10.5155 | 9.7174 | 3.0307 | -0.24858 | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 10.526 | 9.6046 | 2.9915 | -0.25241 | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 10.526 | 9.3598 | 2.9066 | -0.26018 | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 10.526 | 8.8655 | 2.7369 | -0.27354 | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 10.526 | 8.2613 | 2.5322 | -0.28567 | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 10.526 | 7.7547 | 2.363 | -0.29231 | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 10.526 | 7.4211 | 2.2527 | -0.29493 | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 10.526 | 7.2212 | 2.187 | -0.29583 | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 10.526 | 7.1109 | 2.1509 | -0.29611 | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 10.526 | 7.1019 | 2.1479 | -0.29613 | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 10.526 | 7.2673 | 2.2021 | -0.29567 | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 10.526 | 7.6931 | 2.3425 | -0.2929 | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 10.526 | 8.3417 | 2.5593 | -0.28433 | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 10.5155 | 8.7835 | 2.7089 | -0.27545 | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 10.4102 | 8.9085 | 2.7515 | -0.2725 | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 10.1892 | 8.9587 | 2.7687 | -0.27125 | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 9.9576 | 8.9906 | 2.7796 | -0.27045 | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 9.8313 | 9.0224 | 2.7905 | -0.26963 | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 9.9681 | 9.0532 | 2.8011 | -0.26883 | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 10.0313 | 9.0696 | 2.8067 | -0.2684 | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 10.2944 | 9.1374 | 2.83 | -0.26657 | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 10.4734 | 9.333 | 2.8974 | -0.26098 | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 10.526 | 9.6315 | 3.0008 | -0.25152 | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 10.526 | 9.7526 | 3.043 | -0.24735 | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 10.526 | 9.7174 | 3.0307 | -0.24858 | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 10.526 | 9.6046 | 2.9915 | -0.25241 | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 10.526 | 9.3598 | 2.9066 | -0.26018 | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 10.526 | 8.8655 | 2.7369 | -0.27354 | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 10.526 | 8.2613 | 2.5322 | -0.28567 | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 10.526 | 7.7547 | 2.363 | -0.29231 | -3.633%
1 | 7.716 | 2.5361 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0088 | -3.0639 | 1.0088 | -3.0639 | 0.97 | -2.3613 | 0.97 | -2.3613 | -4.8727 | 10.526 | 7.4211 | 2.2527 | -0.29493 | -3.822%
2 | 7.517 | 2.4707 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.01 | -2.982 | 1.01 | -2.982 | 0.97 | -2.2584 | 0.97 | -2.2584 | -5.0127 | 10.526 | 7.2212 | 2.187 | -0.29583 | -3.935%
3 | 7.407 | 2.4346 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9369 | 1.0107 | -2.9369 | 0.97 | -2.2016 | 0.97 | -2.2016 | -5.0896 | 10.526 | 7.1109 | 2.1509 | -0.29611 | -3.998%
4 | 7.398 | 2.4316 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0107 | -2.9332 | 1.0107 | -2.9332 | 0.97 | -2.197 | 0.97 | -2.197 | -5.0959 | 10.526 | 7.1019 | 2.1479 | -0.29613 | -4.003%
5 | 7.563 | 2.4858 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0097 | -3.0009 | 1.0097 | -3.0009 | 0.97 | -2.2821 | 0.97 | -2.2821 | -4.9804 | 10.526 | 7.2673 | 2.2021 | -0.29567 | -3.909%
6 | 7.986 | 2.6249 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0072 | -3.1753 | 1.0072 | -3.1753 | 0.97 | -2.5014 | 0.97 | -2.5014 | -4.681 | 10.526 | 7.6931 | 2.3425 | -0.2929 | -3.668%
7 | 8.626 | 2.8352 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0034 | -3.4411 | 1.0034 | -3.4411 | 0.97 | -2.836 | 0.97 | -2.836 | -4.2186 | 10.526 | 8.3417 | 2.5593 | -0.28433 | -3.296%
8 | 9.059 | 2.9775 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0007 | -3.6222 | 1.0007 | -3.6222 | 0.97 | -3.0644 | 0.97 | -3.0644 | -3.899 | 10.526 | 8.7835 | 2.7089 | -0.27545 | -3.041%
9 | 9.181 | 3.0176 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99998 | -3.6734 | 0.99998 | -3.6734 | 0.97 | -3.129 | 0.97 | -3.129 | -3.808 | 10.526 | 8.9085 | 2.7515 | -0.2725 | -2.968%
10 | 9.23 | 3.0338 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.99968 | -3.694 | 0.99968 | -3.694 | 0.97 | -3.155 | 0.97 | -3.155 | -3.7713 | 10.5155 | 8.9587 | 2.7687 | -0.27125 | -2.939%
11 | 9.261 | 3.0439 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 5 | 0.99949 | -3.707 | 0.99949 | -3.707 | 0.97 | -3.1715 | 0.97 | -3.1715 | -3.7481 | 10.4839 | 8.9906 | 2.7796 | -0.27045 | -2.92%
12 | 9.292 | 3.0541 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.9993 | -3.72 | 0.9993 | -3.72 | 0.97 | -3.1879 | 0.97 | -3.1879 | -3.7248 | 10.4523 | 9.0224 | 2.7905 | -0.26963 | -2.902%
13 | 9.322 | 3.064 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 0.99911 | -3.7327 | 0.99911 | -3.7327 | 0.97 | -3.2039 | 0.97 | -3.2039 | -3.7022 | 10.4523 | 9.0532 | 2.8011 | -0.26883 | -2.884%
14 | 9.338 | 3.0693 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 5 | 0.99901 | -3.7394 | 0.99901 | -3.7394 | 0.97 | -3.2124 | 0.97 | -3.2124 | -3.6902 | 10.4734 | 9.0696 | 2.8067 | -0.2684 | -2.874%
15 | 9.404 | 3.0909 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 5 | 0.99861 | -3.7672 | 0.99861 | -3.7672 | 0.97 | -3.2475 | 0.97 | -3.2475 | -3.6404 | 10.5049 | 9.1374 | 2.83 | -0.26657 | -2.835%
16 | 9.594 | 3.1534 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 0.99743 | -3.8474 | 0.99743 | -3.8474 | 0.97 | -3.3489 | 0.97 | -3.3489 | -3.4965 | 10.5155 | 9.333 | 2.8974 | -0.26098 | -2.72%
17 | 9.883 | 3.2484 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99563 | -3.9698 | 0.99563 | -3.9698 | 0.97 | -3.5036 | 0.97 | -3.5036 | -3.2754 | 10.526 | 9.6315 | 3.0008 | -0.25152 | -2.545%
18 | 10 | 3.2868 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.9949 | -4.0195 | 0.9949 | -4.0195 | 0.97 | -3.5665 | 0.97 | -3.5665 | -3.1852 | 10.526 | 9.7526 | 3.043 | -0.24735 | -2.474%
19 | 9.966 | 3.2757 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99511 | -4.0051 | 0.99511 | -4.0051 | 0.97 | -3.5482 | 0.97 | -3.5482 | -3.2114 | 10.526 | 9.7174 | 3.0307 | -0.24858 | -2.494%
20 | 9.857 | 3.2398 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99579 | -3.9588 | 0.99579 | -3.9588 | 0.97 | -3.4897 | 0.97 | -3.4897 | -3.2954 | 10.526 | 9.6046 | 2.9915 | -0.25241 | -2.561%
21 | 9.62 | 3.1619 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 0.99727 | -3.8584 | 0.99727 | -3.8584 | 0.97 | -3.3628 | 0.97 | -3.3628 | -3.4767 | 10.526 | 9.3598 | 2.9066 | -0.26018 | -2.705%
22 | 9.139 | 3.0038 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0002 | -3.6557 | 1.0002 | -3.6557 | 0.97 | -3.1067 | 0.97 | -3.1067 | -3.8394 | 10.526 | 8.8655 | 2.7369 | -0.27354 | -2.993%
23 | 8.547 | 2.8093 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0038 | -3.4081 | 1.0038 | -3.4081 | 0.97 | -2.7945 | 0.97 | -2.7945 | -4.2763 | 10.526 | 8.2613 | 2.5322 | -0.28567 | -3.342%
24 | 8.047 | 2.6449 | 0.95 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0069 | -3.2005 | 1.0069 | -3.2005 | 0.97 | -2.5331 | 0.97 | -2.5331 | -4.6375 | 10.526 | 7.7547 | 2.363 | -0.29231 | -3.633%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1789 | 1.0293 | -0.94925 | 1.0036 | -3.0794 | -5.263 | 5.263 | 7.6149 | 1.5073 | -0.10107 | -1.31%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0295 | -0.92167 | 1.0045 | -2.9945 | -5.263 | 5.263 | 7.4186 | 1.4685 | -0.098441 | -1.31%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.90644 | 1.0051 | -2.9476 | -5.263 | 5.263 | 7.31 | 1.4471 | -0.097011 | -1.31%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90519 | 1.0051 | -2.9438 | -5.263 | 5.263 | 7.3011 | 1.4453 | -0.096896 | -1.31%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92805 | 1.0043 | -3.0141 | -5.263 | 5.263 | 7.464 | 1.4775 | -0.099039 | -1.31%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.98673 | 1.0023 | -3.195 | -5.263 | 5.263 | 7.8815 | 1.5599 | -0.10453 | -1.309%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0282 | -1.0751 | 0.99929 | -3.4661 | -5.2525 | 5.2525 | 8.5141 | 1.6853 | -0.11186 | -1.297%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.028 | -1.1388 | 0.99751 | -3.6555 | -5.1156 | 5.1156 | 8.9447 | 1.7715 | -0.11427 | -1.261%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0289 | -1.1656 | 0.99796 | -3.7151 | -4.7051 | 4.7051 | 9.0747 | 1.801 | -0.10628 | -1.158%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.142 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0303 | -1.186 | 0.99913 | -3.7461 | -4.142 | 4.142 | 9.1361 | 1.8183 | -0.093877 | -1.017%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0316 | -1.2068 | 1.0002 | -3.7808 | -3.5736 | 3.5736 | 9.1785 | 1.8313 | -0.082523 | -0.8911%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0324 | -1.2183 | 1.0009 | -3.7982 | -3.2578 | 3.2578 | 9.2167 | 1.8419 | -0.075344 | -0.8108%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0322 | -1.2174 | 1.0007 | -3.798 | -3.3525 | 3.3525 | 9.2458 | 1.8475 | -0.076178 | -0.8172%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0318 | -1.2161 | 1.0002 | -3.8025 | -3.5052 | 3.5052 | 9.2581 | 1.8485 | -0.079882 | -0.8554%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.942 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0306 | -1.2149 | 0.99879 | -3.824 | -3.942 | 3.942 | 9.3133 | 1.8554 | -0.090747 | -0.965%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.029 | -1.2293 | 0.99653 | -3.8984 | -4.4578 | 4.4578 | 9.489 | 1.8854 | -0.10501 | -1.095%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0274 | -1.2596 | 0.99382 | -4.0211 | -4.9209 | 4.9209 | 9.7626 | 1.9347 | -0.12035 | -1.218%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0265 | -1.2699 | 0.99253 | -4.0692 | -5.1893 | 5.1893 | 9.8713 | 1.9534 | -0.12871 | -1.287%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2636 | 0.99252 | -4.0535 | -5.2577 | 5.2577 | 9.836 | 1.9457 | -0.13004 | -1.305%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0265 | -1.2481 | 0.99306 | -4.0057 | -5.263 | 5.263 | 9.7282 | 1.9244 | -0.12877 | -1.306%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.2148 | 0.99425 | -3.902 | -5.263 | 5.263 | 9.4943 | 1.8783 | -0.1257 | -1.307%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1474 | 0.99665 | -3.6926 | -5.263 | 5.263 | 9.0195 | 1.7846 | -0.11947 | -1.307%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0648 | 0.99957 | -3.4363 | -5.263 | 5.263 | 8.4352 | 1.6693 | -0.1118 | -1.308%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99521 | 1.002 | -3.2212 | -5.263 | 5.263 | 7.9417 | 1.5718 | -0.10532 | -1.309%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.94926 | 1.0036 | -3.0795 | -5.263 | 5.263 | 7.615 | 1.5073 | -0.10102 | -1.309%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0295 | -0.92167 | 1.0045 | -2.9945 | -5.263 | 5.263 | 7.4186 | 1.4685 | -0.098441 | -1.31%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.90644 | 1.0051 | -2.9476 | -5.263 | 5.263 | 7.31 | 1.4471 | -0.097011 | -1.31%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90519 | 1.0051 | -2.9438 | -5.263 | 5.263 | 7.3011 | 1.4453 | -0.096896 | -1.31%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92805 | 1.0043 | -3.0141 | -5.263 | 5.263 | 7.464 | 1.4775 | -0.099039 | -1.31%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.98673 | 1.0023 | -3.195 | -5.263 | 5.263 | 7.8815 | 1.5599 | -0.10453 | -1.309%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0281 | -1.0758 | 0.99918 | -3.4704 | -5.263 | 5.263 | 8.5132 | 1.6847 | -0.11283 | -1.308%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1364 | 0.99706 | -3.6579 | -5.2577 | 5.2577 | 8.9407 | 1.7691 | -0.11831 | -1.306%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0276 | -1.1547 | 0.99659 | -3.7115 | -5.2051 | 5.2051 | 9.0624 | 1.7936 | -0.11864 | -1.292%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0278 | -1.1632 | 0.99672 | -3.73 | -5.0946 | 5.0946 | 9.1141 | 1.8052 | -0.1159 | -1.256%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0281 | -1.1703 | 0.99686 | -3.7453 | -4.9788 | 4.9788 | 9.1474 | 1.8128 | -0.11358 | -1.226%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0282 | -1.1761 | 0.99687 | -3.7598 | -4.9156 | 4.9156 | 9.1795 | 1.8198 | -0.11248 | -1.21%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.028 | -1.1787 | 0.99654 | -3.7717 | -4.9841 | 4.9841 | 9.2076 | 1.8247 | -0.11445 | -1.228%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0279 | -1.1802 | 0.99638 | -3.7782 | -5.0156 | 5.0156 | 9.2226 | 1.8273 | -0.11538 | -1.236%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0275 | -1.1862 | 0.99572 | -3.8047 | -5.1472 | 5.1472 | 9.2847 | 1.8384 | -0.11931 | -1.269%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.027 | -1.2107 | 0.99454 | -3.886 | -5.2367 | 5.2367 | 9.4701 | 1.8741 | -0.12385 | -1.291%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0265 | -1.2518 | 0.99293 | -4.0171 | -5.263 | 5.263 | 9.7539 | 1.9295 | -0.1291 | -1.306%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0263 | -1.2682 | 0.99234 | -4.0684 | -5.263 | 5.263 | 9.8694 | 1.9523 | -0.13061 | -1.306%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2634 | 0.99251 | -4.0535 | -5.263 | 5.263 | 9.8358 | 1.9457 | -0.13017 | -1.306%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0265 | -1.2481 | 0.99306 | -4.0057 | -5.263 | 5.263 | 9.7282 | 1.9244 | -0.12877 | -1.306%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.2148 | 0.99425 | -3.902 | -5.263 | 5.263 | 9.4943 | 1.8783 | -0.1257 | -1.307%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1474 | 0.99665 | -3.6926 | -5.263 | 5.263 | 9.0195 | 1.7846 | -0.11947 | -1.307%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0648 | 0.99957 | -3.4363 | -5.263 | 5.263 | 8.4352 | 1.6693 | -0.1118 | -1.308%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99521 | 1.002 | -3.2212 | -5.263 | 5.263 | 7.9417 | 1.5718 | -0.10532 | -1.309%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0293 | -0.94926 | 1.0036 | -3.0795 | -5.263 | 5.263 | 7.615 | 1.5073 | -0.10102 | -1.309%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.043 | -1.0477 | 1.0178 | -3.0945 | 1.0295 | -0.92167 | 1.0045 | -2.9945 | -5.263 | 5.263 | 7.4186 | 1.4685 | -0.098441 | -1.31%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0297 | -0.90644 | 1.0051 | -2.9476 | -5.263 | 5.263 | 7.31 | 1.4471 | -0.097011 | -1.31%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0297 | -0.90519 | 1.0051 | -2.9438 | -5.263 | 5.263 | 7.3011 | 1.4453 | -0.096896 | -1.31%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0295 | -0.92805 | 1.0043 | -3.0141 | -5.263 | 5.263 | 7.464 | 1.4775 | -0.099039 | -1.31%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.0289 | -0.98673 | 1.0023 | -3.195 | -5.263 | 5.263 | 7.8815 | 1.5599 | -0.10453 | -1.309%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0281 | -1.0758 | 0.99918 | -3.4704 | -5.263 | 5.263 | 8.5132 | 1.6847 | -0.11283 | -1.308%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0276 | -1.1363 | 0.99705 | -3.6578 | -5.263 | 5.263 | 8.9406 | 1.769 | -0.11844 | -1.307%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0274 | -1.1533 | 0.99644 | -3.7108 | -5.263 | 5.263 | 9.061 | 1.7928 | -0.12002 | -1.307%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0273 | -1.1603 | 0.99621 | -3.7322 | -5.2577 | 5.2577 | 9.1095 | 1.8024 | -0.12053 | -1.306%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0274 | -1.165 | 0.9961 | -3.7458 | -5.2419 | 5.2419 | 9.1405 | 1.8087 | -0.12055 | -1.302%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0274 | -1.1697 | 0.99599 | -3.7595 | -5.2262 | 5.2262 | 9.1714 | 1.8149 | -0.12057 | -1.298%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0273 | -1.1739 | 0.99584 | -3.7726 | -5.2262 | 5.2262 | 9.201 | 1.8208 | -0.12095 | -1.298%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0273 | -1.1749 | 0.99582 | -3.7746 | -5.2367 | 5.2367 | 9.2174 | 1.8242 | -0.12059 | -1.291%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0272 | -1.1837 | 0.99545 | -3.803 | -5.2525 | 5.2525 | 9.2822 | 1.8369 | -0.12181 | -1.295%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0269 | -1.2113 | 0.9944 | -3.8908 | -5.2577 | 5.2577 | 9.4688 | 1.8733 | -0.12523 | -1.305%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0265 | -1.2518 | 0.99293 | -4.0171 | -5.263 | 5.263 | 9.7539 | 1.9295 | -0.1291 | -1.306%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0263 | -1.2682 | 0.99234 | -4.0684 | -5.263 | 5.263 | 9.8694 | 1.9523 | -0.13061 | -1.306%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0264 | -1.2634 | 0.99251 | -4.0535 | -5.263 | 5.263 | 9.8358 | 1.9457 | -0.13017 | -1.306%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0265 | -1.2481 | 0.99306 | -4.0057 | -5.263 | 5.263 | 9.7282 | 1.9244 | -0.12877 | -1.306%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9947 | 1.0268 | -1.2148 | 0.99425 | -3.902 | -5.263 | 5.263 | 9.4943 | 1.8783 | -0.1257 | -1.307%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0275 | -1.1474 | 0.99665 | -3.6926 | -5.263 | 5.263 | 9.0195 | 1.7846 | -0.11947 | -1.307%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5328 | 1.0282 | -1.0648 | 0.99957 | -3.4363 | -5.263 | 5.263 | 8.4352 | 1.6693 | -0.1118 | -1.308%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0289 | -0.99521 | 1.002 | -3.2212 | -5.263 | 5.263 | 7.9417 | 1.5718 | -0.10532 | -1.309%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0153 | -0.82299 | 0.98984 | -2.9909 | -10.526 | 10.526 | 7.5108 | 1.4463 | -0.20515 | -2.659%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.79536 | 0.99079 | -2.9048 | -10.526 | 10.526 | 7.3171 | 1.4091 | -0.19989 | -2.659%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.7801 | 0.99131 | -2.8573 | -10.526 | 10.526 | 7.21 | 1.3886 | -0.19698 | -2.659%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0157 | -0.77886 | 0.99136 | -2.8534 | -10.526 | 10.526 | 7.2013 | 1.3869 | -0.19674 | -2.659%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0155 | -0.80174 | 0.99057 | -2.9247 | -10.526 | 10.526 | 7.3619 | 1.4177 | -0.20111 | -2.659%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.86052 | 0.98855 | -3.1079 | -10.526 | 10.526 | 7.7737 | 1.4966 | -0.21231 | -2.658%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0143 | -0.948 | 0.98566 | -3.3774 | -10.5049 | 10.5049 | 8.3986 | 1.617 | -0.22741 | -2.636%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0145 | -1.0151 | 0.98426 | -3.5713 | -10.2313 | 10.2313 | 8.8266 | 1.7015 | -0.23235 | -2.565%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0165 | -1.0522 | 0.98581 | -3.6382 | -9.4102 | 9.4102 | 8.9649 | 1.7358 | -0.2161 | -2.354%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.284 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0194 | -1.0868 | 0.98847 | -3.68 | -8.284 | 8.284 | 9.039 | 1.7606 | -0.19099 | -2.069%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0223 | -1.1212 | 0.99112 | -3.7221 | -7.1472 | 7.1472 | 9.0949 | 1.7816 | -0.16609 | -1.793%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0239 | -1.14 | 0.99261 | -3.7435 | -6.5156 | 6.5156 | 9.1405 | 1.7965 | -0.15151 | -1.631%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0235 | -1.1374 | 0.99213 | -3.7439 | -6.7051 | 6.7051 | 9.1669 | 1.8005 | -0.15505 | -1.663%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0227 | -1.1323 | 0.99127 | -3.7459 | -7.0103 | 7.0103 | 9.1754 | 1.7993 | -0.16255 | -1.741%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.884 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0203 | -1.1205 | 0.98867 | -3.761 | -7.884 | 7.884 | 9.2193 | 1.7995 | -0.18468 | -1.964%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0173 | -1.122 | 0.98505 | -3.8274 | -8.9155 | 8.9155 | 9.3804 | 1.8207 | -0.21358 | -2.226%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0144 | -1.142 | 0.98105 | -3.9487 | -9.8418 | 9.8418 | 9.6382 | 1.8605 | -0.24478 | -2.477%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0128 | -1.1459 | 0.97903 | -3.9945 | -10.3786 | 10.3786 | 9.7383 | 1.874 | -0.26173 | -2.617%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0124 | -1.1379 | 0.97883 | -3.9778 | -10.5155 | 10.5155 | 9.7016 | 1.8655 | -0.26441 | -2.653%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0126 | -1.1223 | 0.97935 | -3.9293 | -10.526 | 10.526 | 9.5952 | 1.8451 | -0.2618 | -2.656%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.0129 | -1.089 | 0.98054 | -3.8243 | -10.526 | 10.526 | 9.3645 | 1.801 | -0.25554 | -2.656%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0135 | -1.0215 | 0.98293 | -3.612 | -10.526 | 10.526 | 8.8962 | 1.7115 | -0.24281 | -2.657%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0143 | -0.9387 | 0.98583 | -3.3524 | -10.526 | 10.526 | 8.3198 | 1.6012 | -0.22715 | -2.658%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0149 | -0.86901 | 0.98825 | -3.1344 | -10.526 | 10.526 | 7.8331 | 1.508 | -0.21392 | -2.658%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0153 | -0.82298 | 0.98984 | -2.9909 | -10.526 | 10.526 | 7.5108 | 1.4463 | -0.20516 | -2.659%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.79536 | 0.99079 | -2.9048 | -10.526 | 10.526 | 7.3171 | 1.4091 | -0.19989 | -2.659%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.7801 | 0.99131 | -2.8573 | -10.526 | 10.526 | 7.21 | 1.3886 | -0.19698 | -2.659%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0157 | -0.77886 | 0.99136 | -2.8534 | -10.526 | 10.526 | 7.2013 | 1.3869 | -0.19674 | -2.659%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0155 | -0.80174 | 0.99057 | -2.9247 | -10.526 | 10.526 | 7.3619 | 1.4177 | -0.20111 | -2.659%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.86052 | 0.98855 | -3.1079 | -10.526 | 10.526 | 7.7737 | 1.4966 | -0.21231 | -2.658%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0142 | -0.94973 | 0.98545 | -3.3869 | -10.526 | 10.526 | 8.3968 | 1.616 | -0.22924 | -2.658%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0136 | -1.0105 | 0.98335 | -3.5769 | -10.5155 | 10.5155 | 8.8186 | 1.6968 | -0.24045 | -2.654%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0138 | -1.0301 | 0.98303 | -3.6319 | -10.4102 | 10.4102 | 8.9399 | 1.721 | -0.24114 | -2.627%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0144 | -1.04 | 0.98353 | -3.6469 | -10.1892 | 10.1892 | 8.9943 | 1.7341 | -0.23571 | -2.554%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.015 | -1.05 | 0.98399 | -3.6643 | -9.9576 | 9.9576 | 9.03 | 1.7431 | -0.23098 | -2.494%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0153 | -1.0574 | 0.98416 | -3.68 | -9.8313 | 9.8313 | 9.0633 | 1.7507 | -0.22873 | -2.462%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0149 | -1.0583 | 0.98366 | -3.6909 | -9.9681 | 9.9681 | 9.0893 | 1.7544 | -0.23274 | -2.497%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0147 | -1.059 | 0.98341 | -3.6969 | -10.0313 | 10.0313 | 9.1033 | 1.7565 | -0.23465 | -2.513%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0139 | -1.0618 | 0.98239 | -3.7217 | -10.2944 | 10.2944 | 9.1613 | 1.7651 | -0.24266 | -2.58%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0132 | -1.084 | 0.98098 | -3.8025 | -10.4734 | 10.4734 | 9.3421 | 1.7979 | -0.25194 | -2.626%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0125 | -1.126 | 0.97922 | -3.9408 | -10.526 | 10.526 | 9.6205 | 1.85 | -0.26249 | -2.656%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0124 | -1.1424 | 0.97863 | -3.9928 | -10.526 | 10.526 | 9.7344 | 1.8717 | -0.26558 | -2.656%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0124 | -1.1377 | 0.97881 | -3.9777 | -10.526 | 10.526 | 9.7013 | 1.8654 | -0.26468 | -2.656%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0126 | -1.1223 | 0.97935 | -3.9293 | -10.526 | 10.526 | 9.5952 | 1.8451 | -0.2618 | -2.656%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.0129 | -1.089 | 0.98054 | -3.8243 | -10.526 | 10.526 | 9.3645 | 1.801 | -0.25554 | -2.656%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0135 | -1.0215 | 0.98293 | -3.612 | -10.526 | 10.526 | 8.8962 | 1.7115 | -0.24281 | -2.657%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0143 | -0.9387 | 0.98583 | -3.3524 | -10.526 | 10.526 | 8.3198 | 1.6012 | -0.22715 | -2.658%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0149 | -0.86901 | 0.98825 | -3.1344 | -10.526 | 10.526 | 7.8331 | 1.508 | -0.21392 | -2.658%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0427 | -1.0754 | 1.0168 | -3.1788 | 1.0153 | -0.82298 | 0.98984 | -2.9909 | -10.526 | 10.526 | 7.5108 | 1.4463 | -0.20516 | -2.659%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.043 | -1.0478 | 1.0178 | -3.0945 | 1.0156 | -0.79536 | 0.99079 | -2.9048 | -10.526 | 10.526 | 7.3171 | 1.4091 | -0.19989 | -2.659%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0325 | 1.0183 | -3.048 | 1.0157 | -0.7801 | 0.99131 | -2.8573 | -10.526 | 10.526 | 7.21 | 1.3886 | -0.19698 | -2.659%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0431 | -1.0312 | 1.0184 | -3.0442 | 1.0157 | -0.77886 | 0.99136 | -2.8534 | -10.526 | 10.526 | 7.2013 | 1.3869 | -0.19674 | -2.659%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0429 | -1.0541 | 1.0176 | -3.114 | 1.0155 | -0.80174 | 0.99057 | -2.9247 | -10.526 | 10.526 | 7.3619 | 1.4177 | -0.20111 | -2.659%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0424 | -1.113 | 1.0155 | -3.2935 | 1.015 | -0.86052 | 0.98855 | -3.1079 | -10.526 | 10.526 | 7.7737 | 1.4966 | -0.21231 | -2.658%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0416 | -1.2022 | 1.0124 | -3.5666 | 1.0142 | -0.94973 | 0.98545 | -3.3869 | -10.526 | 10.526 | 8.3968 | 1.616 | -0.22924 | -2.658%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.041 | -1.2628 | 1.0102 | -3.7525 | 1.0136 | -1.0103 | 0.98332 | -3.5768 | -10.526 | 10.526 | 8.8183 | 1.6966 | -0.24069 | -2.657%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2799 | 1.0096 | -3.805 | 1.0135 | -1.0274 | 0.98272 | -3.6305 | -10.526 | 10.526 | 8.9371 | 1.7193 | -0.24392 | -2.657%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0408 | -1.2868 | 1.0094 | -3.8261 | 1.0134 | -1.0345 | 0.98251 | -3.6522 | -10.5155 | 10.5155 | 8.985 | 1.7286 | -0.24497 | -2.654%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 3 | 1.0408 | -1.2912 | 1.0092 | -3.8395 | 1.0135 | -1.0396 | 0.98244 | -3.6662 | -10.4839 | 10.4839 | 9.016 | 1.7348 | -0.24502 | -2.646%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2955 | 1.0091 | -3.8529 | 1.0135 | -1.0447 | 0.98237 | -3.6803 | -10.4523 | 10.4523 | 9.0469 | 1.7411 | -0.24507 | -2.637%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 3 | 1.0407 | -1.2997 | 1.0089 | -3.8658 | 1.0135 | -1.0489 | 0.98222 | -3.6935 | -10.4523 | 10.4523 | 9.0761 | 1.7466 | -0.24586 | -2.637%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 3 | 1.0407 | -1.302 | 1.0088 | -3.8727 | 1.0135 | -1.0482 | 0.98225 | -3.6897 | -10.4734 | 10.4734 | 9.0927 | 1.7502 | -0.24527 | -2.627%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 3 | 1.0406 | -1.3112 | 1.0085 | -3.9012 | 1.0133 | -1.0566 | 0.98184 | -3.7183 | -10.5049 | 10.5049 | 9.1562 | 1.7621 | -0.24775 | -2.635%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 3 | 1.0403 | -1.3379 | 1.0075 | -3.9834 | 1.0129 | -1.0856 | 0.9807 | -3.8129 | -10.5155 | 10.5155 | 9.3394 | 1.7964 | -0.25458 | -2.654%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0399 | -1.3786 | 1.0061 | -4.1087 | 1.0125 | -1.126 | 0.97922 | -3.9408 | -10.526 | 10.526 | 9.6205 | 1.85 | -0.26249 | -2.656%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3951 | 1.0055 | -4.1596 | 1.0124 | -1.1424 | 0.97863 | -3.9928 | -10.526 | 10.526 | 9.7344 | 1.8717 | -0.26558 | -2.656%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0398 | -1.3903 | 1.0057 | -4.1448 | 1.0124 | -1.1377 | 0.97881 | -3.9777 | -10.526 | 10.526 | 9.7013 | 1.8654 | -0.26468 | -2.656%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.04 | -1.3749 | 1.0062 | -4.0974 | 1.0126 | -1.1223 | 0.97935 | -3.9293 | -10.526 | 10.526 | 9.5952 | 1.8451 | -0.2618 | -2.656%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0403 | -1.3416 | 1.0074 | -3.9946 | 1.0129 | -1.089 | 0.98054 | -3.8243 | -10.526 | 10.526 | 9.3645 | 1.801 | -0.25554 | -2.656%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0409 | -1.2741 | 1.0098 | -3.7869 | 1.0135 | -1.0215 | 0.98293 | -3.612 | -10.526 | 10.526 | 8.8962 | 1.7115 | -0.24281 | -2.657%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0417 | -1.1912 | 1.0128 | -3.5327 | 1.0143 | -0.9387 | 0.98583 | -3.3524 | -10.526 | 10.526 | 8.3198 | 1.6012 | -0.22715 | -2.658%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 3 | 1.0423 | -1.1215 | 1.0152 | -3.3194 | 1.0149 | -0.86901 | 0.98825 | -3.1344 | -10.526 | 10.526 | 7.8331 | 1.508 | -0.21392 | -2.658%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0296 | -2.1143 | 1.0168 | -3.1788 | 1.0019 | -1.6728 | 0.98929 | -2.7709 | -5.263 | 5.263 | 7.5067 | 1.4438 | -0.20931 | -2.713%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0025 | -1.6177 | 0.99024 | -2.6858 | -5.263 | 5.263 | 7.3131 | 1.4068 | -0.20391 | -2.713%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.0028 | -1.5873 | 0.99077 | -2.6388 | -5.263 | 5.263 | 7.2061 | 1.3863 | -0.20092 | -2.713%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0029 | -1.5848 | 0.99081 | -2.635 | -5.263 | 5.263 | 7.1973 | 1.3846 | -0.20068 | -2.713%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0023 | -1.6304 | 0.99002 | -2.7055 | -5.263 | 5.263 | 7.3578 | 1.4153 | -0.20516 | -2.713%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.001 | -1.7478 | 0.98799 | -2.8868 | -5.263 | 5.263 | 7.7694 | 1.4941 | -0.21665 | -2.713%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99924 | -1.9218 | 0.9851 | -3.1543 | -5.2525 | 5.2525 | 8.3939 | 1.6143 | -0.23213 | -2.691%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99861 | -2.0543 | 0.98371 | -3.3521 | -5.1156 | 5.1156 | 8.8218 | 1.6987 | -0.23724 | -2.619%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 1.0004 | -2.1236 | 0.98531 | -3.4367 | -4.7051 | 4.7051 | 8.9604 | 1.7331 | -0.22064 | -2.403%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.142 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 1.0033 | -2.1863 | 0.98802 | -3.5032 | -4.142 | 4.142 | 9.035 | 1.7582 | -0.19505 | -2.113%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 1.0061 | -2.2485 | 0.99073 | -3.5693 | -3.5736 | 3.5736 | 9.0914 | 1.7796 | -0.16957 | -1.831%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 1.0077 | -2.2824 | 0.99227 | -3.6045 | -3.2578 | 3.2578 | 9.1373 | 1.7947 | -0.15468 | -1.665%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 1.0072 | -2.2778 | 0.99178 | -3.6014 | -3.3525 | 3.3525 | 9.1637 | 1.7986 | -0.15827 | -1.698%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 1.0064 | -2.2694 | 0.9909 | -3.5967 | -3.5052 | 3.5052 | 9.1721 | 1.7973 | -0.16594 | -1.777%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.942 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 1.0038 | -2.2513 | 0.98825 | -3.5926 | -3.942 | 3.942 | 9.2154 | 1.7972 | -0.18862 | -2.006%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 1.0004 | -2.2604 | 0.98457 | -3.6352 | -4.4578 | 4.4578 | 9.3759 | 1.818 | -0.21812 | -2.273%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99688 | -2.3066 | 0.9805 | -3.734 | -4.9209 | 4.9209 | 9.6329 | 1.8573 | -0.25013 | -2.531%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99502 | -2.3178 | 0.97844 | -3.767 | -5.1893 | 5.1893 | 9.7325 | 1.8706 | -0.26748 | -2.675%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99475 | -2.3027 | 0.97824 | -3.7474 | -5.2577 | 5.2577 | 9.6958 | 1.8621 | -0.27022 | -2.711%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99508 | -2.2715 | 0.97876 | -3.6992 | -5.263 | 5.263 | 9.5895 | 1.8417 | -0.26753 | -2.714%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99585 | -2.2047 | 0.97995 | -3.5953 | -5.263 | 5.263 | 9.3589 | 1.7977 | -0.26108 | -2.714%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.9974 | -2.0696 | 0.98235 | -3.3853 | -5.263 | 5.263 | 8.891 | 1.7084 | -0.24799 | -2.714%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99929 | -1.904 | 0.98526 | -3.1285 | -5.263 | 5.263 | 8.3151 | 1.5984 | -0.23189 | -2.713%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0009 | -1.7647 | 0.9877 | -2.913 | -5.263 | 5.263 | 7.8287 | 1.5054 | -0.21831 | -2.713%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0019 | -1.6728 | 0.98929 | -2.7709 | -5.263 | 5.263 | 7.5067 | 1.4438 | -0.20932 | -2.713%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0025 | -1.6177 | 0.99024 | -2.6858 | -5.263 | 5.263 | 7.3131 | 1.4068 | -0.20391 | -2.713%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.0028 | -1.5873 | 0.99077 | -2.6388 | -5.263 | 5.263 | 7.2061 | 1.3863 | -0.20092 | -2.713%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0029 | -1.5848 | 0.99081 | -2.635 | -5.263 | 5.263 | 7.1973 | 1.3846 | -0.20068 | -2.713%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0023 | -1.6304 | 0.99002 | -2.7055 | -5.263 | 5.263 | 7.3578 | 1.4153 | -0.20516 | -2.713%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.001 | -1.7478 | 0.98799 | -2.8868 | -5.263 | 5.263 | 7.7694 | 1.4941 | -0.21665 | -2.713%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99904 | -1.926 | 0.98488 | -3.1627 | -5.263 | 5.263 | 8.392 | 1.6131 | -0.23404 | -2.713%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99769 | -2.0476 | 0.98277 | -3.3509 | -5.2577 | 5.2577 | 8.8134 | 1.6937 | -0.24556 | -2.711%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99759 | -2.0861 | 0.98246 | -3.4076 | -5.2051 | 5.2051 | 8.9347 | 1.7179 | -0.24629 | -2.683%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99818 | -2.1039 | 0.98298 | -3.4279 | -5.0946 | 5.0946 | 8.9893 | 1.7311 | -0.24069 | -2.608%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.9987 | -2.1225 | 0.98345 | -3.4503 | -4.9788 | 4.9788 | 9.0251 | 1.7402 | -0.23586 | -2.547%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99894 | -2.1366 | 0.98363 | -3.4687 | -4.9156 | 4.9156 | 9.0584 | 1.7479 | -0.23357 | -2.514%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99848 | -2.1392 | 0.98312 | -3.4764 | -4.9841 | 4.9841 | 9.0843 | 1.7515 | -0.23767 | -2.55%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99826 | -2.1409 | 0.98287 | -3.4809 | -5.0156 | 5.0156 | 9.0984 | 1.7536 | -0.23963 | -2.566%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99733 | -2.1481 | 0.98183 | -3.4995 | -5.1472 | 5.1472 | 9.1562 | 1.762 | -0.24783 | -2.635%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99623 | -2.1937 | 0.9804 | -3.5754 | -5.2367 | 5.2367 | 9.3367 | 1.7947 | -0.25735 | -2.682%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.995 | -2.2789 | 0.97863 | -3.7106 | -5.263 | 5.263 | 9.6148 | 1.8465 | -0.26824 | -2.714%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99461 | -2.3119 | 0.97804 | -3.762 | -5.263 | 5.263 | 9.7286 | 1.8682 | -0.27142 | -2.714%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99472 | -2.3023 | 0.97821 | -3.747 | -5.263 | 5.263 | 9.6955 | 1.8619 | -0.2705 | -2.714%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99508 | -2.2715 | 0.97876 | -3.6992 | -5.263 | 5.263 | 9.5895 | 1.8417 | -0.26753 | -2.714%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99585 | -2.2047 | 0.97995 | -3.5953 | -5.263 | 5.263 | 9.3589 | 1.7977 | -0.26108 | -2.714%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.9974 | -2.0696 | 0.98235 | -3.3853 | -5.263 | 5.263 | 8.891 | 1.7084 | -0.24799 | -2.714%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99929 | -1.904 | 0.98526 | -3.1285 | -5.263 | 5.263 | 8.3151 | 1.5984 | -0.23189 | -2.713%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0009 | -1.7647 | 0.9877 | -2.913 | -5.263 | 5.263 | 7.8287 | 1.5054 | -0.21831 | -2.713%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 1.0019 | -1.6728 | 0.98929 | -2.7709 | -5.263 | 5.263 | 7.5067 | 1.4438 | -0.20932 | -2.713%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 1.0025 | -1.6177 | 0.99024 | -2.6858 | -5.263 | 5.263 | 7.3131 | 1.4068 | -0.20391 | -2.713%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 1.0028 | -1.5873 | 0.99077 | -2.6388 | -5.263 | 5.263 | 7.2061 | 1.3863 | -0.20092 | -2.713%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 1.0029 | -1.5848 | 0.99081 | -2.635 | -5.263 | 5.263 | 7.1973 | 1.3846 | -0.20068 | -2.713%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 1.0023 | -1.6304 | 0.99002 | -2.7055 | -5.263 | 5.263 | 7.3578 | 1.4153 | -0.20516 | -2.713%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 1.001 | -1.7478 | 0.98799 | -2.8868 | -5.263 | 5.263 | 7.7694 | 1.4941 | -0.21665 | -2.713%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.99904 | -1.926 | 0.98488 | -3.1627 | -5.263 | 5.263 | 8.392 | 1.6131 | -0.23404 | -2.713%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0254 | -2.4894 | 1.0102 | -3.7525 | 0.99766 | -2.0472 | 0.98275 | -3.3505 | -5.263 | 5.263 | 8.8132 | 1.6936 | -0.24581 | -2.713%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99727 | -2.0814 | 0.98214 | -3.4036 | -5.263 | 5.263 | 8.9319 | 1.7162 | -0.24913 | -2.714%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99714 | -2.0956 | 0.98193 | -3.4253 | -5.2577 | 5.2577 | 8.9798 | 1.7255 | -0.2502 | -2.711%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99713 | -2.1055 | 0.98186 | -3.4399 | -5.2419 | 5.2419 | 9.0107 | 1.7317 | -0.25027 | -2.702%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99712 | -2.1155 | 0.98179 | -3.4545 | -5.2262 | 5.2262 | 9.0417 | 1.7379 | -0.25032 | -2.694%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99702 | -2.1239 | 0.98164 | -3.4676 | -5.2262 | 5.2262 | 9.0709 | 1.7435 | -0.25113 | -2.694%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99706 | -2.122 | 0.98168 | -3.4639 | -5.2367 | 5.2367 | 9.0875 | 1.7471 | -0.25049 | -2.682%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99676 | -2.1391 | 0.98127 | -3.4914 | -5.2525 | 5.2525 | 9.151 | 1.7589 | -0.25304 | -2.691%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99597 | -2.1978 | 0.98011 | -3.5842 | -5.2577 | 5.2577 | 9.3339 | 1.7931 | -0.2601 | -2.711%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.995 | -2.2789 | 0.97863 | -3.7106 | -5.263 | 5.263 | 9.6148 | 1.8465 | -0.26824 | -2.714%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99461 | -2.3119 | 0.97804 | -3.762 | -5.263 | 5.263 | 9.7286 | 1.8682 | -0.27142 | -2.714%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99472 | -2.3023 | 0.97821 | -3.747 | -5.263 | 5.263 | 9.6955 | 1.8619 | -0.2705 | -2.714%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99508 | -2.2715 | 0.97876 | -3.6992 | -5.263 | 5.263 | 9.5895 | 1.8417 | -0.26753 | -2.714%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9947 | 0.99585 | -2.2047 | 0.97995 | -3.5953 | -5.263 | 5.263 | 9.3589 | 1.7977 | -0.26108 | -2.714%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.9974 | -2.0696 | 0.98235 | -3.3853 | -5.263 | 5.263 | 8.891 | 1.7084 | -0.24799 | -2.714%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.99929 | -1.904 | 0.98526 | -3.1285 | -5.263 | 5.263 | 8.3151 | 1.5984 | -0.23189 | -2.713%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 4 | 1.0286 | -2.2064 | 1.0152 | -3.3194 | 1.0009 | -1.7647 | 0.9877 | -2.913 | -5.263 | 5.263 | 7.8287 | 1.5054 | -0.21831 | -2.713%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4815 | 0.97713 | -2.5966 | -7.4845 | 10.526 | 7.4155 | 1.3906 | -0.30053 | -3.895%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99024 | -1.4264 | 0.97809 | -2.511 | -7.4837 | 10.526 | 7.2242 | 1.355 | -0.29275 | -3.895%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3959 | 0.97861 | -2.4637 | -7.4836 | 10.526 | 7.1185 | 1.3353 | -0.28845 | -3.894%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3934 | 0.97865 | -2.4599 | -7.4836 | 10.526 | 7.1099 | 1.3337 | -0.2881 | -3.894%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4391 | 0.97787 | -2.5308 | -7.4839 | 10.526 | 7.2685 | 1.3632 | -0.29455 | -3.895%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5564 | 0.97584 | -2.7131 | -7.4846 | 10.526 | 7.6749 | 1.4389 | -0.31109 | -3.895%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7347 | 0.97273 | -2.9907 | -7.4854 | 10.5049 | 8.2899 | 1.5531 | -0.33613 | -3.897%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.8559 | 0.9706 | -3.1796 | -7.4858 | 10.2313 | 8.7059 | 1.6303 | -0.35309 | -3.898%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99501 | -2.048 | 0.9799 | -3.3749 | -5.6736 | 9.4102 | 8.9117 | 1.7043 | -0.26929 | -2.933%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.284 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99485 | -2.0617 | 0.97965 | -3.3962 | -5.6741 | 8.284 | 8.9593 | 1.7134 | -0.27073 | -2.933%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0704 | 0.9795 | -3.4098 | -5.6741 | 7.1472 | 8.9894 | 1.7191 | -0.27164 | -2.933%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.0791 | 0.97935 | -3.4233 | -5.6741 | 6.5156 | 9.0194 | 1.7248 | -0.27256 | -2.933%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0875 | 0.9792 | -3.4364 | -5.6742 | 6.7051 | 9.0486 | 1.7303 | -0.27344 | -2.933%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.092 | 0.97912 | -3.4434 | -5.6742 | 7.0103 | 9.0641 | 1.7333 | -0.27391 | -2.933%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.884 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1106 | 0.97879 | -3.4723 | -5.6742 | 7.884 | 9.1281 | 1.7454 | -0.27586 | -2.933%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1641 | 0.97784 | -3.5555 | -5.6744 | 8.9155 | 9.3125 | 1.7804 | -0.28146 | -2.934%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2455 | 0.97638 | -3.6824 | -5.6745 | 9.8418 | 9.593 | 1.8336 | -0.28999 | -2.934%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2786 | 0.97579 | -3.7339 | -5.6746 | 10.3786 | 9.7066 | 1.8551 | -0.29344 | -2.934%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.269 | 0.97596 | -3.7189 | -5.6746 | 10.5155 | 9.6736 | 1.8489 | -0.29244 | -2.934%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2382 | 0.97651 | -3.6709 | -5.6745 | 10.526 | 9.5678 | 1.8288 | -0.28922 | -2.934%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.1714 | 0.97771 | -3.5669 | -5.6744 | 10.526 | 9.3378 | 1.7852 | -0.28223 | -2.934%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8783 | 0.9702 | -3.2146 | -7.4862 | 10.526 | 8.7828 | 1.6446 | -0.35622 | -3.898%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7127 | 0.97311 | -2.9563 | -7.4851 | 10.526 | 8.214 | 1.539 | -0.33304 | -3.897%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5734 | 0.97554 | -2.7395 | -7.4845 | 10.526 | 7.7335 | 1.4498 | -0.31348 | -3.896%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4815 | 0.97714 | -2.5966 | -7.484 | 10.526 | 7.4155 | 1.3906 | -0.30053 | -3.895%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99024 | -1.4264 | 0.97809 | -2.511 | -7.4837 | 10.526 | 7.2242 | 1.355 | -0.29275 | -3.895%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3959 | 0.97861 | -2.4637 | -7.4836 | 10.526 | 7.1185 | 1.3353 | -0.28845 | -3.894%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3934 | 0.97865 | -2.4599 | -7.4836 | 10.526 | 7.1099 | 1.3337 | -0.2881 | -3.894%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4391 | 0.97787 | -2.5308 | -7.4839 | 10.526 | 7.2685 | 1.3632 | -0.29455 | -3.895%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5564 | 0.97584 | -2.7131 | -7.4846 | 10.526 | 7.6749 | 1.4389 | -0.31109 | -3.895%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7347 | 0.97273 | -2.9907 | -7.4854 | 10.526 | 8.2899 | 1.5531 | -0.33613 | -3.897%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.8559 | 0.9706 | -3.1796 | -7.4858 | 10.5155 | 8.7059 | 1.6303 | -0.35309 | -3.898%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99501 | -2.048 | 0.9799 | -3.3749 | -5.6736 | 10.4102 | 8.9117 | 1.7043 | -0.26929 | -2.933%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99485 | -2.0617 | 0.97965 | -3.3962 | -5.6741 | 10.1892 | 8.9593 | 1.7134 | -0.27073 | -2.933%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0704 | 0.9795 | -3.4098 | -5.6741 | 9.9576 | 8.9894 | 1.7191 | -0.27164 | -2.933%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.0791 | 0.97935 | -3.4233 | -5.6741 | 9.8313 | 9.0194 | 1.7248 | -0.27256 | -2.933%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0875 | 0.9792 | -3.4364 | -5.6742 | 9.9681 | 9.0486 | 1.7303 | -0.27344 | -2.933%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.092 | 0.97912 | -3.4434 | -5.6742 | 10.0313 | 9.0641 | 1.7333 | -0.27391 | -2.933%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1106 | 0.97879 | -3.4723 | -5.6742 | 10.2944 | 9.1281 | 1.7454 | -0.27586 | -2.933%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1641 | 0.97784 | -3.5555 | -5.6744 | 10.4734 | 9.3125 | 1.7804 | -0.28146 | -2.934%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2455 | 0.97638 | -3.6824 | -5.6745 | 10.526 | 9.593 | 1.8336 | -0.28999 | -2.934%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2786 | 0.97579 | -3.7339 | -5.6746 | 10.526 | 9.7066 | 1.8551 | -0.29344 | -2.934%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.269 | 0.97596 | -3.7189 | -5.6746 | 10.526 | 9.6736 | 1.8489 | -0.29244 | -2.934%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2382 | 0.97651 | -3.6709 | -5.6745 | 10.526 | 9.5678 | 1.8288 | -0.28922 | -2.934%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.1714 | 0.97771 | -3.5669 | -5.6744 | 10.526 | 9.3378 | 1.7852 | -0.28223 | -2.934%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8783 | 0.9702 | -3.2146 | -7.4862 | 10.526 | 8.7828 | 1.6446 | -0.35622 | -3.898%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7127 | 0.97311 | -2.9563 | -7.4851 | 10.526 | 8.214 | 1.539 | -0.33304 | -3.897%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5734 | 0.97554 | -2.7395 | -7.4845 | 10.526 | 7.7335 | 1.4498 | -0.31348 | -3.896%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0296 | -2.1144 | 1.0168 | -3.1788 | 0.98963 | -1.4815 | 0.97714 | -2.5966 | -7.484 | 10.526 | 7.4155 | 1.3906 | -0.30053 | -3.895%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0302 | -2.0591 | 1.0178 | -3.0945 | 0.99024 | -1.4264 | 0.97809 | -2.511 | -7.4837 | 10.526 | 7.2242 | 1.355 | -0.29275 | -3.895%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0286 | 1.0183 | -3.048 | 0.99058 | -1.3959 | 0.97861 | -2.4637 | -7.4836 | 10.526 | 7.1185 | 1.3353 | -0.28845 | -3.894%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0306 | -2.0261 | 1.0184 | -3.0442 | 0.99061 | -1.3934 | 0.97865 | -2.4599 | -7.4836 | 10.526 | 7.1099 | 1.3337 | -0.2881 | -3.894%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0301 | -2.0719 | 1.0176 | -3.114 | 0.9901 | -1.4391 | 0.97787 | -2.5308 | -7.4839 | 10.526 | 7.2685 | 1.3632 | -0.29455 | -3.895%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0288 | -2.1895 | 1.0155 | -3.2935 | 0.98879 | -1.5564 | 0.97584 | -2.7131 | -7.4846 | 10.526 | 7.6749 | 1.4389 | -0.31109 | -3.895%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0268 | -2.3681 | 1.0124 | -3.5666 | 0.98678 | -1.7347 | 0.97273 | -2.9907 | -7.4854 | 10.526 | 8.2899 | 1.5531 | -0.33613 | -3.897%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0254 | -2.4895 | 1.0102 | -3.7525 | 0.98541 | -1.8559 | 0.9706 | -3.1796 | -7.4858 | 10.526 | 8.7059 | 1.6303 | -0.35309 | -3.898%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.025 | -2.5237 | 1.0096 | -3.805 | 0.99501 | -2.048 | 0.9799 | -3.3749 | -5.6736 | 10.526 | 8.9117 | 1.7043 | -0.26929 | -2.933%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0249 | -2.5375 | 1.0094 | -3.8261 | 0.99485 | -2.0617 | 0.97965 | -3.3962 | -5.6741 | 10.5155 | 8.9593 | 1.7134 | -0.27073 | -2.933%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 4 | 1.0248 | -2.5462 | 1.0092 | -3.8395 | 0.99475 | -2.0704 | 0.9795 | -3.4098 | -5.6741 | 10.4839 | 8.9894 | 1.7191 | -0.27164 | -2.933%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0247 | -2.5549 | 1.0091 | -3.8529 | 0.99465 | -2.0791 | 0.97935 | -3.4233 | -5.6741 | 10.4523 | 9.0194 | 1.7248 | -0.27256 | -2.933%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 4 | 1.0246 | -2.5634 | 1.0089 | -3.8658 | 0.99456 | -2.0875 | 0.9792 | -3.4364 | -5.6742 | 10.4523 | 9.0486 | 1.7303 | -0.27344 | -2.933%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 4 | 1.0245 | -2.5679 | 1.0088 | -3.8727 | 0.99451 | -2.092 | 0.97912 | -3.4434 | -5.6742 | 10.4734 | 9.0641 | 1.7333 | -0.27391 | -2.933%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 4 | 1.0243 | -2.5864 | 1.0085 | -3.9012 | 0.99429 | -2.1106 | 0.97879 | -3.4723 | -5.6742 | 10.5049 | 9.1281 | 1.7454 | -0.27586 | -2.933%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 4 | 1.0237 | -2.64 | 1.0075 | -3.9834 | 0.99368 | -2.1641 | 0.97784 | -3.5555 | -5.6744 | 10.5155 | 9.3125 | 1.7804 | -0.28146 | -2.934%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0227 | -2.7216 | 1.0061 | -4.1087 | 0.99273 | -2.2455 | 0.97638 | -3.6824 | -5.6745 | 10.526 | 9.593 | 1.8336 | -0.28999 | -2.934%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0223 | -2.7547 | 1.0055 | -4.1596 | 0.99235 | -2.2786 | 0.97579 | -3.7339 | -5.6746 | 10.526 | 9.7066 | 1.8551 | -0.29344 | -2.934%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0225 | -2.745 | 1.0057 | -4.1448 | 0.99246 | -2.269 | 0.97596 | -3.7189 | -5.6746 | 10.526 | 9.6736 | 1.8489 | -0.29244 | -2.934%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0228 | -2.7142 | 1.0062 | -4.0974 | 0.99282 | -2.2382 | 0.97651 | -3.6709 | -5.6745 | 10.526 | 9.5678 | 1.8288 | -0.28922 | -2.934%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0236 | -2.6473 | 1.0074 | -3.9946 | 0.99359 | -2.1714 | 0.97771 | -3.5669 | -5.6744 | 10.526 | 9.3378 | 1.7852 | -0.28223 | -2.934%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0251 | -2.5119 | 1.0098 | -3.7869 | 0.98515 | -1.8783 | 0.9702 | -3.2146 | -7.4862 | 10.526 | 8.7828 | 1.6446 | -0.35622 | -3.898%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.027 | -2.346 | 1.0128 | -3.5327 | 0.98704 | -1.7127 | 0.97311 | -2.9563 | -7.4851 | 10.526 | 8.214 | 1.539 | -0.33304 | -3.897%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 4 | 1.0286 | -2.2065 | 1.0152 | -3.3194 | 0.9886 | -1.5734 | 0.97554 | -2.7395 | -7.4845 | 10.526 | 7.7335 | 1.4498 | -0.31348 | -3.896%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0168 | -3.1788 | 1.0168 | -3.1788 | 0.97451 | -2.4059 | 0.97451 | -2.4059 | -5.263 | 5.263 | 7.3958 | 1.3792 | -0.32016 | -4.149%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97548 | -2.321 | 0.97548 | -2.321 | -5.263 | 5.263 | 7.2053 | 1.344 | -0.31174 | -4.147%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97601 | -2.2741 | 0.97601 | -2.2741 | -5.263 | 5.263 | 7.0999 | 1.3245 | -0.30708 | -4.146%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97606 | -2.2703 | 0.97606 | -2.2703 | -5.263 | 5.263 | 7.0913 | 1.3229 | -0.3067 | -4.146%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97525 | -2.3406 | 0.97525 | -2.3406 | -5.263 | 5.263 | 7.2493 | 1.3521 | -0.31369 | -4.148%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97318 | -2.5216 | 0.97318 | -2.5216 | -5.263 | 5.263 | 7.6544 | 1.4269 | -0.3316 | -4.152%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2525 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2525 | 5.2525 | 8.2671 | 1.5398 | -0.35892 | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1156 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 5.1156 | 8.7007 | 1.6272 | -0.35834 | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.7051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97199 | -3.1176 | 0.97199 | -3.1176 | -4.7051 | 4.7051 | 8.841 | 1.6626 | -0.34005 | -3.704%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.142 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97651 | -3.2173 | 0.97651 | -3.2173 | -4.142 | 4.142 | 8.9309 | 1.6966 | -0.29912 | -3.241%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5736 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.98115 | -3.3097 | 0.98115 | -3.3097 | -3.5736 | 3.5736 | 9.0043 | 1.7279 | -0.25669 | -2.772%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.2578 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.98366 | -3.367 | 0.98366 | -3.367 | -3.2578 | 3.2578 | 9.0587 | 1.748 | -0.23332 | -2.511%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.3525 | 5 | 1.0089 | -3.8658 | 1.0089 | -3.8658 | 0.9827 | -3.3669 | 0.9827 | -3.3669 | -3.3525 | 3.3525 | 9.0806 | 1.7493 | -0.24144 | -2.59%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.5052 | 5 | 1.0088 | -3.8727 | 1.0088 | -3.8727 | 0.98133 | -3.3527 | 0.98133 | -3.3527 | -3.5052 | 3.5052 | 9.0843 | 1.7452 | -0.25367 | -2.716%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 5.263 | 3.942 | 5 | 1.0085 | -3.9012 | 1.0085 | -3.9012 | 0.97731 | -3.3209 | 0.97731 | -3.3209 | -3.942 | 3.942 | 9.1145 | 1.7374 | -0.28947 | -3.078%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.4578 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97199 | -3.3328 | 0.97199 | -3.3328 | -4.4578 | 4.4578 | 9.2578 | 1.748 | -0.33623 | -3.505%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 5.263 | 4.9209 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 4.9209 | 9.5314 | 1.797 | -0.35157 | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.1893 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 5.1893 | 9.65 | 1.8215 | -0.35 | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.2577 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 5.2577 | 9.6155 | 1.8144 | -0.35047 | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 5.263 | 9.5051 | 1.7916 | -0.3519 | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 5.263 | 9.2655 | 1.7424 | -0.35454 | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 5.263 | 8.781 | 1.6435 | -0.358 | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.263 | 5.263 | 8.1882 | 1.5239 | -0.35882 | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97288 | -2.5478 | 0.97288 | -2.5478 | -5.263 | 5.263 | 7.7128 | 1.4377 | -0.33419 | -4.153%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97451 | -2.4059 | 0.97451 | -2.4059 | -5.263 | 5.263 | 7.3958 | 1.3792 | -0.32017 | -4.149%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97548 | -2.321 | 0.97548 | -2.321 | -5.263 | 5.263 | 7.2053 | 1.344 | -0.31174 | -4.147%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97601 | -2.2741 | 0.97601 | -2.2741 | -5.263 | 5.263 | 7.0999 | 1.3245 | -0.30708 | -4.146%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97606 | -2.2703 | 0.97606 | -2.2703 | -5.263 | 5.263 | 7.0913 | 1.3229 | -0.3067 | -4.146%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97525 | -2.3406 | 0.97525 | -2.3406 | -5.263 | 5.263 | 7.2493 | 1.3521 | -0.31369 | -4.148%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97318 | -2.5216 | 0.97318 | -2.5216 | -5.263 | 5.263 | 7.6544 | 1.4269 | -0.3316 | -4.152%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.263 | 5.263 | 8.2671 | 1.5398 | -0.35892 | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2577 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 5.2577 | 8.7007 | 1.6272 | -0.35834 | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2051 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 5.2051 | 8.8232 | 1.6521 | -0.35781 | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0946 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 5.0946 | 8.8725 | 1.6621 | -0.35755 | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9788 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 4.9788 | 8.9036 | 1.6685 | -0.35737 | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 4.9156 | 8.9348 | 1.6748 | -0.35718 | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 4.9841 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 4.9841 | 8.965 | 1.681 | -0.35699 | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.0156 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 5.0156 | 8.9811 | 1.6842 | -0.35688 | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.1472 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 5.1472 | 9.0476 | 1.6978 | -0.35641 | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.2367 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 5.2367 | 9.2392 | 1.737 | -0.3548 | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 5.263 | 9.5314 | 1.797 | -0.35157 | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 5.263 | 9.65 | 1.8215 | -0.35 | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 5.263 | 9.6155 | 1.8144 | -0.35047 | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 5.263 | 9.5051 | 1.7916 | -0.3519 | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 5.263 | 9.2655 | 1.7424 | -0.35454 | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 5.263 | 8.781 | 1.6435 | -0.358 | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.263 | 5.263 | 8.1882 | 1.5239 | -0.35882 | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97288 | -2.5478 | 0.97288 | -2.5478 | -5.263 | 5.263 | 7.7128 | 1.4377 | -0.33419 | -4.153%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97451 | -2.4059 | 0.97451 | -2.4059 | -5.263 | 5.263 | 7.3958 | 1.3792 | -0.32017 | -4.149%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97548 | -2.321 | 0.97548 | -2.321 | -5.263 | 5.263 | 7.2053 | 1.344 | -0.31174 | -4.147%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97601 | -2.2741 | 0.97601 | -2.2741 | -5.263 | 5.263 | 7.0999 | 1.3245 | -0.30708 | -4.146%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97606 | -2.2703 | 0.97606 | -2.2703 | -5.263 | 5.263 | 7.0913 | 1.3229 | -0.3067 | -4.146%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97525 | -2.3406 | 0.97525 | -2.3406 | -5.263 | 5.263 | 7.2493 | 1.3521 | -0.31369 | -4.148%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0155 | -3.2935 | 1.0155 | -3.2935 | 0.97318 | -2.5216 | 0.97318 | -2.5216 | -5.263 | 5.263 | 7.6544 | 1.4269 | -0.3316 | -4.152%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.263 | 5.263 | 8.2671 | 1.5398 | -0.35892 | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 5.263 | 8.7007 | 1.6272 | -0.35834 | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 5.263 | 8.8232 | 1.6521 | -0.35781 | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 5.2577 | 8.8725 | 1.6621 | -0.35755 | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2419 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 5.2419 | 8.9036 | 1.6685 | -0.35737 | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 5.2262 | 8.9348 | 1.6748 | -0.35718 | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2262 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 5.2262 | 8.965 | 1.681 | -0.35699 | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2367 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 5.2367 | 8.9811 | 1.6842 | -0.35688 | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2525 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 5.2525 | 9.0476 | 1.6978 | -0.35641 | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.2577 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 5.2577 | 9.2392 | 1.737 | -0.3548 | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 5.263 | 9.5314 | 1.797 | -0.35157 | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 5.263 | 9.65 | 1.8215 | -0.35 | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 5.263 | 9.6155 | 1.8144 | -0.35047 | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 5.263 | 9.5051 | 1.7916 | -0.3519 | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 5.263 | 9.2655 | 1.7424 | -0.35454 | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 5.263 | 8.781 | 1.6435 | -0.358 | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.263 | 5.263 | 8.1882 | 1.5239 | -0.35882 | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 5.263 | 5.263 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97288 | -2.5478 | 0.97288 | -2.5478 | -5.263 | 5.263 | 7.7128 | 1.4377 | -0.33419 | -4.153%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.331 | 0.97 | -2.331 | -5.7876 | 10.526 | 7.3623 | 1.3597 | -0.35373 | -4.584%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2297 | 0.97 | -2.2297 | -5.8994 | 10.526 | 7.1655 | 1.3209 | -0.35147 | -4.676%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1739 | 0.97 | -2.1739 | -5.9608 | 10.526 | 7.057 | 1.2996 | -0.35004 | -4.726%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1693 | 0.97 | -2.1693 | -5.9658 | 10.526 | 7.0481 | 1.2979 | -0.34992 | -4.73%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2531 | 0.97 | -2.2531 | -5.8736 | 10.526 | 7.211 | 1.3299 | -0.35203 | -4.655%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4688 | 0.97 | -2.4688 | -5.6347 | 10.526 | 7.6298 | 1.4126 | -0.35618 | -4.46%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5049 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2666 | 10.5049 | 8.2671 | 1.5398 | -0.35894 | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.2313 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 10.2313 | 8.7007 | 1.6272 | -0.35834 | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 9.4102 | 8.8232 | 1.6521 | -0.35781 | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.284 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 8.284 | 8.8725 | 1.6621 | -0.35755 | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.1472 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 7.1472 | 8.9036 | 1.6685 | -0.35737 | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.5156 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 6.5156 | 8.9348 | 1.6748 | -0.35718 | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | very sunny | 10.526 | 6.7051 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 6.7051 | 8.965 | 1.681 | -0.35699 | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.0103 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 7.0103 | 8.9811 | 1.6842 | -0.35688 | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | very sunny | 10.526 | 7.884 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 7.884 | 9.0476 | 1.6978 | -0.35641 | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | very sunny | 10.526 | 8.9155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 8.9155 | 9.2392 | 1.737 | -0.3548 | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | very sunny | 10.526 | 9.8418 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 9.8418 | 9.5314 | 1.797 | -0.35157 | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.3786 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 10.3786 | 9.65 | 1.8215 | -0.35 | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.5155 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 10.5155 | 9.6155 | 1.8144 | -0.35047 | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 10.526 | 9.5051 | 1.7916 | -0.3519 | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 10.526 | 9.2655 | 1.7424 | -0.35454 | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 10.526 | 8.781 | 1.6435 | -0.358 | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.3125 | 10.526 | 8.1882 | 1.5239 | -0.35882 | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | very sunny | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.5 | 0.97 | -2.5 | -5.6 | 10.526 | 7.6904 | 1.4246 | -0.35662 | -4.432%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.331 | 0.97 | -2.331 | -5.7876 | 10.526 | 7.3623 | 1.3597 | -0.35374 | -4.584%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2297 | 0.97 | -2.2297 | -5.8994 | 10.526 | 7.1655 | 1.3209 | -0.35147 | -4.676%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1739 | 0.97 | -2.1739 | -5.9608 | 10.526 | 7.057 | 1.2996 | -0.35004 | -4.726%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1693 | 0.97 | -2.1693 | -5.9658 | 10.526 | 7.0481 | 1.2979 | -0.34992 | -4.73%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2531 | 0.97 | -2.2531 | -5.8736 | 10.526 | 7.211 | 1.3299 | -0.35203 | -4.655%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4688 | 0.97 | -2.4688 | -5.6347 | 10.526 | 7.6298 | 1.4126 | -0.35618 | -4.46%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2666 | 10.526 | 8.2671 | 1.5398 | -0.35894 | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.5155 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 10.5155 | 8.7007 | 1.6272 | -0.35834 | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4102 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 10.4102 | 8.8232 | 1.6521 | -0.35781 | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.1892 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 10.1892 | 8.8725 | 1.6621 | -0.35755 | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9576 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 9.9576 | 8.9036 | 1.6685 | -0.35737 | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.8313 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 9.8313 | 8.9348 | 1.6748 | -0.35718 | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 9.9681 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 9.9681 | 8.965 | 1.681 | -0.35699 | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.0313 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 10.0313 | 8.9811 | 1.6842 | -0.35688 | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.2944 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 10.2944 | 9.0476 | 1.6978 | -0.35641 | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.4734 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 10.4734 | 9.2392 | 1.737 | -0.3548 | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 10.526 | 9.5314 | 1.797 | -0.35157 | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 10.526 | 9.65 | 1.8215 | -0.35 | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 10.526 | 9.6155 | 1.8144 | -0.35047 | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 10.526 | 9.5051 | 1.7916 | -0.3519 | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 10.526 | 9.2655 | 1.7424 | -0.35454 | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 10.526 | 8.781 | 1.6435 | -0.358 | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.3125 | 10.526 | 8.1882 | 1.5239 | -0.35882 | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | moderate sun | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.5 | 0.97 | -2.5 | -5.6 | 10.526 | 7.6904 | 1.4246 | -0.35662 | -4.432%
1 | 7.716 | 1.5668 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0168 | -3.1789 | 1.0168 | -3.1789 | 0.97 | -2.331 | 0.97 | -2.331 | -5.7876 | 10.526 | 7.3623 | 1.3597 | -0.35374 | -4.584%
2 | 7.517 | 1.5264 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0178 | -3.0946 | 1.0178 | -3.0946 | 0.97 | -2.2297 | 0.97 | -2.2297 | -5.8994 | 10.526 | 7.1655 | 1.3209 | -0.35147 | -4.676%
3 | 7.407 | 1.5041 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0183 | -3.0481 | 1.0183 | -3.0481 | 0.97 | -2.1739 | 0.97 | -2.1739 | -5.9608 | 10.526 | 7.057 | 1.2996 | -0.35004 | -4.726%
4 | 7.398 | 1.5022 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0184 | -3.0443 | 1.0184 | -3.0443 | 0.97 | -2.1693 | 0.97 | -2.1693 | -5.9658 | 10.526 | 7.0481 | 1.2979 | -0.34992 | -4.73%
5 | 7.563 | 1.5357 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0176 | -3.1141 | 1.0176 | -3.1141 | 0.97 | -2.2531 | 0.97 | -2.2531 | -5.8736 | 10.526 | 7.211 | 1.3299 | -0.35203 | -4.655%
6 | 7.986 | 1.6216 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0155 | -3.2936 | 1.0155 | -3.2936 | 0.97 | -2.4688 | 0.97 | -2.4688 | -5.6347 | 10.526 | 7.6298 | 1.4126 | -0.35618 | -4.46%
7 | 8.626 | 1.7516 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0124 | -3.5667 | 1.0124 | -3.5667 | 0.97 | -2.7974 | 0.97 | -2.7974 | -5.2666 | 10.526 | 8.2671 | 1.5398 | -0.35894 | -4.161%
8 | 9.059 | 1.8395 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0102 | -3.7525 | 1.0102 | -3.7525 | 0.97 | -3.0215 | 0.97 | -3.0215 | -5.0127 | 10.526 | 8.7007 | 1.6272 | -0.35834 | -3.956%
9 | 9.181 | 1.8643 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0096 | -3.8051 | 1.0096 | -3.8051 | 0.97 | -3.0849 | 0.97 | -3.0849 | -4.9405 | 10.526 | 8.8232 | 1.6521 | -0.35781 | -3.897%
10 | 9.23 | 1.8742 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 1.0094 | -3.8262 | 1.0094 | -3.8262 | 0.97 | -3.1104 | 0.97 | -3.1104 | -4.9114 | 10.5155 | 8.8725 | 1.6621 | -0.35755 | -3.874%
11 | 9.261 | 1.8805 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4839 | 5 | 1.0092 | -3.8395 | 1.0092 | -3.8395 | 0.97 | -3.1265 | 0.97 | -3.1265 | -4.893 | 10.4839 | 8.9036 | 1.6685 | -0.35737 | -3.859%
12 | 9.292 | 1.8868 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 1.0091 | -3.8529 | 1.0091 | -3.8529 | 0.97 | -3.1426 | 0.97 | -3.1426 | -4.8745 | 10.4523 | 8.9348 | 1.6748 | -0.35718 | -3.844%
13 | 9.322 | 1.8929 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4523 | 5 | 1.0089 | -3.8659 | 1.0089 | -3.8659 | 0.97 | -3.1583 | 0.97 | -3.1583 | -4.8566 | 10.4523 | 8.965 | 1.681 | -0.35699 | -3.83%
14 | 9.338 | 1.8962 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.4734 | 5 | 1.0088 | -3.8728 | 1.0088 | -3.8728 | 0.97 | -3.1666 | 0.97 | -3.1666 | -4.8471 | 10.4734 | 8.9811 | 1.6842 | -0.35688 | -3.822%
15 | 9.404 | 1.9096 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5049 | 5 | 1.0085 | -3.9013 | 1.0085 | -3.9013 | 0.97 | -3.201 | 0.97 | -3.201 | -4.8077 | 10.5049 | 9.0476 | 1.6978 | -0.35641 | -3.79%
16 | 9.594 | 1.9481 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.5155 | 5 | 1.0075 | -3.9834 | 1.0075 | -3.9834 | 0.97 | -3.3002 | 0.97 | -3.3002 | -4.6937 | 10.5155 | 9.2392 | 1.737 | -0.3548 | -3.698%
17 | 9.883 | 2.0068 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0061 | -4.1088 | 1.0061 | -4.1088 | 0.97 | -3.4517 | 0.97 | -3.4517 | -4.5187 | 10.526 | 9.5314 | 1.797 | -0.35157 | -3.557%
18 | 10 | 2.0306 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0055 | -4.1596 | 1.0055 | -4.1596 | 0.97 | -3.5132 | 0.97 | -3.5132 | -4.4474 | 10.526 | 9.65 | 1.8215 | -0.35 | -3.5%
19 | 9.966 | 2.0237 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0057 | -4.1448 | 1.0057 | -4.1448 | 0.97 | -3.4953 | 0.97 | -3.4953 | -4.4682 | 10.526 | 9.6155 | 1.8144 | -0.35047 | -3.517%
20 | 9.857 | 2.0015 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0062 | -4.0975 | 1.0062 | -4.0975 | 0.97 | -3.4381 | 0.97 | -3.4381 | -4.5346 | 10.526 | 9.5051 | 1.7916 | -0.3519 | -3.57%
21 | 9.62 | 1.9534 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0074 | -3.9947 | 1.0074 | -3.9947 | 0.97 | -3.3138 | 0.97 | -3.3138 | -4.678 | 10.526 | 9.2655 | 1.7424 | -0.35454 | -3.685%
22 | 9.139 | 1.8558 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0098 | -3.7869 | 1.0098 | -3.7869 | 0.97 | -3.063 | 0.97 | -3.063 | -4.9654 | 10.526 | 8.781 | 1.6435 | -0.358 | -3.917%
23 | 8.547 | 1.7355 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0128 | -3.5328 | 1.0128 | -3.5328 | 0.97 | -2.7567 | 0.97 | -2.7567 | -5.3125 | 10.526 | 8.1882 | 1.5239 | -0.35882 | -4.198%
24 | 8.047 | 1.634 | 0.98 | ZIP - Comm | cloudy | 10.526 | 10.526 | 5 | 1.0152 | -3.3195 | 1.0152 | -3.3195 | 0.97 | -2.5 | 0.97 | -2.5 | -5.6 | 10.526 | 7.6904 | 1.4246 | -0.35662 | -4.432%